## README
Topic | Guidance
Registry | AIDCF-007A Canonical Master Control Registry, version 1.1 (amendment AIDCF-007A-AMD-002), 2026-10-10.
Status | PROPOSED - Draft for controlled review. Version 1.0 (AIDCF-007A-AMD-001) remains the approved cardinality and identifier baseline until v1.1 completes controlled methodology review and independent ratification.
What changed in v1.1 | Control content rewritten per control (objective, requirement, criteria, parameters, evidence profile, procedure, testing safety, UNKNOWN rule); IDs and 15/90/360 structure unchanged; duplicate titles fixed (MCF-NET-004, MCF-STO-019); control-specific gate mappings with CRITICAL/SUPPORTING roles replace whole-domain mapping; Required Assurance Level assigned per control from its claim type (AL2-AL5).
Gate roll-up | A gate cannot PASS unless every in-scope CRITICAL control is CONFORMING at its required claim type; PARTIAL never yields PASS. SUPPORTING controls inform the gate evaluation. CG-11 and CG-12 are meta-gates evaluated across all controls. See AIDCF-010.
Vocabularies | All codes are canonical per AIDCF-002 and registries/vocabularies/.
Constitutional rule | Controls do not create assurance by existence. Missing evidence is UNKNOWN, not N/A. Scores never override gates (AIDCF-006).
Parameters | Engineering values are capability-profile parameters; defaults are illustrative unless attributed to a named source.
Machine-readable copies | registries/controls/controls.json (full), controls.csv, gate-mappings.csv, evidence-profiles.csv, parameters.csv.

## Summary
Metric | Value
Domains | 15
Families | 90
Controls | 360
Controls per family | 4
Unique titles | 360
CRITICAL gate mappings | 106
SUPPORTING gate mappings | 483
Claim type DESIGN | 52
Claim type IMPLEMENTATION | 94
Claim type OPERATION | 133
Claim type EFFECTIVENESS | 52
Claim type RESILIENCE | 29

## Domains
Domain Code | Domain | Families | Controls | Gates with CRITICAL controls
GOV | Governance, Accountability and Assurance Direction | 6 | 24 | CG-13
CAP | AI Capability, Service Outcome and Demand Management | 6 | 24 | CG-01; CG-02; CG-13; CG-14
DEP | Dependency, Concentration and External Reliance Management | 6 | 24 | CG-02; CG-03; CG-13
PHY | Physical Site, Building and Security Infrastructure | 6 | 24 | CG-04; CG-09
POW | Electrical Power Infrastructure and Energy Continuity | 6 | 24 | CG-04; CG-05; CG-07; CG-09; CG-10
THM | Cooling, Thermal and Fluid Infrastructure | 6 | 24 | CG-04; CG-06; CG-07; CG-09; CG-10
ENV | Environmental and Resource Performance | 6 | 24 | CG-04
CMP | AI Compute Infrastructure | 6 | 24 | CG-08; CG-09; CG-10; CG-14
STO | AI Storage and Data Infrastructure | 6 | 24 | CG-08; CG-09; CG-10
NET | AI Network and Interconnect Architecture | 6 | 24 | CG-08; CG-09; CG-10; CG-14
OPS | Building Operations and Service Management | 6 | 24 | CG-04; CG-07; CG-13; CG-14
RES | Resilience, Continuity and Recovery | 6 | 24 | CG-09; CG-10
SUP | Supply Chain, OEM and Ecosystem Assurance | 6 | 24 | CG-03; CG-15
SEC | Digital, OT and Control-Plane Security | 6 | 24 | CG-07; CG-15
EVA | Evidence, Assessment and Assurance Management | 6 | 24 | CG-01; CG-02

## Families
Family ID | Domain Code | Control Family | Controls | Gates with CRITICAL controls
GOV-01 | GOV | Governance architecture | MCF-GOV-001 Governance Charter; MCF-GOV-002 Decision Rights; MCF-GOV-003 Committee Oversight; MCF-GOV-004 Methodology Ownership | CG-13
GOV-02 | GOV | Accountability and responsibility | MCF-GOV-005 RACI and Role Ownership; MCF-GOV-006 Critical Function Accountability; MCF-GOV-007 Risk Acceptance Authority; MCF-GOV-008 Evidence Custody | CG-13
GOV-03 | GOV | Policy and standards management | MCF-GOV-009 Policy Hierarchy; MCF-GOV-010 Technical Standard Baselines; MCF-GOV-011 Exception Governance; MCF-GOV-012 Document Lifecycle
GOV-04 | GOV | Risk and assurance governance | MCF-GOV-013 Assurance Plan; MCF-GOV-014 Risk Appetite Linkage; MCF-GOV-015 Critical Gate Governance; MCF-GOV-016 Independent Review
GOV-05 | GOV | Stakeholder and regulatory interface | MCF-GOV-017 Stakeholder Obligations; MCF-GOV-018 Regulatory Monitoring; MCF-GOV-019 Customer Commitments; MCF-GOV-020 External Reporting
GOV-06 | GOV | Ethics, impartiality and competence | MCF-GOV-021 Conflict Management; MCF-GOV-022 Assessor Independence; MCF-GOV-023 Competence Management; MCF-GOV-024 Appeal and Challenge
CAP-01 | CAP | Capability inventory | MCF-CAP-001 Capability Register; MCF-CAP-002 Capability Ownership; MCF-CAP-003 Lifecycle Status; MCF-CAP-004 Architecture Linkage | CG-01; CG-02; CG-13
CAP-02 | CAP | Service outcome definition | MCF-CAP-005 Availability Outcomes; MCF-CAP-006 Performance Outcomes; MCF-CAP-007 Integrity Outcomes; MCF-CAP-008 Recovery Outcomes | CG-01
CAP-03 | CAP | Criticality and materiality | MCF-CAP-009 Criticality Criteria; MCF-CAP-010 Impact Tolerance; MCF-CAP-011 Stakeholder Consequence; MCF-CAP-012 Priority Classification | CG-01
CAP-04 | CAP | Demand and growth modelling | MCF-CAP-013 Current Demand Baseline; MCF-CAP-014 Peak and Transient Demand; MCF-CAP-015 Growth Forecast; MCF-CAP-016 Scenario Demand
CAP-05 | CAP | Operating envelope | MCF-CAP-017 Load Envelope; MCF-CAP-018 Environmental Envelope; MCF-CAP-019 Duration Limits; MCF-CAP-020 State-Specific Limits
CAP-06 | CAP | Capability lifecycle and change | MCF-CAP-021 Design-to-Operation Traceability; MCF-CAP-022 Commissioning Acceptance; MCF-CAP-023 Material Change Impact; MCF-CAP-024 Retirement Control | CG-14
DEP-01 | DEP | Dependency discovery | MCF-DEP-001 Asset-to-Function Mapping; MCF-DEP-002 Upstream Dependency Mapping; MCF-DEP-003 Downstream Consequence Mapping; MCF-DEP-004 Recovery Dependency Mapping | CG-03
DEP-02 | DEP | Shared and common-mode dependencies | MCF-DEP-005 Shared Source Analysis; MCF-DEP-006 Common Controller Analysis; MCF-DEP-007 Shared Route Analysis; MCF-DEP-008 Shared Human Dependency Analysis | CG-03
DEP-03 | DEP | External providers and utilities | MCF-DEP-009 Utility Dependency; MCF-DEP-010 Telecom Dependency; MCF-DEP-011 OEM Dependency; MCF-DEP-012 Cloud and Service Dependency | CG-03
DEP-04 | DEP | Concentration and substitutability | MCF-DEP-013 Capacity Concentration; MCF-DEP-014 Supplier Concentration; MCF-DEP-015 Knowledge Concentration; MCF-DEP-016 Substitution Readiness
DEP-05 | DEP | Boundary and interface control | MCF-DEP-017 Assessment Boundary; MCF-DEP-018 Provider Boundary; MCF-DEP-019 Tenant Boundary; MCF-DEP-020 Cross-Boundary Enforcement | CG-02; CG-03; CG-13
DEP-06 | DEP | Dependency monitoring and review | MCF-DEP-021 Dependency Health Indicators; MCF-DEP-022 Provider Performance; MCF-DEP-023 Change Detection; MCF-DEP-024 Periodic Revalidation
PHY-01 | PHY | Site and location resilience | MCF-PHY-001 Site Hazard Assessment; MCF-PHY-002 External Exposure; MCF-PHY-003 Access and Logistics; MCF-PHY-004 Adjacent Risk
PHY-02 | PHY | Building and structural integrity | MCF-PHY-005 Structural Capacity; MCF-PHY-006 Rack Loading; MCF-PHY-007 Anchorage and Vibration; MCF-PHY-008 Building Envelope
PHY-03 | PHY | Physical zoning and segregation | MCF-PHY-009 Security Zones; MCF-PHY-010 Fire Zones; MCF-PHY-011 Water Zones; MCF-PHY-012 Tenant Segregation | CG-09
PHY-04 | PHY | Access and surveillance | MCF-PHY-013 Identity-Based Access; MCF-PHY-014 Visitor Control; MCF-PHY-015 Surveillance Coverage; MCF-PHY-016 Alarm Response
PHY-05 | PHY | Asset movement and custody | MCF-PHY-017 Delivery Controls; MCF-PHY-018 Equipment Movement; MCF-PHY-019 Media Custody; MCF-PHY-020 Decommissioning Custody
PHY-06 | PHY | Fire, life safety and emergency interfaces | MCF-PHY-021 Fire Detection; MCF-PHY-022 Suppression Interfaces; MCF-PHY-023 Egress and Emergency Access; MCF-PHY-024 Emergency Shutdown Governance | CG-04
POW-01 | POW | Utility and grid interface | MCF-POW-001 Utility Capacity; MCF-POW-002 Grid Quality; MCF-POW-003 Connection Reliability; MCF-POW-004 Utility Contingency | CG-05
POW-02 | POW | Generation and fuel | MCF-POW-005 Generator Capacity; MCF-POW-006 Start Reliability; MCF-POW-007 Fuel Autonomy; MCF-POW-008 Fuel Replenishment | CG-05
POW-03 | POW | UPS and energy storage | MCF-POW-009 UPS Topology; MCF-POW-010 Battery Condition; MCF-POW-011 Runtime and Derating; MCF-POW-012 Bypass Exposure | CG-04; CG-05
POW-04 | POW | Distribution and protection | MCF-POW-013 Switchgear Integrity; MCF-POW-014 Selective Coordination; MCF-POW-015 Busway and PDU Capacity; MCF-POW-016 Earthing and Bonding | CG-04; CG-09
POW-05 | POW | Power quality and transient response | MCF-POW-017 Voltage Quality; MCF-POW-018 Harmonics; MCF-POW-019 Transient Ride-Through; MCF-POW-020 Load-Step Response | CG-05
POW-06 | POW | Electrical monitoring, maintenance and recovery | MCF-POW-021 EPMS Coverage; MCF-POW-022 Preventive Maintenance; MCF-POW-023 Switching Procedures; MCF-POW-024 Black-Start and Restoration | CG-04; CG-07; CG-10
THM-01 | THM | Thermal architecture and capacity | MCF-THM-001 Heat-Load Model; MCF-THM-002 Design Capacity; MCF-THM-003 Resilient Capacity; MCF-THM-004 Seasonal Derating | CG-06
THM-02 | THM | Air cooling systems | MCF-THM-005 Airflow Management; MCF-THM-006 Containment; MCF-THM-007 CRAH and In-Row Capacity; MCF-THM-008 Air-Side Monitoring
THM-03 | THM | Liquid cooling systems | MCF-THM-009 Direct-to-Chip Architecture; MCF-THM-010 CDU Capacity; MCF-THM-011 Secondary Loop Integrity; MCF-THM-012 Quick-Disconnect Management | CG-06
THM-04 | THM | Heat rejection and water systems | MCF-THM-013 Chiller Capacity; MCF-THM-014 Cooling Tower or Dry Cooler; MCF-THM-015 Water Continuity; MCF-THM-016 Heat-Rejection Dependency | CG-06
THM-05 | THM | Fluid quality and leak management | MCF-THM-017 Coolant Compatibility; MCF-THM-018 Water Quality; MCF-THM-019 Leak Detection; MCF-THM-020 Isolation and Drainage | CG-04; CG-09
THM-06 | THM | Thermal control, maintenance and recovery | MCF-THM-021 Control Stability; MCF-THM-022 Sensor Trust; MCF-THM-023 Maintenance States; MCF-THM-024 Thermal Recovery | CG-07; CG-10
ENV-01 | ENV | Environmental operating conditions | MCF-ENV-001 Temperature Control; MCF-ENV-002 Humidity Control; MCF-ENV-003 Particulate and Corrosion; MCF-ENV-004 Vibration and Acoustic Conditions
ENV-02 | ENV | Energy performance | MCF-ENV-005 PUE Measurement; MCF-ENV-006 Energy Allocation; MCF-ENV-007 Efficiency Under Load; MCF-ENV-008 Resilience-Efficiency Trade-Off
ENV-03 | ENV | Water performance | MCF-ENV-009 Water Source and Quality; MCF-ENV-010 WUE Measurement; MCF-ENV-011 Water Scarcity Response; MCF-ENV-012 Discharge Control
ENV-04 | ENV | Carbon and resource reporting | MCF-ENV-013 Carbon Accounting Boundary; MCF-ENV-014 Energy Attribute Evidence; MCF-ENV-015 Embodied Resource Data; MCF-ENV-016 Reporting Traceability
ENV-05 | ENV | Hazardous materials and waste | MCF-ENV-017 Battery Materials; MCF-ENV-018 Refrigerants and Coolants; MCF-ENV-019 Fuel and Suppressant Handling; MCF-ENV-020 Hardware and Media Waste | CG-04
ENV-06 | ENV | Climate adaptation and resource continuity | MCF-ENV-021 Heatwave Readiness; MCF-ENV-022 Drought Readiness; MCF-ENV-023 Flood Adaptation; MCF-ENV-024 Long-Term Resource Constraints
CMP-01 | CMP | Compute architecture and configuration | MCF-CMP-001 Accelerator Architecture; MCF-CMP-002 Node Configuration; MCF-CMP-003 Rack-Scale Composition; MCF-CMP-004 Approved Baseline
CMP-02 | CMP | Cluster and scale-up domains | MCF-CMP-005 Cluster Topology; MCF-CMP-006 Scale-Up Domain Integrity; MCF-CMP-007 Partitioning; MCF-CMP-008 Fault-Domain Design | CG-08; CG-09
CMP-03 | CMP | Capacity, scheduling and utilisation | MCF-CMP-009 Usable Accelerator Capacity; MCF-CMP-010 Scheduler Controls; MCF-CMP-011 Resource Reservation; MCF-CMP-012 Contention Management | CG-08
CMP-04 | CMP | Firmware, driver and compatibility | MCF-CMP-013 Firmware Baseline; MCF-CMP-014 Driver Compatibility; MCF-CMP-015 Upgrade Testing; MCF-CMP-016 Rollback Readiness | CG-08; CG-14
CMP-05 | CMP | Compute health and observability | MCF-CMP-017 GPU Telemetry; MCF-CMP-018 Node Health; MCF-CMP-019 Error and Degradation Detection; MCF-CMP-020 Performance Baselines | CG-08
CMP-06 | CMP | Compute lifecycle and recovery | MCF-CMP-021 Provisioning; MCF-CMP-022 Spares and RMA; MCF-CMP-023 Node Rebuild; MCF-CMP-024 Secure Retirement | CG-10
STO-01 | STO | Storage architecture and tiering | MCF-STO-001 Training Data Tier; MCF-STO-002 Checkpoint Tier; MCF-STO-003 Model and Artifact Tier; MCF-STO-004 Archive Tier
STO-02 | STO | Performance and capacity | MCF-STO-005 Throughput and IOPS; MCF-STO-006 Metadata Performance; MCF-STO-007 Capacity Headroom; MCF-STO-008 Burst Handling | CG-08
STO-03 | STO | Integrity and consistency | MCF-STO-009 Data Integrity; MCF-STO-010 Metadata Integrity; MCF-STO-011 Checksum and Scrubbing; MCF-STO-012 Configuration Consistency | CG-08
STO-04 | STO | Protection and replication | MCF-STO-013 Snapshot Protection; MCF-STO-014 Replication; MCF-STO-015 Erasure Coding; MCF-STO-016 Immutable Recovery Copy | CG-09; CG-10
STO-05 | STO | Checkpoint and recovery services | MCF-STO-017 Checkpoint Durability; MCF-STO-018 Restart Readiness; MCF-STO-019 Storage Recovery Sequencing; MCF-STO-020 Recovery Validation | CG-08; CG-10
STO-06 | STO | Storage monitoring and lifecycle | MCF-STO-021 Storage Telemetry; MCF-STO-022 Capacity Forecasting; MCF-STO-023 Media Health; MCF-STO-024 Secure Sanitisation
NET-01 | NET | Scale-up and scale-out fabrics | MCF-NET-001 Fabric Topology; MCF-NET-002 Path Diversity; MCF-NET-003 Oversubscription; MCF-NET-004 Fabric Fault-Domain Design | CG-08; CG-09
NET-02 | NET | Performance and congestion control | MCF-NET-005 Latency Baseline; MCF-NET-006 Loss and Retransmission; MCF-NET-007 Congestion Control; MCF-NET-008 Collective Communication Performance | CG-08
NET-03 | NET | Storage and service networks | MCF-NET-009 Storage Fabric; MCF-NET-010 Frontend Network; MCF-NET-011 Service Gateways; MCF-NET-012 Traffic Isolation | CG-08
NET-04 | NET | Management and out-of-band networks | MCF-NET-013 Management Separation; MCF-NET-014 Console Access; MCF-NET-015 OOB Resilience; MCF-NET-016 Break-Glass Access | CG-10
NET-05 | NET | Physical connectivity and optics | MCF-NET-017 Cabling Standards; MCF-NET-018 Optics Compatibility; MCF-NET-019 Cross-Connect Control; MCF-NET-020 Path Documentation
NET-06 | NET | Network control and observability | MCF-NET-021 Controller Resilience; MCF-NET-022 Configuration Management; MCF-NET-023 Flow Telemetry; MCF-NET-024 Time and Core Services | CG-14
OPS-01 | OPS | Operating model and staffing | MCF-OPS-001 24x7 Coverage; MCF-OPS-002 Role Clarity; MCF-OPS-003 Shift Handover; MCF-OPS-004 Competence and Authorisation | CG-04; CG-13
OPS-02 | OPS | Procedure and work control | MCF-OPS-005 Standard Operating Procedures; MCF-OPS-006 Method Statements; MCF-OPS-007 Permit to Work; MCF-OPS-008 Lockout and Tagout | CG-04; CG-14
OPS-03 | OPS | Maintenance and reliability | MCF-OPS-009 Maintenance Strategy; MCF-OPS-010 Condition Monitoring; MCF-OPS-011 Calibration; MCF-OPS-012 Deferred Maintenance
OPS-04 | OPS | Alarm, incident and problem management | MCF-OPS-013 Alarm Rationalisation; MCF-OPS-014 Incident Response; MCF-OPS-015 Root Cause Analysis; MCF-OPS-016 Problem Elimination | CG-07
OPS-05 | OPS | Change and configuration management | MCF-OPS-017 Configuration Baseline; MCF-OPS-018 Change Assessment; MCF-OPS-019 Temporary Configuration; MCF-OPS-020 Rollback and Validation | CG-14
OPS-06 | OPS | Capacity and service operations | MCF-OPS-021 Capacity Review; MCF-OPS-022 Service Level Monitoring; MCF-OPS-023 Resource Balancing; MCF-OPS-024 Operational Reporting
RES-01 | RES | Resilience strategy | MCF-RES-001 Minimum Service Outcome; MCF-RES-002 Graceful Degradation; MCF-RES-003 Resilience Scenarios; MCF-RES-004 Resilience Ownership
RES-02 | RES | Fault-domain and containment design | MCF-RES-005 Fault-Domain Definition; MCF-RES-006 Containment Boundaries; MCF-RES-007 Blast Radius; MCF-RES-008 Isolation Validation | CG-09
RES-03 | RES | Continuity planning | MCF-RES-009 Continuity Strategy; MCF-RES-010 Alternative Capacity; MCF-RES-011 Site and Provider Continuity; MCF-RES-012 Crisis Priorities
RES-04 | RES | Recovery planning | MCF-RES-013 Recovery Dependencies; MCF-RES-014 Recovery Sequencing; MCF-RES-015 Configuration Restoration; MCF-RES-016 Data and Checkpoint Recovery | CG-10
RES-05 | RES | Testing and exercising | MCF-RES-017 Component Tests; MCF-RES-018 Integrated Scenario Tests; MCF-RES-019 Tabletop Exercises; MCF-RES-020 Lessons and Retest | CG-10
RES-06 | RES | Crisis and adaptive response | MCF-RES-021 Crisis Command; MCF-RES-022 Stakeholder Communications; MCF-RES-023 Emergency Change; MCF-RES-024 Post-Event Adaptation
SUP-01 | SUP | Supplier due diligence | MCF-SUP-001 Supplier Capability; MCF-SUP-002 Financial and Operational Resilience; MCF-SUP-003 Security and Quality Posture; MCF-SUP-004 Sub-Tier Visibility | CG-03
SUP-02 | SUP | Contract and service obligations | MCF-SUP-005 Service Levels; MCF-SUP-006 Evidence Rights; MCF-SUP-007 Incident Notification; MCF-SUP-008 Exit and Transition Rights
SUP-03 | SUP | Hardware and component provenance | MCF-SUP-009 Approved Sourcing; MCF-SUP-010 Counterfeit Prevention; MCF-SUP-011 Chain of Custody; MCF-SUP-012 Component Traceability
SUP-04 | SUP | Software, firmware and update supply | MCF-SUP-013 Release Provenance; MCF-SUP-014 Signature Validation; MCF-SUP-015 Compatibility Assurance; MCF-SUP-016 Vulnerability Response
SUP-05 | SUP | Spares, logistics and obsolescence | MCF-SUP-017 Critical Spares; MCF-SUP-018 Lead Times; MCF-SUP-019 Logistics Continuity; MCF-SUP-020 End-of-Life Planning
SUP-06 | SUP | Remote support and third-party access | MCF-SUP-021 Support Identity; MCF-SUP-022 Activation and Approval; MCF-SUP-023 Session Monitoring; MCF-SUP-024 Revocation and Review | CG-15
SEC-01 | SEC | Identity and privileged access | MCF-SEC-001 Human Identity; MCF-SEC-002 Machine Identity; MCF-SEC-003 Privileged Access; MCF-SEC-004 Break-Glass Governance | CG-15
SEC-02 | SEC | Control-plane protection | MCF-SEC-005 BMS and EPMS Security; MCF-SEC-006 Cluster Manager Security; MCF-SEC-007 Fabric Controller Security; MCF-SEC-008 Storage Controller Security | CG-07; CG-15
SEC-03 | SEC | Network security and segmentation | MCF-SEC-009 Security Zoning; MCF-SEC-010 Management-Plane Segmentation; MCF-SEC-011 Filtering and Gateways; MCF-SEC-012 Remote Access | CG-07; CG-15
SEC-04 | SEC | Configuration, vulnerability and patching | MCF-SEC-013 Secure Baseline; MCF-SEC-014 Vulnerability Management; MCF-SEC-015 Patch Governance; MCF-SEC-016 Exception and Compensating Control
SEC-05 | SEC | Detection and response | MCF-SEC-017 Security Telemetry; MCF-SEC-018 Behaviour Detection; MCF-SEC-019 Incident Containment; MCF-SEC-020 Forensic Readiness
SEC-06 | SEC | AI-enabled and automated action | MCF-SEC-021 Agent or Automation Authority; MCF-SEC-022 Approval Controls; MCF-SEC-023 Command Allowlisting; MCF-SEC-024 Safe Rollback | CG-07; CG-15
EVA-01 | EVA | Evidence architecture | MCF-EVA-001 Evidence Taxonomy; MCF-EVA-002 Evidence Ownership; MCF-EVA-003 Evidence Repository; MCF-EVA-004 Retention and Protection
EVA-02 | EVA | Evidence provenance and quality | MCF-EVA-005 Source Provenance; MCF-EVA-006 Integrity and Custody; MCF-EVA-007 Relevance and Reliability; MCF-EVA-008 Currency and Coverage
EVA-03 | EVA | Assessment planning and execution | MCF-EVA-009 Decision Question; MCF-EVA-010 Scope and Criteria; MCF-EVA-011 Sampling and Testing; MCF-EVA-012 Specialist Involvement | CG-01; CG-02
EVA-04 | EVA | Findings, UNKNOWN and limitations | MCF-EVA-013 Finding Traceability; MCF-EVA-014 UNKNOWN Preservation; MCF-EVA-015 Conflict Handling; MCF-EVA-016 Limitation Disclosure
EVA-05 | EVA | Critical gates and decisions | MCF-EVA-017 Gate Applicability; MCF-EVA-018 Gate Evidence; MCF-EVA-019 Independent Decision; MCF-EVA-020 Claim Language
EVA-06 | EVA | Reassessment and continuing assurance | MCF-EVA-021 Evidence Expiry; MCF-EVA-022 Change Triggers; MCF-EVA-023 Monitoring Coverage; MCF-EVA-024 Decision Suspension and Supersession

## Control Registry
Control ID | Domain Code | Domain | Family ID | Control Family | Control Title | Control Objective | Normative Requirement | Assessment Criteria | Parameters | Minimum Evidence | Assessment Methods | Assessment Procedure | Control Type | Claim Type | Required Assurance Level | Lifecycle Stages | Operating States | Applicability | CRITICAL Gates | SUPPORTING Gates | Failure Modes | Ontology Classes | Testing Safety | UNKNOWN Rule | Informative References | Related Controls | Status | Version | Amendment ID
MCF-GOV-001 | GOV | Governance, Accountability and Assurance Direction | GOV-01 | Governance architecture | Governance Charter | Establish one approved charter that defines who directs, oversees and is accountable for assurance of each in-scope Capability Instance, which decision questions the programme serves, and the limits of reliance on AIDCF conclusions. | The governing body shall approve an assurance governance charter that names the in-scope Capability Instances, the accountable executive, the assurance programme lead, the decision authority and the oversight committee; states the decision questions served and the intended users of conclusions; defines the programme model (self-assessment, co-sourced, second-party or independent provider); and states that AIDCF conclusions do not replace engineering, statutory or safety approval and are not certification. The accountable executive shall review the charter at no more than the governance charter review interval and after any change of ownership, organisation or programme model, and shall record the outcome of each review. | 1) The charter in use is the approved version, and the approval was given by the governing body or by a body holding a documented delegation from it. 2) The charter names, by role and current incumbent, the accountable executive, assurance programme lead, decision authority and oversight committee. 3) Every Capability Instance recorded as in scope in the capability register (MCF-CAP-001) falls within the charter scope; no in-scope instance is uncovered. 4) The charter states the decision questions served, the intended users, the programme model and the non-substitution limits (no replacement of engineering, statutory or safety approval; no certification). 5) The charter defines the independence safeguards required before a material gate result or Assurance Decision is relied upon. 6) The most recent charter review is within the review interval and post-dates every charter trigger event (ownership, reorganisation, programme-model change). | Governance charter review interval [months] default 12 (Capability-profile parameter set by the governing body; illustrative, shortened where the capability is changing rapidly) | Approved governance charter with version identifier and effective date; Governing-body resolution or minute recording approval of that charter version; Delegation instrument where approval was given below the governing body; Reconciliation of charter scope to a dated extract of the capability register; Record of the most recent charter review and its outcome | DOCUMENT_REVIEW; INQUIRY; RECONCILIATION | 1) Obtain the charter in force and its approval record; confirm version identity and the authority of the approving body. 2) Reconcile the charter scope to a dated capability register extract and list any in-scope Capability Instance not covered. 3) Confirm the named roles against current appointment records. 4) Inspect the charter for decision questions, intended users, programme model, independence safeguards and non-substitution statements. 5) Interview the accountable executive to confirm their understanding of charter authority and the escalation route to the governing body. 6) Compare the last review date with the review interval and with trigger events since that review. | DIRECTIVE | DESIGN | AL2 | PLAN; DESIGN; OPERATE; CHANGE | NORMAL | Applies to every AIDCF assurance programme. For a single commissioned assessment, an engagement letter approved by the decision authority may satisfy the control if it contains the same content; full non-applicability is not permitted. |  | CG-13 | No approved authority exists for issuing assurance conclusions; Charter scope omits a Capability Instance that is reported on; AIDCF conclusion is represented as engineering approval or certification; Charter remains in force after the accountable executive has left | AssuranceProgram; CapabilityInstance; AssuranceDecision | Non-intrusive document review and interview only; no site or system testing. Governing-body papers can be commercially sensitive and are accessed through the evidence lead under the classification rules of AIDCF-008. | If the approval record cannot be produced, or the approving body's authority cannot be established, record a U1 or U6 UNKNOWN against the charter; approval shall not be inferred from the charter being in use. | ISO 37000 (governance of organizations); ISO/IEC 38500 (governance of IT for the organization); ISO/IEC/IEEE 15026-2 (assurance case); AIDCF-011 Assurance Program Framework | MCF-GOV-002; MCF-GOV-003; MCF-CAP-001; MCF-EVA-009 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-GOV-002 | GOV | Governance, Accountability and Assurance Direction | GOV-01 | Governance architecture | Decision Rights | Ensure that every consequential decision affecting the AI capability and its assurance (risk acceptance, gate disposition, Assurance Decision, emergency load action, test authorisation, exception approval) has a defined, delegated decision right that is used as designed, including in emergency states. | The accountable executive shall maintain a decision-rights matrix that, for each decision class affecting an in-scope Capability Instance, names the role holding the decision right, its financial or risk limits, the escalation route, the delegation and sub-delegation rules, and the emergency decision rights that apply when the normal holder is unavailable. The assurance programme lead shall ensure that workflow and approval systems enforce the matrix, and that every decision in the sample population was taken by a role holding the right at the time it was taken. | 1) A decision-rights matrix exists, is approved by the accountable executive and covers at minimum: risk acceptance, gate disposition, Assurance Decision issue, exception approval, hazardous test authorisation, and emergency load curtailment or shutdown of AI workloads. 2) Each decision class names a single holding role, limits, escalation route and the emergency alternate. 3) Approval workflows (change, exception, risk and decision registers) are configured so that only roles holding the right can approve the corresponding record type. 4) In a sample of decisions taken during the assessment period, every approver held the decision right and was within limits on the date of the decision. 5) Emergency decision rights are defined for EMERGENCY and RECOVERY states and at least one exercised or rehearsed emergency decision shows the alternate route was usable. 6) No decision in the sample was taken by an assessor on behalf of management. | Decision sample size per decision class [records] default 10 or the full population if smaller (Judgemental sample per AIDCF-008 sampling principles; illustrative, increased if exceptions are found) | Approved decision-rights matrix with version and approval record; Delegation and sub-delegation instruments in force during the period; Export of approver role configuration from change, exception, risk and decision workflow tools; Sampled decision records with approver identity, role and date; Emergency decision-right definition and record of its exercise or rehearsal | DOCUMENT_REVIEW; INSPECTION; SAMPLING; RECONCILIATION; INQUIRY | 1) Obtain the decision-rights matrix and confirm it covers the minimum decision classes, including emergency classes. 2) Extract approver role configuration from each workflow tool and reconcile it to the matrix; list roles able to approve without holding the right. 3) Define the population of decisions per class for the period and select a sample using the stated sample size. 4) For each sampled decision, verify approver identity, role held on that date and limits, against appointment and delegation records. 5) Review the emergency decision-right record and interview the emergency alternate on how they would exercise it. 6) Expand the sample by the same size again for any class where a nonconforming decision is found, and record the result. | PREVENTIVE | IMPLEMENTATION | AL3 | PLAN; OPERATE; CHANGE | NORMAL; EMERGENCY; RECOVERY | Applies to every in-scope Capability Instance. Decision classes that do not occur (for example no hazardous testing is permitted) may be marked NOT_APPLICABLE individually with rationale; the matrix as a whole is always applicable. | CG-13 |  | Unauthorised risk acceptance; Gate disposition or Assurance Decision issued by a role without authority; No one able to authorise emergency curtailment of AI load when the normal holder is unavailable; Workflow tool allows any user to approve; Assessor makes a management decision | AssuranceDecision; Action; ReviewRecord | Read-only extraction of workflow configuration under the tool owner's supervision; no test approvals are submitted in production systems. Emergency decision rights are examined by walkthrough or tabletop, never by declaring a real emergency. | If a workflow tool configuration cannot be extracted, or decisions cannot be tied to the approver's role on the date taken, record a U2 or U6 UNKNOWN; the decision class is treated as uncontrolled for CG-13 until resolved. | ISO 37000 (governance of organizations); COSO Internal Control - Integrated Framework; ISO/IEC 38500 (governance of IT for the organization) | MCF-GOV-001; MCF-GOV-005; MCF-GOV-007; MCF-EVA-019 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-GOV-003 | GOV | Governance, Accountability and Assurance Direction | GOV-01 | Governance architecture | Committee Oversight | Ensure that a standing oversight committee actually receives, challenges and acts on assurance information about the AI capability, including gate failures, critical UNKNOWN Records and overdue actions, at a frequency matched to the rate of change. | The governing body shall constitute an assurance oversight committee with written terms of reference, quorum and membership that includes at least one member independent of the operating line. The committee chair shall ensure that the committee meets at no more than the oversight meeting interval, receives at every meeting the current gate register, UNKNOWN register (US3 and above), findings register and overdue action list for each in-scope Capability Instance, records challenge and decisions in minutes, and tracks its own actions to closure. | 1) Terms of reference define purpose, membership, quorum, frequency, independence of at least one member, and escalation to the governing body. 2) Meetings were held at intervals not exceeding the oversight meeting interval throughout the assessment period and each was quorate. 3) Every meeting pack in the sample contained the current gate register, UNKNOWN register (US3 and above), findings register and overdue action list. 4) Minutes record challenge or questions on at least each gate FAIL and each US4/US5 UNKNOWN Record presented, and the decision or action taken. 5) Committee actions are tracked and closed with evidence, and overdue committee actions are escalated to the governing body. 6) Any gate FAIL or US4/US5 UNKNOWN Record arising between meetings was notified to the chair within the out-of-cycle notification time. | Oversight meeting interval [months] default 3 (Capability-profile parameter; illustrative, shortened during build, major change or after a gate FAIL) Out-of-cycle notification time for gate FAIL or US4/US5 UNKNOWN [working days] default 5 (Capability-profile parameter; illustrative) | Approved committee terms of reference; Meeting calendar and attendance records for the period; Sampled meeting packs with register extracts; Approved minutes and committee action log; Out-of-cycle notifications for gate FAIL or US4/US5 UNKNOWN events | DOCUMENT_REVIEW; SAMPLING; RECONCILIATION; INQUIRY | 1) Obtain terms of reference and confirm membership, quorum, independence and escalation provisions. 2) List all meetings in the period from the calendar and attendance records; test interval and quorum for each. 3) Select meeting packs and confirm the four mandatory registers were included and were current at the meeting date. 4) Reconcile gate FAIL and US4/US5 UNKNOWN Records in the gate and UNKNOWN registers to the minutes; identify any not presented or not challenged. 5) Trace committee actions to closure evidence and confirm escalation of overdue items. 6) Interview the chair and the independent member on how challenge is exercised and recorded. | DETECTIVE | OPERATION | AL4 | OPERATE; CHANGE | NORMAL | Applies to every programme where conclusions are relied upon beyond the immediate management team. For a single assessment with no continuing programme, review of the result by the decision authority may substitute, recorded as NOT_APPLICABLE with rationale. |  | CG-13 | Gate FAIL or critical UNKNOWN never reaches oversight; Committee receives scores only and no gate or UNKNOWN information; Oversight meets too infrequently for the rate of capability change; Committee actions are not tracked | AssuranceProgram; GateResult; UnknownRecord; Action; ReviewRecord | Document and interview review only. Observation of a live committee meeting requires the chair's prior consent and is confined to the agenda items concerning the in-scope capability. | If minutes for a meeting in the period are missing, record a U1 UNKNOWN for that meeting and do not count it as held; if more than one meeting in the period is affected, the criterion on meeting interval is not met. | ISO 37000 (governance of organizations); Institute of Internal Auditors Three Lines Model; AIDCF-012 Reporting and Assurance Statement Standard | MCF-GOV-001; MCF-GOV-015; MCF-EVA-014; MCF-EVA-013 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-GOV-004 | GOV | Governance, Accountability and Assurance Direction | GOV-01 | Governance architecture | Methodology Ownership | Ensure that the assessment methodology actually applied (AIDCF artifact versions, capability profile, scoring version, any local tailoring) has a named owner, is version-controlled, and is identical to the version declared in reports. | The assurance programme lead shall appoint a methodology owner who shall maintain a controlled methodology baseline listing the AIDCF artifact versions (including AIDCF-007A, AIDCF-008, AIDCF-009 and AIDCF-010), the capability profile, scoring version and every approved local tailoring, each with rationale and approval. The methodology owner shall ensure that assessment tools and templates are configured to that baseline and that every report declares the baseline version actually used. | 1) A methodology owner is appointed in writing and holds competence in AIDCF and assurance methods. 2) A controlled methodology baseline exists listing artifact versions, capability profile version, scoring version and approved tailorings with rationale and approver. 3) No tailoring weakens a critical-gate rule, an evidence floor or the UNKNOWN treatment of AIDCF-008 and AIDCF-010. 4) The control registry, vocabularies and scoring logic configured in the assessment tool match the declared baseline version (hash or version comparison). 5) Every report in the sample declares a baseline version, and that version was the one in force on the assessment date. |  | Methodology owner appointment record; Methodology baseline record with versions, tailorings, rationale and approvals; Tool configuration export showing registry, vocabulary and scoring versions; Sampled reports with declared methodology baseline | DOCUMENT_REVIEW; RECONCILIATION; INSPECTION; SAMPLING | 1) Confirm the methodology owner appointment and competence record. 2) Review the methodology baseline and each tailoring; test each tailoring against gate rules, evidence floors and UNKNOWN treatment. 3) Extract registry, vocabulary and scoring versions from the assessment tool and compare them with the release manifest of the declared baseline. 4) Sample issued reports and compare the declared baseline with the baseline in force on each assessment date. 5) Record any divergence as a Finding and identify affected results. | DIRECTIVE | IMPLEMENTATION | AL3 | PLAN; OPERATE; CHANGE | NORMAL | Applies to every programme that issues AIDCF control, gate or decision results. |  |  | Results produced under an undeclared or superseded control registry; Local tailoring silently weakens a gate or evidence floor; Scoring version in tool differs from the version reported; No one accountable for methodology changes | AssuranceProgram; ReleaseManifest; AssessmentProcedure; ScoreSnapshot | Read-only inspection of tool configuration in a non-production or export copy; no change to scoring logic is made during assessment. | If the tool configuration cannot be compared with a release manifest, record a U8 (method uncertain) UNKNOWN against every result produced with that tool in the period. | ISO/IEC/IEEE 15026-2 (assurance case); ISO 9001 (quality management systems) - control of documented information; AIDCF-014 End-to-End Traceability and Machine-Executable Data Standard | MCF-GOV-012; MCF-GOV-013; MCF-EVA-001; MCF-EVA-020 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-GOV-005 | GOV | Governance, Accountability and Assurance Direction | GOV-02 | Accountability and responsibility | RACI and Role Ownership | Ensure that every role named in the assurance programme and in operation of the AI capability has a current incumbent, a defined RACI position for each process, and no unresolved overlap or gap between owner, operator and providers. | The accountable executive shall maintain a RACI that assigns, for each in-scope process (capability management, assurance, evidence, change, incident, recovery, provider management), exactly one Accountable role and the Responsible, Consulted and Informed roles across owner, operator, tenants and providers. The assurance programme lead shall reconcile the RACI to current appointments and to contractual responsibility clauses at least at the RACI reconciliation interval and after every organisational or contract change. | 1) The RACI covers every in-scope process and assigns exactly one Accountable role to each. 2) Every role in the RACI has a named current incumbent and a deputy. 3) RACI assignments for providers and tenants match the responsibility clauses of the corresponding contracts or service descriptions. 4) No process has a responsibility split between owner, operator and provider that leaves an activity with no Responsible role. 5) Reconciliation to appointments and contracts occurred within the reconciliation interval and after each trigger event. 6) Interviewed role holders describe their RACI position consistently with the document. | RACI reconciliation interval [months] default 6 (Capability-profile parameter; illustrative) | Approved RACI with version; Current appointment or HR role extract for named roles; Responsibility clauses of operator, provider and tenant contracts; RACI reconciliation record; Interview notes from sampled role holders | DOCUMENT_REVIEW; RECONCILIATION; INQUIRY; ANALYSIS | 1) Obtain the RACI and confirm each in-scope process has exactly one Accountable role. 2) Reconcile named roles to current appointment records and identify vacancies or missing deputies. 3) Reconcile provider and tenant assignments to contractual responsibility clauses and list gaps or conflicts. 4) Analyse each process for activities with no Responsible role at owner/operator/provider interfaces. 5) Interview a sample of Accountable and Responsible role holders, including at least one provider role, and compare their description with the RACI. | DIRECTIVE | IMPLEMENTATION | AL3 | PLAN; BUILD; OPERATE; CHANGE | NORMAL; MAINTENANCE; EMERGENCY | Applies to every in-scope Capability Instance. Where the owner and operator are the same organisation, the owner/operator interface criteria are evaluated within the organisation. | CG-13 |  | Two parties each believe the other is responsible for an activity; Accountable role vacant; Provider contract assigns responsibility differently from the RACI; No deputy for an Accountable role during an emergency | CapabilityInstance; RequiredFunction; Dependency; Action | Interview and document review only. Provider contract extracts may be commercially restricted; where access is limited, only responsibility clauses are disclosed under the evidence lead's restriction record. | If a provider or tenant contract cannot be accessed to confirm responsibility clauses, record a U2 UNKNOWN for that interface; it shall not be assumed that the provider is responsible. | ISO/IEC 20000-1 (service management system); ISO 37000 (governance of organizations); ISO/IEC 22237 series (data centre facilities and infrastructures) - management and operational information | MCF-GOV-006; MCF-GOV-002; MCF-CAP-002 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-GOV-006 | GOV | Governance, Accountability and Assurance Direction | GOV-02 | Accountability and responsibility | Critical Function Accountability | Ensure that every Required Function and material Dependency supporting an in-scope Service Outcome (power, cooling, compute, storage, network, control plane, external providers) has one accountable owner with authority to act, recorded in the assurance graph. | The capability owner shall ensure that each Required Function and each material Dependency linked to an in-scope Service Outcome has exactly one accountable owner recorded in the assurance graph, that the owner holds the decision right to commit resources and to authorise degraded-state actions for that function, and that cross-organisational functions (for example utility supply, facility water, network carriers, cloud control planes) have both an internal accountable owner and a named counterparty contact. The assurance programme lead shall reconcile function ownership to the RACI and decision-rights matrix after every change to the Required Function or Dependency set. | 1) Every Required Function and material Dependency in the assurance graph linked to an in-scope Service Outcome has exactly one accountable owner. 2) Each owner holds, in the decision-rights matrix, the right to commit resources and to authorise degraded-state actions for that function. 3) Each external or cross-organisational Dependency has an internal accountable owner and a named counterparty contact with a verified contact route. 4) Function ownership in the graph reconciles to the RACI and decision-rights matrix with no conflicts. 5) Ownership was reconciled after each addition, removal or change of a Required Function or Dependency in the period. |  | Assurance graph extract of Required Functions and Dependencies with owner attributes; RACI and decision-rights matrix extracts; Counterparty contact register with last verification date; Reconciliation record after each function or dependency change | ANALYSIS; RECONCILIATION; DOCUMENT_REVIEW; INQUIRY | 1) Query the assurance graph for all Required Functions and material Dependencies linked to in-scope Service Outcomes and their owner attributes. 2) Identify functions or dependencies with zero or more than one accountable owner. 3) Reconcile each owner to the decision-rights matrix for authority to commit resources and authorise degraded-state actions. 4) Test the counterparty contact route for a sample of external dependencies by confirming the last successful verification. 5) Interview a sample of owners, prioritising shared or external dependencies, on their authority and escalation in a degraded state. | DIRECTIVE | IMPLEMENTATION | AL3 | DESIGN; BUILD; OPERATE; CHANGE | NORMAL; DEGRADED; EMERGENCY; RECOVERY | Applies to every Required Function and material Dependency supporting an in-scope Service Outcome; dependencies assessed as non-material in the DEP domain are excluded with that rationale. | CG-13 | CG-03 | Shared facility water loop has no single accountable owner across facility and IT teams; External carrier dependency has no internal owner; Owner lacks authority to authorise load shedding during a cooling degradation; Ownership not updated after a provider change | RequiredFunction; Dependency; ServiceOutcome; CapabilityInstance | Graph queries are executed read-only. Contact-route verification uses existing records or a pre-agreed non-operational test message; it shall not simulate an incident to a provider. | Any Required Function or material Dependency whose owner cannot be established is recorded as a US4 UNKNOWN Record against CG-13; ownership shall not be presumed from organisational proximity. | ISO 22301 (business continuity management systems); ISO 55000 series (asset management); AIDCF-005 AIDCF-AI Trust Graph Integration Standard | MCF-GOV-005; MCF-CAP-002; MCF-CAP-004; MCF-GOV-002 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-GOV-007 | GOV | Governance, Accountability and Assurance Direction | GOV-02 | Accountability and responsibility | Risk Acceptance Authority | Ensure that residual risks, Findings left open and conditions attached to decisions are accepted only by a role holding risk-acceptance authority for that magnitude, with an expiry and review, and never by assessors. | The accountable executive shall define risk-acceptance authority levels linked to the risk appetite (MCF-GOV-014) and impact tolerances (MCF-CAP-010). Each risk owner shall record every risk acceptance with the risk description, affected Service Outcomes and gates, residual consequence, compensating measures, acceptor, expiry date and review date. The assurance programme lead shall ensure that no acceptance of a risk that would cause a CRITICAL control or gate to be relied upon is recorded without the decision authority's approval, and that expired acceptances revert to open Findings. | 1) Risk-acceptance authority levels are defined and linked to risk appetite and impact tolerance. 2) Every risk acceptance in the sample was made by a role holding authority for its magnitude on the date of acceptance. 3) Every acceptance records affected Service Outcomes and gates, residual consequence, compensating measures, expiry and review date. 4) No acceptance has passed its expiry date without renewal by an authorised acceptor or reversion to an open Finding. 5) No acceptance in the population was made or recommended for acceptance by an assessor. 6) No acceptance is used to convert a gate FAIL or US4/US5 UNKNOWN into PASS; such risks appear only as decision-level conditions. | Maximum risk-acceptance validity [months] default 12 (Capability-profile parameter; illustrative, shorter for acceptances touching gate-critical controls) | Risk-acceptance authority schedule; Risk register extract of acceptances in the period; Sampled acceptance records with acceptor role and date; Register of expired acceptances and their disposition | SAMPLING; DOCUMENT_REVIEW; RECONCILIATION; ANALYSIS | 1) Obtain the authority schedule and confirm linkage to risk appetite and impact tolerance. 2) Extract the full population of acceptances active during the period and select a sample weighted to acceptances touching gate-critical controls. 3) For each sampled acceptance, verify acceptor authority on the date, completeness of required fields and expiry status. 4) Analyse the population for expired acceptances not renewed or reverted, and for acceptances used to clear a gate FAIL or US4/US5 UNKNOWN. 5) Confirm from engagement records that no assessor made or recommended an acceptance. | PREVENTIVE | OPERATION | AL4 | OPERATE; CHANGE | NORMAL; DEGRADED; MAINTENANCE | Applies whenever any residual risk, open Finding or decision condition is accepted for an in-scope Capability Instance. | CG-13 |  | Risk accepted by an operator below the authority threshold; Indefinite risk acceptance with no expiry; Gate FAIL hidden by a risk acceptance; Assessor accepts risk on management's behalf | Finding; Action; AssuranceDecision; GateResult | Document and register review only; no operational activity. | If the acceptor's authority on the acceptance date cannot be established, record a U6 UNKNOWN and treat the acceptance as not made; the underlying Finding is reported as open. | ISO 31000 (risk management guidelines); COSO Enterprise Risk Management framework; ISO 37000 (governance of organizations) | MCF-GOV-014; MCF-CAP-010; MCF-GOV-011; MCF-GOV-002 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-GOV-008 | GOV | Governance, Accountability and Assurance Direction | GOV-02 | Accountability and responsibility | Evidence Custody | Assign accountable custody for assurance evidence so that every Evidence Object relied on by a decision has a custodian, an access policy and an unbroken custody record from collection to retention or destruction. | The assurance programme lead shall appoint an evidence lead who shall assign a custodian role to each evidence repository and each Evidence Package, define who may read, add, alter, export, redact or destroy evidence, and ensure that every custody event defined in AIDCF-008 (transfer, access, export, alteration, redaction, retention action) is recorded. The evidence lead shall review custody records for Evidence Packages supporting gate results before each Assurance Decision is issued. | 1) An evidence lead is appointed and each repository and Evidence Package supporting a gate or decision has a named custodian. 2) Access policies define permitted actions per role and are configured in the repository so that alteration and destruction are restricted to authorised roles. 3) For a sample of Evidence Objects supporting gate results, the custody log is complete from collection to current state with no unexplained gap. 4) Custody review of gate-supporting Evidence Packages was performed before each Assurance Decision in the period. 5) Transfers of evidence to or from providers are recorded with sender, receiver, method, time and integrity value. |  | Evidence lead appointment and custodian register; Repository access policy and role configuration export; Custody logs for sampled Evidence Objects; Pre-decision custody review records; Provider evidence transfer records | INSPECTION; SAMPLING; RECONCILIATION; DOCUMENT_REVIEW | 1) Confirm evidence lead appointment and custodian assignment for each repository and gate-supporting package. 2) Extract role configuration and compare with the access policy; list roles able to alter or destroy evidence without authority. 3) Sample Evidence Objects supporting gate results and trace custody logs from collection to current state. 4) Verify pre-decision custody reviews for each decision in the period. 5) Trace a sample of provider evidence transfers and confirm integrity values were recorded and verified on receipt. | PREVENTIVE | OPERATION | AL4 | PLAN; OPERATE; DECOMMISSION | NORMAL | Applies to all evidence relied on for control, gate or decision results. Operational records retained only in source systems are within scope when cited as evidence. |  | CG-13 | Evidence altered after collection with no record; No custodian for provider-supplied test reports; Evidence destroyed before decision challenge period ends; Shared accounts used to upload evidence | EvidenceObject; EvidencePackage; DistributionControl | Read-only inspection of repository configuration and logs. Any test of access restrictions uses a dedicated test account and test object approved by the evidence lead; production evidence is never altered. | If custody logs are absent for a period or object, record a U7 UNKNOWN against the affected Evidence Objects; they may not be used to support a gate result until integrity is re-established by re-collection or independent corroboration. | ISO/IEC 27037 (identification, collection, acquisition and preservation of digital evidence); ISO 15489-1 (records management); AIDCF-008 Evidence Model | MCF-EVA-002; MCF-EVA-006; MCF-EVA-004; MCF-EVA-003 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-GOV-009 | GOV | Governance, Accountability and Assurance Direction | GOV-03 | Policy and standards management | Policy Hierarchy | Ensure that policies, technical standards, procedures and runbooks governing the AI capability form a coherent hierarchy in which each lower document traces to a higher one and contradictions are identified and resolved. | The policy owner shall maintain a policy hierarchy register that identifies, for each in-scope document, its level (policy, standard, procedure, runbook), parent document, owner, scope (sites, halls, clusters, systems) and approval status. The policy owner shall ensure that no procedure or runbook relies on a superseded or absent parent, and that identified contradictions between documents are recorded and resolved by the owner of the higher document. | 1) A register exists listing each in-scope policy, standard, procedure and runbook with level, parent, owner, scope and approval status. 2) Every document below policy level traces to an approved, current parent. 3) Policy-level documents cover at minimum assurance, risk, change, incident, safety of work, information security, evidence and provider management for the in-scope capability. 4) Contradictions identified in the period (including those found by the assessor in a sample comparison) are recorded and resolved by the higher-document owner. 5) Scopes declared in documents cover all in-scope sites, halls and clusters without gaps. |  | Policy hierarchy register; Approved policy-level documents; Sample of standards, procedures and runbooks with parent references; Contradiction log and resolution records | DOCUMENT_REVIEW; ANALYSIS; RECONCILIATION | 1) Obtain the register and confirm completeness against the document management system. 2) Check that minimum policy topics are covered for the in-scope capability. 3) Trace a sample of procedures and runbooks, prioritising emergency and recovery runbooks, to approved current parents. 4) Compare a sample of document pairs at adjacent levels for contradictions in requirements, roles or limits. 5) Reconcile declared document scopes to the capability register and identify uncovered sites, halls or clusters. | DIRECTIVE | DESIGN | AL2 | PLAN; DESIGN; OPERATE | NORMAL | Applies to every organisation operating or assuring an in-scope Capability Instance; for providers, applies to documents the provider makes available under contract. |  |  | Runbook traces to a superseded standard; Contradictory limits in procedure and standard; No policy covering evidence or provider management; New cluster not covered by any operating procedure | Control; ControlDomain; CapabilityInstance | Document review only; no runbook is exercised. Emergency runbooks are read in the document system, not at operational consoles. | If a document cited as parent cannot be produced, record a U1 UNKNOWN against the child document and treat the child as untraced. | ISO 9001 (quality management systems); ISO/IEC 27001 (information security management systems); ISO 37301 (compliance management systems) | MCF-GOV-010; MCF-GOV-012; MCF-GOV-011 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-GOV-010 | GOV | Governance, Accountability and Assurance Direction | GOV-03 | Policy and standards management | Technical Standard Baselines | Ensure that the engineering and technical standards baseline the capability is designed, built and operated against (electrical, mechanical, fire, OT security, accelerator platform, network and storage standards and vendor envelopes) is declared, versioned and actually applied to the as-built and as-configured state. | The chief engineer for the capability shall declare a technical standards baseline listing each external standard family, internal engineering standard and OEM specification applied to in-scope infrastructure, with edition or version, scope of application and any declared deviation. The chief engineer shall ensure that design, commissioning and change records cite the baseline edition applied, and that adoption of a new edition is controlled through change control with impact assessment. | 1) A technical standards baseline lists the standards, internal engineering standards and OEM specifications applied, with edition, scope and deviations. 2) The baseline covers each infrastructure domain in scope (power, thermal, physical, compute, storage, network, OT and control-plane security). 3) Design and commissioning records in a sample cite the baseline edition applied. 4) Each declared deviation has a rationale, a compensating measure and approval through exception governance (MCF-GOV-011). 5) Adoption of new editions or OEM specification revisions in the period was processed through change control with impact assessment. |  | Technical standards baseline with editions and scope; Sampled design and commissioning records citing the baseline; Deviation register entries with approvals; Change records for edition adoption | DOCUMENT_REVIEW; RECONCILIATION; SAMPLING; INQUIRY | 1) Obtain the baseline and confirm coverage of each in-scope infrastructure domain. 2) Ask each domain specialist to confirm that listed standard families are applicable and complete for their domain. 3) Sample design and commissioning records and verify citation of the baseline edition. 4) Trace deviations to approved exceptions and confirm compensating measures. 5) Trace edition adoptions in the period to change records with impact assessment. | DIRECTIVE | IMPLEMENTATION | AL3 | DESIGN; BUILD; COMMISSION; CHANGE | NORMAL | Applies to all in-scope infrastructure. Where a colocation provider owns the facility baseline, the provider's baseline is assessed through MCF-SUP controls and referenced here. |  | CG-14 | Design built against an undeclared standard edition; OEM thermal or power envelope revision not reflected in design; Undocumented deviation from an applied standard; New technology deployed with no applicable standard declared | ArchitectureSnapshot; InfrastructureSystem; Control | Document review only; no inspection of energised equipment is required for this control. | If the edition applied to a design cannot be determined, record a U8 UNKNOWN against the affected DESIGN claims in the relevant infrastructure domain. | ISO/IEC 22237 series (data centre facilities and infrastructures); EN 50600 series (data centre facilities and infrastructures); ASHRAE TC 9.9 thermal guidelines for data processing environments; IEC 62443 series (industrial automation and control systems security) | MCF-GOV-009; MCF-GOV-011; MCF-CAP-021 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-GOV-011 | GOV | Governance, Accountability and Assurance Direction | GOV-03 | Policy and standards management | Exception Governance | Ensure that every deviation from policy, technical baseline or control requirement is recorded, risk-assessed, approved by an authorised role, time-bound and visible in assurance reporting, so that exceptions do not silently accumulate into an unassessed configuration. | The policy owner shall operate an exception process in which each exception records the requirement deviated from, affected Capability Instances, Service Outcomes, controls and gates, the risk assessment, compensating measures, approver, expiry and closure criteria. Exceptions affecting a gate-critical control shall be approved by the decision authority. The assurance programme lead shall ensure that the exception register is an input to every assessment and that expired exceptions are escalated to the oversight committee. | 1) Every exception in the sample records the deviated requirement, affected scope, controls and gates, risk assessment, compensating measures, approver, expiry and closure criteria. 2) Exceptions affecting gate-critical controls were approved by the decision authority. 3) No exception in the register is past expiry without renewal or closure; expired exceptions were escalated to the oversight committee. 4) The exception register was used as an input to each assessment in the period and affected controls reference the relevant exceptions. 5) Configuration or practice found by the assessor to deviate from a requirement has a corresponding exception or is raised as a Finding. | Maximum exception duration [months] default 6 (Capability-profile parameter; illustrative, renewable once by the approver) | Exception register extract for the period; Sampled exception records with approvals; Oversight committee records of expired-exception escalation; Assessment planning records citing the exception register | SAMPLING; DOCUMENT_REVIEW; RECONCILIATION; ANALYSIS | 1) Extract the exception register for the period and analyse expiry status across the population. 2) Sample exceptions, weighting toward gate-critical controls, and test completeness and approver authority. 3) Confirm escalation of expired exceptions in oversight committee records. 4) Reconcile deviations observed in other domain assessments to the register and raise Findings for undeclared deviations. 5) Confirm that the assessment plan and affected control assessments reference active exceptions. | PREVENTIVE | OPERATION | AL4 | OPERATE; CHANGE | NORMAL; MAINTENANCE; DEGRADED | Applies to every in-scope Capability Instance. If no exceptions exist, the control is still assessed by testing for undeclared deviations. |  | CG-14; CG-13 | Temporary bypass of a protection or interlock left in place indefinitely; Exceptions approved by the requester; Exception register not used in assessment, so results ignore known deviations; Accumulated exceptions create an unassessed configuration | Finding; Control; Action; ArchitectureSnapshot | Register review only. Where the assessor verifies a deviation in a live system, it is by read-only inspection with the system owner present. | If the existence of undeclared deviations cannot be tested for a domain (for example configuration not accessible), record a U5 coverage-gap UNKNOWN for that domain against this control. | ISO 37301 (compliance management systems); ISO/IEC 27001 (information security management systems); ISO 31000 (risk management guidelines) | MCF-GOV-007; MCF-GOV-010; MCF-CAP-023 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-GOV-012 | GOV | Governance, Accountability and Assurance Direction | GOV-03 | Policy and standards management | Document Lifecycle | Ensure that documents used to operate and assure the capability are controlled through creation, review, approval, publication, supersession and withdrawal, so that the version at the point of use is the approved current version. | The policy owner shall define document lifecycle states, review intervals by document level and approval roles, and the document control administrator shall ensure that only approved current versions are published at points of use (control room, plant rooms, runbook systems, assessor workpaper templates), that superseded versions are withdrawn from points of use while retained in history, and that review dates are tracked. | 1) Lifecycle states, review intervals by document level and approval roles are defined. 2) At a sample of points of use (including control room and runbook system), the version available is the approved current version. 3) Superseded documents are withdrawn from points of use and retained in history with supersession metadata. 4) No document in the sample is past its review date without a recorded extension. 5) Emergency and recovery runbooks are available at the point of use in a form usable during loss of the primary document system. | Runbook review interval [months] default 12 (Capability-profile parameter; illustrative, shorter for emergency runbooks after change) | Document control procedure; Document management system version and status export; Point-of-use inspection record; Offline or alternate runbook availability record | INSPECTION; SAMPLING; RECONCILIATION | 1) Obtain the document control procedure and confirm lifecycle states, review intervals and approval roles. 2) Select points of use, including the control room and runbook system, and compare available versions with the document management system. 3) Check that superseded versions are absent at points of use and present in history. 4) Test review dates on a sample of documents. 5) Inspect alternate availability of emergency and recovery runbooks for loss of the primary document system. | PREVENTIVE | IMPLEMENTATION | AL3 | BUILD; OPERATE; CHANGE | NORMAL; EMERGENCY; RECOVERY | Applies to all controlled documents used to operate or assure in-scope infrastructure. |  | CG-14 | Operator executes a superseded switching or cooling procedure; Emergency runbook unavailable when the document system is down; Assessor uses a superseded template; Review dates lapse unnoticed | EvidenceObject; AssessmentProcedure; ReleaseManifest | Point-of-use inspection in control rooms and plant rooms is escorted, follows site induction and access rules, and does not involve touching operational equipment. | If the version at a point of use cannot be compared with the system of record, record a U6 UNKNOWN for that point of use. | ISO 9001 (quality management systems) - control of documented information; ISO 15489-1 (records management); ISO/IEC 20000-1 (service management system) | MCF-GOV-009; MCF-GOV-004; MCF-EVA-021 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-GOV-013 | GOV | Governance, Accountability and Assurance Direction | GOV-04 | Risk and assurance governance | Assurance Plan | Ensure that a risk-based assurance plan determines which Capability Instances, Service Outcomes, claim types and gates are assessed, at what Assurance Level, by whom and when, so that assurance effort follows consequence and change rather than convenience. | The assurance programme lead shall prepare, and the oversight committee shall approve, an assurance plan for each planning period that, for each in-scope Capability Instance, states the decision questions, target Assurance Level (AL0-AL6), claim types and gates to be evaluated, assessment type, provider model, resourcing and schedule, and the rationale linking depth to criticality (MCF-CAP-009) and planned change (MCF-CAP-023). The programme lead shall record and approve deviations from the plan. | 1) An approved assurance plan exists for the current period. 2) For each in-scope Capability Instance the plan states decision questions, target Assurance Level, claim types, gates, assessment type, provider model and schedule. 3) Planned depth is justified by criticality classification and planned material change; higher-criticality instances are not planned at a lower Assurance Level than lower-criticality instances without rationale. 4) Gates CG-01 to CG-15 are each planned for evaluation or recorded as APPROVED_NA with boundary rationale for each instance. 5) Deviations from the plan in the period are recorded and approved. | Assurance planning period [months] default 12 (Programme parameter; illustrative) | Approved assurance plan; Criticality classification extract; Planned change schedule used for planning; Plan deviation records | DOCUMENT_REVIEW; ANALYSIS; RECONCILIATION | 1) Obtain the approved plan and approval record. 2) Reconcile plan coverage to the capability register and criticality classification. 3) Analyse planned depth against criticality and planned change; identify inversions. 4) Confirm each gate is planned or recorded as APPROVED_NA with rationale. 5) Review plan deviations and their approvals. | DIRECTIVE | DESIGN | AL2 | PLAN; OPERATE; CHANGE | NORMAL | Applies to continuing programmes. For a one-off assessment the engagement plan satisfies the control. |  |  | Low-consequence systems assessed deeply while critical ones are not; Gates omitted from plan without rationale; Planned change not reflected in assurance schedule; Plan never approved | AssuranceProgram; Assessment; CriticalGate; CapabilityInstance | Desk review of planning records only; draft plans for future periods are treated as confidential programme information. | If criticality classification is unavailable, record a U1 UNKNOWN against this control and the depth-justification criterion is not met. | ISO 19011 (guidelines for auditing management systems); ISAE 3000 (assurance engagements other than audits or reviews of historical financial information); AIDCF-011 Assurance Program Framework | MCF-GOV-014; MCF-CAP-009; MCF-EVA-010; MCF-GOV-015 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-GOV-014 | GOV | Governance, Accountability and Assurance Direction | GOV-04 | Risk and assurance governance | Risk Appetite Linkage | Ensure that the organisation's stated risk appetite is translated into measurable limits for the AI capability (for example tolerated outcome interruption, tolerated loss of training progress, tolerated degraded-state duration) that drive impact tolerances, risk acceptance and decision conditions. | The governing body shall approve a risk appetite statement covering service continuity, safety, data integrity and dependency concentration for the AI capability. The accountable executive shall translate it into measurable appetite limits per Service Outcome class and shall demonstrate that impact tolerances (MCF-CAP-010), risk-acceptance authority (MCF-GOV-007) and decision condition rules reference those limits. | 1) A risk appetite statement covering service continuity, safety, data integrity and concentration is approved by the governing body. 2) Appetite is expressed as measurable limits per Service Outcome class, with units. 3) Each impact tolerance in the capability profile is at or within the corresponding appetite limit, or the exceedance is approved by the governing body. 4) Risk-acceptance authority levels reference appetite limits. 5) Zero appetite for life-safety risk is stated and is not subject to risk acceptance below the governing body. |  | Approved risk appetite statement; Appetite limits schedule per Service Outcome class; Reconciliation of impact tolerances to appetite limits; Risk-acceptance authority schedule | DOCUMENT_REVIEW; RECONCILIATION; INQUIRY | 1) Obtain the approved risk appetite statement and confirm coverage of the four topics. 2) Confirm measurable limits with units per Service Outcome class. 3) Reconcile each impact tolerance to the appetite limit and identify unapproved exceedances. 4) Confirm risk-acceptance authority levels reference appetite limits and that life-safety risk is excluded from delegated acceptance. 5) Interview the accountable executive on how appetite is used in decision conditions. | DIRECTIVE | DESIGN | AL2 | PLAN; DESIGN | NORMAL | Applies to every organisation that owns an in-scope Capability Instance. Providers are not required to share their own appetite. |  |  | Impact tolerances set without reference to governed appetite; Appetite expressed only qualitatively; Life-safety risk accepted operationally; Concentration risk absent from appetite | ServiceOutcome; CapabilityInstance; AssuranceDecision | Desk review only. Risk appetite statements are board-confidential and are viewed in a read-only data room where the organisation requires it. | If appetite is stated only qualitatively, the measurable-limit criterion is not met (PARTIAL), not UNKNOWN; UNKNOWN is recorded only if the approved statement itself cannot be produced. | ISO 31000 (risk management guidelines); COSO Enterprise Risk Management framework; ISO 22301 (business continuity management systems) | MCF-GOV-007; MCF-CAP-010; MCF-CAP-011 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-GOV-015 | GOV | Governance, Accountability and Assurance Direction | GOV-04 | Risk and assurance governance | Critical Gate Governance | Ensure that critical gates are evaluated, disposed and reported under governance that prevents them from being averaged away, re-scoped or overridden, and that every FAIL or UNKNOWN Gate Result reaches the decision authority with its controlling effect. | The decision authority shall maintain a gate register for each in-scope Capability Instance recording, for every gate CG-01 to CG-15, applicability, CRITICAL control results, evidence sufficiency against the gate floor, Gate Result, controlling effect on the decision and closure criteria. The assurance programme lead shall ensure that Gate Results are computed by the roll-up rule of AIDCF-010, that no Gate Result is changed except by reassessment, and that APPROVED_NA is granted only by the decision authority with a boundary rationale. | 1) A gate register exists for each in-scope Capability Instance covering all fifteen gates. 2) In a sample of assessments, each recorded Gate Result reproduces when the AIDCF-010 roll-up rule is reapplied to the recorded CRITICAL control results and gate evidence. 3) Every APPROVED_NA was granted by the decision authority with a boundary rationale. 4) No Gate Result in the register history was changed without a corresponding reassessment record. 5) Every FAIL or UNKNOWN Gate Result appears with its controlling effect in the decision record and on the first page of the executive report. 6) No decision in the sample was issued at a state above the ceiling implied by its Gate Results. |  | Gate register with history; Assessment records with CRITICAL control results and gate evidence; APPROVED_NA approvals; Decision records and executive reports for sampled assessments | REPERFORMANCE; SAMPLING; RECONCILIATION; DOCUMENT_REVIEW | 1) Obtain the gate register and confirm all fifteen gates are recorded per Capability Instance. 2) Select assessments and reapply the AIDCF-010 roll-up rule to the recorded CRITICAL control results and evidence sufficiency. 3) Compare reperformed Gate Results with recorded results and investigate differences. 4) Review APPROVED_NA approvals and register history for changes without reassessment. 5) Trace FAIL and UNKNOWN Gate Results to decision records and executive reports; test decision state against the gate ceiling. | PREVENTIVE | OPERATION | AL4 | OPERATE; CHANGE | NORMAL | Applies to every programme issuing Assurance Decisions. |  | CG-13 | Gate FAIL offset by a high domain score; Gate marked APPROVED_NA to avoid failure; Gate Result edited after review; Critical UNKNOWN omitted from executive report | CriticalGate; GateResult; AssuranceDecision; AssuranceReport | Reperformance uses exported records; no change is made to the system of record. | If the CRITICAL control results underlying a Gate Result cannot be retrieved, record a U1 UNKNOWN against that Gate Result and treat the reperformance criterion as not met for that assessment. | ISO/IEC/IEEE 15026-2 (assurance case); AIDCF-010 Scoring and Decision Framework; AIDCF-012 Reporting and Assurance Statement Standard | MCF-EVA-017; MCF-EVA-018; MCF-GOV-003; MCF-EVA-019 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-GOV-016 | GOV | Governance, Accountability and Assurance Direction | GOV-04 | Risk and assurance governance | Independent Review | Ensure that a competent reviewer independent of the assessment team challenges method, evidence, gates, UNKNOWN treatment and decision wording before material conclusions are relied upon, and that the review demonstrably detects errors. | The assurance programme lead shall ensure that every Assurance Decision supporting a material decision question is subject, before issue, to independent review by a reviewer who did not prepare or perform the assessment, has no conflict under MCF-GOV-021 and holds the competence defined in MCF-GOV-023. The independent reviewer shall record challenges, responses and dispositions, and shall have authority to withhold their concurrence. The programme lead shall periodically test review effectiveness by reperformance or by seeded-defect review. | 1) Every material Assurance Decision in the period has an independent review record dated before issue. 2) Each reviewer is independent of preparation and performance, conflict-free and competent for the domains reviewed. 3) Review records show challenge to method, evidence sufficiency, Gate Results, UNKNOWN treatment and decision wording, with dispositions. 4) No decision was issued over a withheld concurrence without escalation to the governing body or oversight committee. 5) Review effectiveness was tested in the period (reperformance of a completed review or seeded-defect exercise), and the test detected at least the defects the review was expected to detect, or the shortfall was addressed. | Review effectiveness test frequency [tests per year] default 1 (Programme parameter; illustrative) | Independent review records for each material decision; Reviewer independence and competence declarations; Withheld-concurrence escalation records; Review effectiveness test record with seeded defects and detection outcome | DOCUMENT_REVIEW; REPERFORMANCE; TEST; INQUIRY | 1) List material decisions in the period and match each to a review record dated before issue. 2) Verify reviewer independence and competence declarations against engagement records and the competence register. 3) Examine review records for challenge across the five topics and for dispositions. 4) Check for decisions issued over withheld concurrence and their escalation. 5) Examine the review effectiveness test design, seeded defects and detection results; where no test exists, reperform one completed review and compare findings. | DETECTIVE | EFFECTIVENESS | AL5 | OPERATE | NORMAL | Applies to Assurance Decisions relied on for material decision questions or by intended users beyond the management team. Internal-only diagnostic assessments at AL0-AL1 are excluded. |  | CG-13 | Reviewer from the same team as the assessor; Review performed after issue; Review signs off without challenge; Reviewer lacks competence in the domain where the decisive gate sits | ReviewRecord; AssuranceDecision; DecisionRecommendation | Seeded-defect tests use copies of closed engagements with synthetic defects clearly labelled; they are never introduced into live engagements or live reports. | If a review record exists but its date relative to issue cannot be established, record a U7 UNKNOWN and treat the decision as not independently reviewed for this control. | ISO 19011 (guidelines for auditing management systems); ISAE 3000 (assurance engagements other than audits or reviews of historical financial information); Institute of Internal Auditors Global Internal Audit Standards (quality assurance and improvement) | MCF-GOV-021; MCF-GOV-022; MCF-GOV-023; MCF-EVA-019 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-GOV-017 | GOV | Governance, Accountability and Assurance Direction | GOV-05 | Stakeholder and regulatory interface | Stakeholder Obligations | Ensure that obligations owed to stakeholders (customers, tenants, regulators, grid and water authorities, insurers, lenders, community) that constrain the AI capability are identified and translated into Service Outcomes, tolerances or constraints. | The capability owner shall maintain a stakeholder obligation register identifying each obligation that constrains an in-scope Capability Instance (for example contracted availability, data residency, grid connection conditions, water abstraction limits, noise and emission permits, insurance warranties), its source document, owner and the Service Outcome, tolerance or operating constraint into which it is translated. | 1) A stakeholder obligation register exists covering customers, tenants, regulators, utilities, insurers and financiers relevant to the instance. 2) Each obligation identifies its source document, owner and the Service Outcome, tolerance or constraint into which it is translated. 3) Grid connection and utility conditions that constrain load ramp rates, curtailment or on-site generation are captured. 4) A sample of source contracts and permits contains no constraining obligation absent from the register. 5) Obligations with conflicting requirements are identified and resolved by the capability owner. |  | Stakeholder obligation register; Sampled source contracts, permits and connection agreements; Traceability from obligations to Service Outcomes and constraints | DOCUMENT_REVIEW; SAMPLING; RECONCILIATION | 1) Obtain the register and confirm stakeholder classes covered. 2) Sample source documents and identify constraining obligations absent from the register. 3) Trace each sampled obligation to a Service Outcome, tolerance or constraint. 4) Confirm grid and utility constraints on ramp rate, curtailment and generation are captured. 5) Review conflict identification and resolution. | DIRECTIVE | DESIGN | AL2 | PLAN; DESIGN; OPERATE | NORMAL | Applies to every in-scope Capability Instance. |  | CG-01 | Grid connection ramp-rate limit unknown to operators of synchronous training workloads; Data residency obligation not reflected in recovery site selection; Insurance warranty breached by unrecorded configuration; Contracted availability exceeds designed capability | ServiceOutcome; CapabilityInstance; Dependency | Document review only; contract access governed by the evidence lead's restriction record. | If a source contract or permit cannot be accessed, record a U2 UNKNOWN against the obligations it would contain. | ISO 37301 (compliance management systems); ISO 22301 (business continuity management systems) | MCF-GOV-019; MCF-GOV-018; MCF-CAP-005; MCF-CAP-011 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-GOV-018 | GOV | Governance, Accountability and Assurance Direction | GOV-05 | Stakeholder and regulatory interface | Regulatory Monitoring | Ensure that changes in law, regulation, permits and mandatory standards affecting the AI capability (energy, water, emissions, safety, data and critical-infrastructure regimes) are detected, assessed for impact and actioned in time. | The compliance owner shall operate a regulatory monitoring process covering each jurisdiction in which in-scope infrastructure is located, record each relevant change with an impact assessment against Service Outcomes, controls and obligations, assign actions, and report material changes to the oversight committee. Changes affecting life safety, hazardous energy or reporting duties shall be escalated within the regulatory escalation time. | 1) Monitoring covers each jurisdiction and regulatory topic relevant to in-scope infrastructure. 2) Each relevant change in the period has an impact assessment and assigned actions. 3) Material changes were reported to the oversight committee. 4) Changes affecting life safety, hazardous energy or reporting duties were escalated within the escalation time. 5) Actions arising from regulatory changes are tracked to closure or have approved exceptions. | Regulatory escalation time for safety or reporting-duty changes [working days] default 10 (Programme parameter; illustrative) | Regulatory monitoring scope by jurisdiction and topic; Change log with impact assessments for the period; Oversight committee reports; Action tracking records | DOCUMENT_REVIEW; SAMPLING; INQUIRY | 1) Confirm monitoring scope by jurisdiction and topic. 2) Sample changes from the log and test impact assessments and actions. 3) Check escalation timing for safety and reporting-duty changes. 4) Confirm committee reporting of material changes. 5) Interview the compliance owner on sources and coverage limits. | DETECTIVE | OPERATION | AL4 | PLAN; OPERATE; CHANGE | NORMAL | Applies to every organisation that owns or operates in-scope infrastructure. AIDCF does not determine legal compliance; this control assesses the monitoring process only. |  | CG-14 | New energy-reporting duty missed; Permit condition change not reflected in operating envelope; Safety regulation change not escalated; Jurisdiction omitted from monitoring | Event; Action; ReassessmentTrigger | Desk review of the change log and impact assessments; no legal opinion is given or implied by the assessor. | If the monitoring scope cannot be confirmed for a jurisdiction, record a U5 coverage-gap UNKNOWN for that jurisdiction. | ISO 37301 (compliance management systems); ISO 31000 (risk management guidelines) | MCF-GOV-017; MCF-GOV-020; MCF-EVA-022 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-GOV-019 | GOV | Governance, Accountability and Assurance Direction | GOV-05 | Stakeholder and regulatory interface | Customer Commitments | Ensure that what is promised to customers and tenants (SLAs, SLOs, credits, capacity reservations, recovery commitments) reconciles to the approved Service Outcomes and to the capability actually provided, so that commitments do not exceed assured capability. | The commercial owner shall ensure that each customer or tenant commitment concerning availability, performance, integrity, capacity or recovery of an in-scope Capability Instance is recorded with its metric definition, measurement method and exclusions, and is reconciled by the capability owner to the approved Service Outcomes and tolerances before signature and after every change to either. Commitments exceeding approved Service Outcomes shall be approved by the accountable executive with a recorded risk acceptance. | 1) Each in-scope customer or tenant commitment is recorded with metric definition, measurement method and exclusions. 2) Each commitment is reconciled to an approved Service Outcome with the same metric definition and measurement window. 3) No commitment exceeds the approved Service Outcome tolerance without accountable-executive approval and risk acceptance. 4) Reconciliation was performed before signature for commitments made in the period. 5) Measurement of committed metrics uses the same data sources as Service Outcome measurement. |  | Commitment register with metric definitions; Reconciliation records to Service Outcomes; Approvals and risk acceptances for exceedances; Sampled contracts or service descriptions | RECONCILIATION; SAMPLING; DOCUMENT_REVIEW | 1) Obtain the commitment register and confirm completeness against the contract system. 2) Sample contracts and reperform reconciliation of metric definitions, windows and exclusions to Service Outcomes. 3) Identify exceedances and verify approvals and risk acceptances. 4) Confirm reconciliation dates precede signature. 5) Compare data sources for commitment reporting with those for Service Outcome measurement. | PREVENTIVE | IMPLEMENTATION | AL3 | PLAN; OPERATE; CHANGE | NORMAL | Applies where in-scope capability is provided to external customers or internal tenants under defined commitments. Not applicable to purely internal research capability without commitments, with rationale. |  | CG-01 | SLA promises accelerator availability beyond designed redundancy; SLA measured with different exclusions from Service Outcome; Recovery commitment shorter than tested recovery time; Capacity reservation exceeds power or cooling envelope | ServiceOutcome; CapabilityInstance; CapacityAssertion | Document review only; commercial terms are disclosed only to the extent needed and under restriction. | If a contract cannot be accessed, record a U2 UNKNOWN for that commitment; it shall not be assumed to match the Service Outcome. | ISO/IEC 20000-1 (service management system); ISO/IEC 19086 series (cloud computing service level agreement framework) | MCF-GOV-017; MCF-CAP-005; MCF-CAP-006; MCF-CAP-008 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-GOV-020 | GOV | Governance, Accountability and Assurance Direction | GOV-05 | Stakeholder and regulatory interface | External Reporting | Ensure that assurance conclusions communicated externally (customer statements, regulatory submissions, investor or public disclosures) are no stronger than the approved Assurance Decision, carry its limitations, and are approved before release. | The decision authority shall approve every external communication that conveys an AIDCF assurance conclusion before release. The communications owner shall ensure that each such communication uses the controlled decision language of AIDCF-012, identifies the Capability Instance, scope, period and limitations, includes every gate FAIL and US4/US5 UNKNOWN relevant to the audience, contains no prohibited claim (certification, accreditation, universal safety or resilience), and is withdrawn or corrected when the underlying decision is suspended, withdrawn or superseded. | 1) Every external communication in the period conveying an AIDCF conclusion was approved by the decision authority before release. 2) Each communication uses controlled decision language and states Capability Instance, scope, period and limitations. 3) No communication contains a prohibited claim. 4) No communication omits a gate FAIL or US4/US5 UNKNOWN material to its audience. 5) Communications based on decisions later suspended, withdrawn or superseded were corrected or withdrawn within the correction time. | External correction time after decision suspension [working days] default 10 (Programme parameter; illustrative) | Register of external communications conveying conclusions; Approval records; Copies of the communications; Correction and withdrawal records | DOCUMENT_REVIEW; RECONCILIATION; SAMPLING | 1) Obtain the communications register and test completeness by searching published and submitted material. 2) Compare each communication with the underlying decision record for state, scope, period and limitations. 3) Screen for prohibited claims. 4) Check inclusion of material gate FAIL and US4/US5 UNKNOWN items. 5) Trace suspended or superseded decisions to correction or withdrawal of communications. | PREVENTIVE | OPERATION | AL4 | OPERATE | NORMAL | Applies whenever an AIDCF conclusion is communicated outside the organisation issuing it. |  |  | Marketing states the facility is 'AIDCF certified'; Customer statement omits a critical UNKNOWN; Communication remains published after decision suspension; Scope broadened in the summary beyond the assessed boundary | AssuranceStatement; AssuranceReport; DistributionControl; AssuranceDecision | Desk review of published and submitted material only; the assessor does not contact external recipients of the communications. | If the completeness of the communications register cannot be tested, record a U5 coverage-gap UNKNOWN and limit the conclusion to communications identified. | AIDCF-012 Reporting and Assurance Statement Standard; ISAE 3000 (assurance engagements other than audits or reviews of historical financial information); ISO/IEC 17000 (conformity assessment vocabulary and general principles) | MCF-EVA-020; MCF-EVA-016; MCF-EVA-024; MCF-GOV-018 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-GOV-021 | GOV | Governance, Accountability and Assurance Direction | GOV-06 | Ethics, impartiality and competence | Conflict Management | Ensure that conflicts of interest affecting assessors, reviewers, specialists and decision authorities (financial, self-review, familiarity, advocacy, intimidation) are declared, evaluated and safeguarded before work begins and throughout the engagement. | The assurance programme lead shall require every assessor, reviewer, specialist and decision authority to declare interests before assignment and on any change, shall evaluate each declared or identified threat (self-review, self-interest, familiarity, advocacy, intimidation), and shall apply and record a safeguard or exclusion. The programme lead shall prohibit outcome-contingent fees for assurance conclusions and shall exclude from assessment any person who designed, built, operates or advised on the control under assessment within the cooling-off period. | 1) Every person assigned to engagements in the period has a declaration dated before assignment. 2) Each declared or identified threat has a recorded evaluation and safeguard or exclusion. 3) No assessor assessed a control they designed, built, operated or advised on within the cooling-off period. 4) No engagement in the period used an outcome-contingent fee. 5) Changes in interests during engagements were declared and re-evaluated. | Self-review cooling-off period [months] default 12 (Programme parameter; illustrative) | Declarations of interest for engagement personnel; Threat evaluations and safeguard records; Engagement assignment records; Fee arrangements for provider engagements | DOCUMENT_REVIEW; RECONCILIATION; SAMPLING; INQUIRY | 1) List engagement personnel and match each to a dated declaration. 2) Review threat evaluations and safeguards. 3) Cross-check assessors against design, change, operation and advisory records for the controls they assessed. 4) Inspect fee arrangements for outcome contingency. 5) Interview a sample of assessors on declaration practice. | PREVENTIVE | OPERATION | AL4 | PLAN; OPERATE | NORMAL | Applies to all engagements producing Control Assessments, Gate Results or Assurance Decisions. |  |  | Assessor reviews a design they produced; Provider paid more for a favourable conclusion; Familiarity threat from long-standing operator relationship unaddressed; Decision authority holds a commercial interest in the outcome | Assessment; ReviewRecord; AssuranceProgram | Document review and interview only; personal declarations are handled as restricted personal data. | If a declaration is missing for a person who assessed a control, record a U1 UNKNOWN and treat that person's results as not independently assessed until a retrospective declaration is evaluated. | ISO/IEC 17020 (requirements for bodies performing inspection) - impartiality; ISO/IEC 17021-1 (requirements for bodies providing audit and certification) - impartiality; ISO 19011 (guidelines for auditing management systems) | MCF-GOV-022; MCF-GOV-016; MCF-GOV-023 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-GOV-022 | GOV | Governance, Accountability and Assurance Direction | GOV-06 | Ethics, impartiality and competence | Assessor Independence | Ensure that the organisational and reporting independence of the assessment function matches the reliance placed on its conclusions, so that preparation, performance, review and decision remain separable. | The governing body shall define the independence level required for each class of intended reliance (management use, customer reliance, regulatory or financing reliance). The assurance programme lead shall ensure that for each engagement the assessment team's reporting line, provider model and separation of preparation, performance, review and decision meet the required level, and that the actual independence level is stated in the Assurance Statement. | 1) Required independence levels are defined per reliance class. 2) For each engagement, the provider model and reporting line meet the required level for the stated intended users. 3) Preparation, performance, independent review and decision are assigned to separate persons or roles as required by the level. 4) The Assurance Statement states the actual independence level and provider model. 5) Assessors did not operate controls or accept risks for management during the engagement. |  | Independence policy with levels per reliance class; Engagement records with team composition, provider model and reporting line; Assurance Statements for the period | DOCUMENT_REVIEW; RECONCILIATION; INQUIRY | 1) Obtain the independence policy and levels. 2) For each engagement, compare provider model, reporting line and role separation with the required level. 3) Compare stated independence level in Assurance Statements with engagement records. 4) Interview management and assessors on any operation of controls or risk acceptance by assessors. | PREVENTIVE | IMPLEMENTATION | AL3 | PLAN; OPERATE | NORMAL | Applies to all engagements; the required level may be management-only for AL0-AL1 diagnostic work. |  | CG-13 | Internal team reporting to the operations head issues customer-facing assurance; One person prepares, reviews and decides; Statement overstates independence; Assessor runs a failover test as operator | Assessment; AssuranceStatement; AssuranceProgram | Document review and interview only. | If the reporting line of an assessment team cannot be established, record a U6 UNKNOWN and restrict intended use to management. | ISO/IEC 17020 (requirements for bodies performing inspection); Institute of Internal Auditors Three Lines Model; ISAE 3000 (assurance engagements other than audits or reviews of historical financial information) | MCF-GOV-021; MCF-GOV-016; MCF-EVA-019 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-GOV-023 | GOV | Governance, Accountability and Assurance Direction | GOV-06 | Ethics, impartiality and competence | Competence Management | Ensure that assessors, specialists and reviewers are competent for the domains, technologies and test methods they apply (for example high-density liquid cooling, accelerator fabrics, protection studies, OT security), and that competence is current. | The assurance programme lead shall maintain a competence framework for each role and domain (aligned to AIDCF-011 Part IX), a register recording each person's evidenced competence and its currency, and an assignment check confirming that every engagement assignment matches recorded competence. Where competence is not available internally, the lead shall engage a specialist under recorded reliance with scope and responsibility. | 1) A competence framework defines required knowledge, experience and evidence per role and domain. 2) A register records each person's competence with evidence and currency date. 3) Every assignment in the period matches recorded, current competence for the domain and method. 4) Specialist reliance is recorded with scope, competence evidence and responsibility. 5) Competence gaps identified in the period have development actions or were filled by specialists. | Competence currency period [months] default 24 (Programme parameter; illustrative, shorter for rapidly changing technologies) | Competence framework; Competence register with evidence; Engagement assignment records; Specialist reliance records | DOCUMENT_REVIEW; SAMPLING; RECONCILIATION; INQUIRY | 1) Review the framework against AIDCF-011 competence expectations and the technologies in scope. 2) Sample register entries and verify evidence at source. 3) Reconcile assignments to recorded competence and currency. 4) Review specialist reliance records. 5) Interview a sample of assessors on their domain experience. | PREVENTIVE | OPERATION | AL4 | PLAN; OPERATE | NORMAL | Applies to all engagement roles. AIDCF does not accredit people; this control assesses the programme's own competence management. |  |  | Mechanical assessor without liquid-cooling experience assesses CDU failover; Lapsed competence for protection-study review; Specialist used without recorded scope; Reviewer unfamiliar with accelerator fabric failure modes | Assessment; ReviewRecord; AssuranceProgram | Document review and interview only; personal data handled under minimisation. | If competence evidence for an assigned person cannot be verified, record a U6 UNKNOWN and apply a CONF-2 ceiling to results that person produced. | ISO/IEC 17024 (requirements for bodies operating certification of persons); ISO 19011 (guidelines for auditing management systems) - competence of auditors; AIDCF-011 Assurance Program Framework | MCF-GOV-016; MCF-EVA-012; MCF-GOV-022 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-GOV-024 | GOV | Governance, Accountability and Assurance Direction | GOV-06 | Ethics, impartiality and competence | Appeal and Challenge | Ensure that capability owners, operators and affected stakeholders can challenge a Finding, Gate Result or Assurance Decision through a defined, impartial process with recorded outcomes, without suppressing the original record. | The decision authority shall maintain an appeal and challenge procedure that defines who may challenge, grounds, time limits, the impartial reviewer, evidence required, and possible outcomes. The decision authority shall ensure that every challenge is logged, decided by a person not involved in the challenged result, and that the original result, the challenge and the outcome are all preserved, with any change made only by reassessment. | 1) A procedure defines eligible challengers, grounds, time limits, reviewer, evidence and outcomes. 2) Every challenge in the period is logged and was decided by a person not involved in the challenged result. 3) Original results, challenges and outcomes are preserved; no original record was deleted or overwritten. 4) Changed results arising from challenges were produced by reassessment with new or re-evaluated evidence. 5) Challenges were decided within the procedure time limits or the delay was recorded. |  | Appeal and challenge procedure; Challenge log for the period; Sampled challenge files with decisions; Record history for challenged results | DOCUMENT_REVIEW; SAMPLING; INSPECTION | 1) Review the procedure. 2) Sample challenges and verify reviewer non-involvement and timeliness. 3) Inspect record history for preservation of original results. 4) Trace changed results to reassessment records. | CORRECTIVE | OPERATION | AL4 | OPERATE | NORMAL | Applies to every programme issuing Findings, Gate Results or Assurance Decisions. |  |  | Finding deleted after management objection; Challenge decided by the original assessor; Result changed without new evidence; No route for operators to contest a Finding | Finding; GateResult; AssuranceDecision; ReviewRecord | Document and record inspection only. | If record history cannot demonstrate preservation of originals, record a U7 UNKNOWN against challenged results. | ISO/IEC 17020 (requirements for bodies performing inspection) - complaints and appeals; ISO/IEC 17021-1 (requirements for bodies providing audit and certification) - appeals | MCF-GOV-016; MCF-EVA-015; MCF-EVA-013 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-CAP-001 | CAP | AI Capability, Service Outcome and Demand Management | CAP-01 | Capability inventory | Capability Register | Maintain an authoritative register of AI Capability Instances (for example a named training cluster, an inference service pool, a sovereign AI hall) so that every assurance claim is anchored to an identified, bounded instance rather than to a site or product. | The capability owner shall maintain a capability register in which each Capability Instance has a unique identifier, a description of the AI work it delivers (training, fine-tuning, inference, data preparation), its physical and logical location (site, hall, pods, clusters), its tenancy model, its lifecycle status, its accountable owner, its Service Outcomes and its current ArchitectureSnapshot reference. The capability owner shall reconcile the register to the scheduler or orchestration inventory and to the facility asset register at no more than the register reconciliation interval and after every material change. | 1) Every Capability Instance has a unique, stable identifier and the required attributes (work type, location, tenancy model, lifecycle status, owner, Service Outcomes, ArchitectureSnapshot reference). 2) Every accelerator cluster, pod or service pool present in the scheduler or orchestration inventory is assigned to exactly one Capability Instance or recorded as out of scope with rationale. 3) Every Capability Instance in the register maps to physical locations present in the facility asset register. 4) The last reconciliation is within the reconciliation interval and after every material change in the period. 5) No assurance report in the period refers to a capability not present in the register at the report date. | Capability register reconciliation interval [months] default 3 (Capability-profile parameter; illustrative, aligned to the rate of cluster expansion) | Capability register extract with all attributes; Scheduler or orchestration inventory export (cluster, pod, node counts) dated within the reconciliation interval; Facility asset register extract for the halls and pods concerned; Reconciliation record listing unmatched items and dispositions | RECONCILIATION; INSPECTION; DOCUMENT_REVIEW; ANALYSIS | 1) Obtain the register extract and check each instance for the required attributes. 2) Extract the scheduler or orchestration inventory and reconcile clusters, pods and node counts to Capability Instances. 3) Reconcile instance locations to the facility asset register. 4) Analyse unmatched items and their dispositions; treat unexplained differences as Findings. 5) Check reconciliation dates against the interval and change events. 6) Compare capabilities named in reports issued in the period with the register. | DIRECTIVE | IMPLEMENTATION | AL3 | PLAN; DESIGN; BUILD; OPERATE; CHANGE | NORMAL | Applies to every assurance programme; there is no assurance subject without it. | CG-01 |  | Assurance claim made about 'the data centre' rather than a defined instance; New cluster in production but not in the register; Same accelerators counted in two instances; Register location does not match physical deployment | CapabilityInstance; ArchitectureSnapshot; AssetInstance | Read-only queries against scheduler and asset systems, executed by the system owner under assessor observation; no job submission or node draining is performed. | If the scheduler or orchestration inventory cannot be accessed, the instance boundary is unverified: record a US5 UNKNOWN Record against the Capability Instance and do not rely on the register alone. | ISO/IEC 22237 series (data centre facilities and infrastructures); ISO/IEC 20000-1 (service management system) - service catalogue; ISO 55000 series (asset management); AIDCF-002 Core Conceptual Model | MCF-CAP-002; MCF-CAP-004; MCF-CAP-003; MCF-GOV-001 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-CAP-002 | CAP | AI Capability, Service Outcome and Demand Management | CAP-01 | Capability inventory | Capability Ownership | Ensure that each Capability Instance has one accountable owner who owns its Service Outcomes, tolerances, risks and remediation, and who has authority over the facility and IT resources needed to sustain them. | The accountable executive shall appoint, for each Capability Instance, one capability owner with documented authority over the Service Outcomes, impact tolerances, risk acceptance within delegated limits, and the commitment of facility, platform and provider resources needed to meet them. The capability owner shall be identified in the capability register, the RACI and the decision-rights matrix, and a deputy shall be named for EMERGENCY and RECOVERY states. | 1) Each Capability Instance has exactly one appointed capability owner with a dated appointment. 2) The owner's authority over Service Outcomes, tolerances, risk acceptance limits and resource commitment is documented. 3) The owner is consistently identified in the capability register, RACI and decision-rights matrix. 4) A deputy is named and authorised for EMERGENCY and RECOVERY states. 5) Where facility and AI platform are run by different organisations, the owner's authority over each is established by contract or internal agreement. |  | Capability owner appointment records; Authority statement or delegation; Capability register, RACI and decision-rights extracts; Deputy appointment; Facility and platform agreements establishing owner authority where organisations differ | DOCUMENT_REVIEW; RECONCILIATION; INQUIRY | 1) Obtain appointment and authority records for each instance. 2) Reconcile owner identity across register, RACI and decision-rights matrix. 3) Confirm deputy appointment and authority for EMERGENCY and RECOVERY. 4) Review agreements establishing authority across facility and platform organisations. 5) Interview the owner and deputy on authority to commit resources and accept risk. | DIRECTIVE | IMPLEMENTATION | AL3 | PLAN; OPERATE; CHANGE | NORMAL; EMERGENCY; RECOVERY | Applies to every Capability Instance in the register. | CG-13 | CG-01 | Instance owned jointly by facility and platform teams with no single accountable owner; Owner lacks authority over the colocation facility; No deputy during a cooling emergency; Owner identity differs between registers | CapabilityInstance; ServiceOutcome; AssuranceDecision | Interview and document review only. | If no appointment record exists, record a US4 UNKNOWN Record against CG-13 for the instance; de facto ownership described in interview is not sufficient. | ISO 37000 (governance of organizations); ISO/IEC 20000-1 (service management system); ISO 55000 series (asset management) | MCF-CAP-001; MCF-GOV-005; MCF-GOV-006; MCF-GOV-002 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-CAP-003 | CAP | AI Capability, Service Outcome and Demand Management | CAP-01 | Capability inventory | Lifecycle Status | Ensure that each Capability Instance's lifecycle status (planned, in design, in build, commissioning, in service, degraded-service, in change, retiring, retired) is accurate at all times so that the claim type, evidence and gates applied match the instance's real stage. | The capability owner shall define lifecycle status values and transition criteria for Capability Instances, shall record each status transition with date, approver and the evidence that the transition criteria were met, and shall not transition an instance to in-service until commissioning acceptance (MCF-CAP-022) is recorded. The assurance programme lead shall use the recorded status to select claim types and Assurance Levels for each assessment. | 1) Lifecycle status values and transition criteria are defined. 2) Every status transition in the period has date, approver and evidence that transition criteria were met. 3) No instance entered in-service status before commissioning acceptance was recorded. 4) The recorded status of each instance matches observed reality (for example production workloads are not running on an instance recorded as commissioning). 5) Assessment plans in the period selected claim types consistent with the recorded status. |  | Lifecycle status definitions and transition criteria; Status transition log for the period; Commissioning acceptance records; Scheduler evidence of production workload on each instance; Assessment plans | DOCUMENT_REVIEW; RECONCILIATION; OBSERVATION; SAMPLING | 1) Review status definitions and transition criteria. 2) Sample transitions and verify approver and criteria evidence. 3) Compare in-service dates with commissioning acceptance dates. 4) Compare recorded status with scheduler or tenancy evidence of production use. 5) Check claim types in assessment plans against recorded status. | DETECTIVE | OPERATION | AL4 | BUILD; COMMISSION; OPERATE; CHANGE; DECOMMISSION | NORMAL; TRANSITION | Applies to every Capability Instance. |  | CG-01; CG-14 | Customer workloads placed on a partially commissioned pod; Instance reported in service after partial retirement; Operation claims assessed on a capability still in build | CapabilityInstance; OperatingState; Event | Read-only scheduler queries; no workload is moved or paused. | If actual production use cannot be determined, record a U5 UNKNOWN against the status criterion and do not assume the recorded status is correct. | ISO/IEC/IEEE 15288 (system life cycle processes); ISO 55000 series (asset management) | MCF-CAP-001; MCF-CAP-022; MCF-CAP-024 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-CAP-004 | CAP | AI Capability, Service Outcome and Demand Management | CAP-01 | Capability inventory | Architecture Linkage | Ensure that each Capability Instance is linked to a current ArchitectureSnapshot that identifies the InfrastructureSystems, AssetInstances and Interfaces implementing its Required Functions (power, cooling, compute, storage, network, control plane), so that the assessment boundary is grounded in the real architecture. | The capability architect shall maintain, for each Capability Instance, a current ArchitectureSnapshot linked in the assurance graph that identifies the Required Functions of each Service Outcome and the InfrastructureSystems, AssetInstances and Interfaces implementing them, including shared and external elements. The capability architect shall version the snapshot after every material change and shall reconcile it to as-built and as-configured evidence at no more than the architecture reconciliation interval. | 1) Each Capability Instance has a current ArchitectureSnapshot reference in the graph. 2) Every Service Outcome is linked to Required Functions, and every Required Function is linked to the InfrastructureSystems that implement it. 3) Shared elements (for example a facility water loop serving several halls, a common spine layer, a shared parallel file system) and external elements are identified as such. 4) A sample of graph links reconciles to as-built drawings, single-line diagrams, P&IDs, topology exports and cluster manifests. 5) The snapshot was versioned after each material change and reconciled within the interval. | Architecture reconciliation interval [months] default 6 (Capability-profile parameter; illustrative) | ArchitectureSnapshot record and version history; Assurance graph extract of Outcome-Function-System links; As-built drawings, single-line diagrams and P&IDs for sampled links; Network topology and cluster manifest exports; Reconciliation record | RECONCILIATION; INSPECTION; ANALYSIS; DOCUMENT_REVIEW | 1) Obtain the snapshot and graph extract and check Outcome-Function-System completeness. 2) Identify shared and external elements and confirm they are marked. 3) Select a sample of links stratified by domain and reconcile to drawings, topology and manifests. 4) Verify a subset of the sample by site inspection or live read-only query. 5) Check versioning against the change log. | DIRECTIVE | IMPLEMENTATION | AL3 | DESIGN; BUILD; COMMISSION; OPERATE; CHANGE | NORMAL | Applies to every Capability Instance assessed above AL1. | CG-02 | CG-03; CG-01 | Assessment boundary drawn from a design that no longer matches the as-built state; Shared facility water loop not identified, hiding common-mode exposure; Storage system serving checkpoints omitted from architecture; Graph links to decommissioned equipment | ArchitectureSnapshot; RequiredFunction; InfrastructureSystem; AssetInstance; Interface | Site verification follows induction and escort rules; no panels are opened and no equipment is operated. Network and cluster exports are read-only. | Any Required Function with no linked implementing system, or any link that cannot be reconciled to evidence, is recorded as a US4 UNKNOWN Record against CG-02. | ISO/IEC/IEEE 42010 (architecture description); ISO/IEC 22237 series (data centre facilities and infrastructures); AIDCF-013 AI Data Centre Assurance Reference Architecture | MCF-CAP-001; MCF-CAP-021; MCF-GOV-006; MCF-EVA-010 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-CAP-005 | CAP | AI Capability, Service Outcome and Demand Management | CAP-02 | Service outcome definition | Availability Outcomes | Define availability Service Outcomes for each Capability Instance in units that reflect AI work actually delivered (for example usable accelerator capacity, job-serving availability), with measurement window, exclusions and tolerance, so that power, cooling and platform continuity can be assessed against a stated target. | The capability owner shall approve, for each Capability Instance, availability Service Outcomes that state the unit of availability (for example fraction of committed accelerators schedulable and healthy, or fraction of inference requests served), the target, the measurement window, the maximum single-interruption duration, permitted exclusions (for example planned maintenance) and the data source for measurement. The capability owner shall ensure the outcomes are consistent with customer commitments (MCF-GOV-019) and impact tolerances (MCF-CAP-010). | 1) Each Capability Instance has at least one approved availability Service Outcome. 2) Each outcome states unit, target, measurement window, maximum single-interruption duration, exclusions and measurement data source. 3) The unit measures delivered AI capability (schedulable healthy accelerators, served requests or equivalent) rather than facility uptime alone. 4) Targets and exclusions are consistent with customer commitments and impact tolerances. 5) The measurement data source exists and produces the metric for the current period. | Availability target [% of measurement window] default 99.5 (training) / 99.9 (inference) (Capability-profile parameter set by the capability owner; illustrative only) Availability measurement window [days] default 30 (Capability-profile parameter; illustrative) Maximum single-interruption duration [minutes] default 60 (Capability-profile parameter; illustrative, derived from impact tolerance) | Approved Service Outcome records for availability; Metric definition and measurement data source description; Current-period metric output; Reconciliation to customer commitments and impact tolerances | DOCUMENT_REVIEW; ANALYSIS; RECONCILIATION; INQUIRY | 1) Obtain approved availability outcomes for each instance and check required fields. 2) Assess whether the unit measures delivered AI capability. 3) Reconcile targets and exclusions to customer commitments and impact tolerances. 4) Obtain the current-period metric and reperform its derivation from the data source for one window. 5) Interview the capability owner on how the target was derived. | DIRECTIVE | DESIGN | AL2 | PLAN; DESIGN; OPERATE; CHANGE | NORMAL; DEGRADED; MAINTENANCE | Applies to every in-service or planned Capability Instance with an availability expectation; research instances with no availability expectation shall record that expectation explicitly rather than omit the outcome. | CG-01 |  | Availability defined as facility power uptime while accelerators are unschedulable; No measurement window, so outages are averaged away; Exclusions so broad that the outcome is untestable; Target exceeds designed redundancy | ServiceOutcome; CapabilityInstance; CapacityAssertion | Desk review and read-only metric extraction; no fault is induced to measure availability. | If the measurement data source cannot produce the metric, the outcome is defined but unmeasurable: criterion 5 is not met and a U1 UNKNOWN is recorded; this is not treated as a missing definition. | ISO/IEC 20000-1 (service management system); IEC 60300 series (dependability management); ISO/IEC 22237 series (data centre facilities and infrastructures) - availability classes | MCF-CAP-010; MCF-GOV-019; MCF-CAP-008; MCF-CAP-006 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-CAP-006 | CAP | AI Capability, Service Outcome and Demand Management | CAP-02 | Service outcome definition | Performance Outcomes | Define performance Service Outcomes that capture whether the infrastructure lets AI work run at its required speed (for example training goodput, step-time stability, inference latency percentiles, collective bandwidth), so that throttling, fabric congestion or storage stalls are visible as outcome failures rather than hidden behind availability. | The capability owner shall approve, for each Capability Instance, performance Service Outcomes that state the metric (for example training goodput fraction, median and tail step time, inference latency at a stated percentile, sustained accelerator power without thermal or power throttling), target, measurement method, measurement window, workload or benchmark reference, and the infrastructure conditions under which the target applies. The AI platform owner shall ensure the measurement method is implemented and its data retained. | 1) Each Capability Instance has at least one approved performance Service Outcome appropriate to its work type. 2) Each outcome states metric, target, method, window, workload or benchmark reference and infrastructure conditions. 3) At least one outcome detects infrastructure-induced degradation (thermal or power throttling, fabric congestion, storage stall). 4) The measurement method is implemented and produces data for the current period. 5) Targets are consistent with the design basis for power per accelerator, cooling capacity and fabric bandwidth. | Training goodput floor [% of wall-clock time doing useful training progress] default 90 (Capability-profile parameter; illustrative) Inference latency percentile and bound [ms at p99] default set per service (Capability-profile parameter; no generic default) Throttling event tolerance [accelerator-hours throttled per week] default 0 attributable to facility conditions (Capability-profile parameter; illustrative) | Approved performance Service Outcome records; Metric and method specifications with workload reference; Current-period metric data; Design basis extracts for power, cooling and fabric | DOCUMENT_REVIEW; ANALYSIS; INQUIRY | 1) Obtain approved performance outcomes and check required fields. 2) Evaluate with a compute specialist whether the metrics detect infrastructure-induced degradation. 3) Confirm current-period data exist and reperform one metric derivation. 4) Compare targets with design basis for power, cooling and fabric. 5) Interview the AI platform owner on measurement implementation and retention. | DIRECTIVE | DESIGN | AL2 | PLAN; DESIGN; OPERATE; CHANGE | NORMAL; DEGRADED | Applies to every Capability Instance whose value depends on delivered compute speed; that is all training and inference instances. | CG-01 | CG-08 | Accelerators thermally throttle under high facility water temperature while availability shows 100%; Fabric congestion halves training throughput unnoticed; Storage stalls during checkpointing degrade goodput; Performance target set without reference to power or cooling design | ServiceOutcome; RequiredFunction; CapacityAssertion | Desk review and read-only metric extraction. Benchmark runs, if requested for corroboration, are scheduled by the platform owner on non-production capacity. | If throttling or congestion data are not collected, record a U1 UNKNOWN against criterion 3; the outcome cannot then support CG-08 evaluation. | MLCommons MLPerf benchmark suites (training and inference); ISO/IEC 25010 (systems and software quality models) - performance efficiency; ASHRAE TC 9.9 thermal guidelines for data processing environments | MCF-CAP-005; MCF-CAP-017; MCF-CAP-018; MCF-CAP-014 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-CAP-007 | CAP | AI Capability, Service Outcome and Demand Management | CAP-02 | Service outcome definition | Integrity Outcomes | Define integrity Service Outcomes for model weights, checkpoints, training data and inference results so that silent data corruption, partial writes and configuration drift are treated as outcome failures with stated tolerances and detection expectations. | The capability owner shall approve, for each Capability Instance, integrity Service Outcomes stating which data and states are protected (model weights, optimiser state, checkpoints, datasets, configuration), the integrity property required (no undetected corruption, verified completeness, version provenance), the detection mechanism expected (checksums, end-to-end verification, accelerator error reporting), the tolerated detection latency and the required response. The data platform owner shall confirm that each detection mechanism exists. | 1) Integrity outcomes identify protected data and states, including checkpoints and model weights. 2) Each outcome states the integrity property, detection mechanism, tolerated detection latency and required response. 3) Undetected corruption of model weights and checkpoints relied upon for recovery has a tolerance of zero. 4) Hardware-originated silent data corruption on accelerators is addressed by a stated detection expectation. 5) The data platform owner has confirmed each detection mechanism exists for the current architecture. | Checkpoint integrity verification point [event] default on write and before restore (Capability-profile parameter; illustrative) Tolerated detection latency for dataset corruption [hours] default 24 (Capability-profile parameter; illustrative) | Approved integrity Service Outcome records; Detection mechanism description per protected data class; Data platform owner confirmation; Response procedure references | DOCUMENT_REVIEW; ANALYSIS; INQUIRY; INSPECTION | 1) Obtain integrity outcomes and check coverage of protected data classes. 2) Review each detection mechanism with a storage or compute specialist. 3) Confirm zero tolerance for undetected corruption of recovery-critical checkpoints and weights. 4) Inspect configuration evidence that detection mechanisms exist (for example checksum settings, error-reporting configuration). 5) Interview the data platform owner on response procedures. | DIRECTIVE | DESIGN | AL2 | DESIGN; OPERATE; CHANGE | NORMAL; RECOVERY | Applies to every Capability Instance that stores model state or data whose corruption would affect outcomes; that is all training instances and inference instances serving stored weights. | CG-01 | CG-08 | Corrupted checkpoint discovered only on restore after a power event; Silent data corruption on an accelerator propagates into a trained model; Partial checkpoint write accepted as complete; Model weights deployed without provenance verification | ServiceOutcome; RequiredFunction; FailureMode | Desk review and read-only configuration inspection; no fault injection into production data. | If no detection mechanism can be shown for a protected data class, criterion 5 is NONCONFORMING (not UNKNOWN); UNKNOWN applies only where mechanism existence cannot be verified. | ISO/IEC 27040 (storage security); ISO/IEC 25012 (data quality model); NIST SP 800-209 (security guidelines for storage infrastructure) | MCF-CAP-008; MCF-CAP-006; MCF-EVA-006 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-CAP-008 | CAP | AI Capability, Service Outcome and Demand Management | CAP-02 | Service outcome definition | Recovery Outcomes | Define recovery Service Outcomes for each Capability Instance (time to restore stated capacity, tolerated loss of training progress, restoration order, recovered-state verification) so that power, cooling, compute, storage, network and control-plane recovery can be assessed against a stated target. | The capability owner shall approve, for each Capability Instance, recovery Service Outcomes that state the recovery time objective for restoring a stated fraction of capacity, the recovery point objective (for training expressed as maximum lost training time, driving checkpoint interval; for inference as maximum state or configuration loss), the restoration order of dependent services (facility power, cooling, control plane, storage, fabric, compute, scheduler), and the verification required before declaring recovery. The capability owner shall ensure these outcomes are consistent with impact tolerances and customer commitments. | 1) Each Capability Instance has approved recovery outcomes with RTO for a stated capacity fraction and RPO. 2) For training instances, RPO is expressed as maximum lost training time and is consistent with the configured checkpoint interval. 3) A restoration order of dependent services is defined from facility power through to scheduler. 4) Verification criteria for declaring recovery are defined (for example accelerator health checks, fabric validation, checkpoint integrity). 5) Recovery outcomes are consistent with impact tolerances and customer commitments. | Recovery time objective [hours to restore stated capacity] default 4 to 80% capacity (Capability-profile parameter; illustrative) Recovery point objective (training) [minutes of lost training] default 30 (Capability-profile parameter; illustrative, constrained by checkpoint write time) Recovered capacity fraction for RTO [% of committed accelerators] default 80 (Capability-profile parameter; illustrative) | Approved recovery Service Outcome records; Restoration order definition; Recovery verification criteria; Checkpoint interval configuration extract; Reconciliation to impact tolerances and commitments | DOCUMENT_REVIEW; RECONCILIATION; ANALYSIS | 1) Obtain recovery outcomes and check RTO, RPO, restoration order and verification criteria. 2) Extract checkpoint interval configuration and compare with RPO. 3) Analyse restoration order against the architecture snapshot for missing dependencies. 4) Reconcile to impact tolerances and customer commitments. | DIRECTIVE | DESIGN | AL2 | DESIGN; OPERATE; CHANGE | RECOVERY; FAILED; EMERGENCY | Applies to every Capability Instance in service or in design. | CG-01 | CG-10 | Checkpoint interval longer than the tolerated lost training time; Restoration order omits the control plane or identity service; No criteria for declaring recovery, so degraded capacity is declared recovered; RTO shorter than the time to restart cooling and stabilise facility water | ServiceOutcome; RequiredFunction; OperatingState | Desk review and read-only configuration extraction; recovery is not exercised under this control. | If the checkpoint interval cannot be extracted, record a U1 UNKNOWN against criterion 2; the RPO is then unsupported for CG-10 evaluation. | ISO 22301 (business continuity management systems); ISO/IEC 27031 (ICT readiness for business continuity) | MCF-CAP-010; MCF-CAP-016; MCF-CAP-007; MCF-CAP-005 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-CAP-009 | CAP | AI Capability, Service Outcome and Demand Management | CAP-03 | Criticality and materiality | Criticality Criteria | Establish approved criteria for classifying Capability Instances, Service Outcomes and Required Functions by criticality, so that assurance depth, evidence floors, gate applicability and remediation priority follow consequence consistently. | The accountable executive shall approve criticality criteria that classify Capability Instances, Service Outcomes and Required Functions into defined classes using stated consequence dimensions (safety, customer and contractual, financial, regulatory, reputational, societal dependency) and thresholds. The capability owner shall apply the criteria to every in-scope item, record the class and rationale, and re-apply them after every material change. | 1) Criticality criteria are approved and define classes, consequence dimensions and thresholds. 2) Every in-scope Capability Instance, Service Outcome and Required Function has a recorded class and rationale. 3) Reperformance of the classification for a sample yields the same class. 4) Classifications were re-applied after each material change in the period. 5) Criticality class is used to set assurance depth in the assurance plan (MCF-GOV-013). |  | Approved criticality criteria; Classification register with rationale; Change-triggered reclassification records | DOCUMENT_REVIEW; REPERFORMANCE; SAMPLING | 1) Review the criteria for classes, dimensions and thresholds. 2) Check completeness of the classification register. 3) Reperform classification for a sample. 4) Check reclassification after material changes and use in the assurance plan. | DIRECTIVE | DESIGN | AL2 | PLAN; DESIGN; CHANGE | NORMAL | Applies to every programme. |  | CG-01 | Inconsistent classification across instances; Criticality not updated after a customer contract change; Assurance depth unrelated to consequence | CapabilityInstance; ServiceOutcome; RequiredFunction | Desk review and reperformance on records only. | If rationale is missing for a classification, reperform it; record a U9 UNKNOWN only if reviewers cannot agree on the class. | ISO 22301 (business continuity management systems) - business impact analysis; ISO 31000 (risk management guidelines) | MCF-CAP-010; MCF-CAP-011; MCF-CAP-012; MCF-GOV-013 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-CAP-010 | CAP | AI Capability, Service Outcome and Demand Management | CAP-03 | Criticality and materiality | Impact Tolerance | Set approved, measurable impact tolerances for each Service Outcome (maximum tolerable interruption, capacity reduction, lost work and integrity loss) that define the limit beyond which harm is unacceptable, and against which gates and decisions are evaluated. | The capability owner shall set, and the accountable executive shall approve, for each Service Outcome of each Capability Instance, impact tolerances stating maximum tolerable interruption duration, maximum tolerable capacity reduction and its duration, maximum tolerable loss of work (for example training progress), and tolerated integrity loss, each with units and the operating states to which it applies. Tolerances shall lie within risk appetite limits (MCF-GOV-014) or have governing-body approval of the exceedance. | 1) Each Service Outcome has approved impact tolerances with units and applicable operating states. 2) Tolerances cover interruption duration, capacity reduction with duration, loss of work and integrity loss. 3) Tolerances lie within risk appetite limits or the exceedance is approved by the governing body. 4) Tolerances are at least as stringent as customer commitments for the same outcome. 5) Tolerances are expressed so that a test or observation can show whether they were breached. | Maximum tolerable interruption [hours] default 8 (Capability-profile parameter; illustrative) Maximum tolerable capacity reduction [% of committed capacity for stated duration] default 50% for 24 h (Capability-profile parameter; illustrative) Maximum tolerable lost training progress [hours of training] default 2 (Capability-profile parameter; illustrative) | Approved impact tolerance records per Service Outcome; Approval record by the accountable executive; Reconciliation to risk appetite and customer commitments | DOCUMENT_REVIEW; RECONCILIATION; ANALYSIS | 1) Obtain tolerance records and approvals for each Service Outcome. 2) Check coverage of the four tolerance dimensions and operating states. 3) Reconcile to risk appetite limits and customer commitments. 4) Assess each tolerance for testability. | DIRECTIVE | DESIGN | AL2 | PLAN; DESIGN; CHANGE | NORMAL; DEGRADED; EMERGENCY; RECOVERY | Applies to every Service Outcome of every in-scope Capability Instance. | CG-01 |  | Tolerance stated qualitatively ('minimal disruption'); Tolerance looser than customer SLA; No tolerance for degraded capacity, only total outage; Tolerance not approved | ServiceOutcome; CapabilityInstance; OperatingState | Desk review only; tolerances are not validated by inducing disruption under this control. | A tolerance that exists but is not testable makes criterion 5 PARTIAL; UNKNOWN is recorded only if the approval cannot be evidenced. | ISO 22301 (business continuity management systems); ISO 22317 (business impact analysis); ISO 31000 (risk management guidelines) | MCF-CAP-005; MCF-CAP-008; MCF-GOV-014; MCF-GOV-007 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-CAP-011 | CAP | AI Capability, Service Outcome and Demand Management | CAP-03 | Criticality and materiality | Stakeholder Consequence | Identify who is harmed, and how, when each Service Outcome is not met (internal research teams, external tenants, downstream services relying on inference, safety-relevant users), so that criticality and tolerances reflect real consequence chains. | The capability owner shall record, for each Service Outcome, the stakeholder groups affected by its failure, the consequence mechanism (for example lost training progress, failed inference for a dependent service, breach of a regulatory obligation), the consequence severity under each operating state and any downstream dependency outside the boundary. The capability owner shall review the analysis with representatives of affected stakeholder groups at least once per planning period. | 1) Each Service Outcome lists affected stakeholder groups and consequence mechanisms. 2) Consequence severity is stated per operating state. 3) Downstream services outside the boundary that depend on the outcome are identified. 4) Representatives of affected stakeholder groups reviewed the analysis in the current planning period. 5) The analysis is reflected in criticality classification and impact tolerances. |  | Stakeholder consequence analysis per Service Outcome; Stakeholder review records; Traceability to criticality and tolerances | DOCUMENT_REVIEW; INQUIRY; ANALYSIS | 1) Obtain the consequence analysis and check coverage per outcome and state. 2) Interview at least one affected stakeholder representative. 3) Check identification of downstream dependent services. 4) Trace the analysis to criticality and tolerance records. | DIRECTIVE | DESIGN | AL2 | PLAN; DESIGN | NORMAL; DEGRADED; FAILED | Applies to every Service Outcome; where the only stakeholder is the owner's own research function, the analysis may be brief but is still required. |  | CG-01 | Inference outage affects a dependent safety-relevant service not considered; Tenants' contractual exposure unknown to the owner; Consequence in degraded state ignored | ServiceOutcome; Dependency; OperatingState | Interview and desk review only; stakeholder interviews do not disclose other stakeholders' confidential information. | If an affected stakeholder group cannot be consulted, record a U2 UNKNOWN against its consequence entry. | ISO 22317 (business impact analysis); ISO 22301 (business continuity management systems) | MCF-CAP-009; MCF-CAP-010; MCF-GOV-017 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-CAP-012 | CAP | AI Capability, Service Outcome and Demand Management | CAP-03 | Criticality and materiality | Priority Classification | Ensure that the relative priority of workloads, tenants and Capability Instances is defined and implemented in the mechanisms that allocate scarce resources during degradation (power capping, load shedding, thermal curtailment, scheduler pre-emption), so that the most critical outcomes are protected first. | The capability owner shall define priority classes for workloads, tenants and Capability Instances derived from criticality, and the AI platform owner and facility operator shall implement those classes in scheduler pre-emption policies, power-capping and load-shedding sequences and thermal curtailment procedures. The capability owner shall confirm at the priority reconciliation interval that implemented sequences match the defined classes. | 1) Priority classes are defined and derived from criticality classification. 2) Scheduler pre-emption and quota configuration implement the priority classes. 3) Power-capping and load-shedding sequences (EPMS or rack power management) and thermal curtailment procedures implement the same priority order. 4) Reconciliation of implemented sequences to priority classes is within the interval. 5) No safety-related or control-plane load is placed in a shed group ahead of AI workload. | Priority reconciliation interval [months] default 6 (Capability-profile parameter; illustrative) | Priority class definitions; Scheduler pre-emption and quota configuration export; Load-shedding and power-capping sequence configuration; Thermal curtailment procedure; Reconciliation record | RECONCILIATION; INSPECTION; DOCUMENT_REVIEW | 1) Review priority class definitions and their derivation from criticality. 2) Export scheduler pre-emption and quota configuration and map to classes. 3) Export load-shedding and power-capping sequences and review thermal curtailment procedures; map to classes. 4) Confirm that safety and control-plane loads are not shed before AI workloads. 5) Check the reconciliation record date. | PREVENTIVE | IMPLEMENTATION | AL3 | DESIGN; COMMISSION; OPERATE; CHANGE | NORMAL; DEGRADED; EMERGENCY | Applies to instances where any resource can become constrained in a degraded state; that is all instances with shared power or cooling. |  | CG-05; CG-06 | Load shedding drops the highest-priority tenant first; Power capping applied uniformly, degrading critical inference; Control-plane servers in the same shed group as training racks; Scheduler pre-emption contradicts facility priority | Safeguard; CapabilityInstance; OperatingState | Read-only configuration export; shed sequences are not exercised under this control. Any sequence test is performed under the POW or THM domain controls with their authorisation requirements. | If EPMS shed-sequence configuration cannot be exported, record a U2 UNKNOWN against criterion 3. | IEC 60364 series (low-voltage electrical installations); ISO/IEC 20000-1 (service management system) | MCF-CAP-009; MCF-CAP-017; MCF-CAP-020 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-CAP-013 | CAP | AI Capability, Service Outcome and Demand Management | CAP-04 | Demand and growth modelling | Current Demand Baseline | Establish a measured baseline of the current IT, cooling and network demand of each Capability Instance (electrical load per pod and hall, heat rejected to air and liquid, facility water flow, fabric utilisation, storage throughput) from telemetry over a representative period, so that capacity and headroom claims rest on measurement rather than nameplate. | The capacity manager shall establish, for each Capability Instance, a demand baseline derived from telemetry over at least the baseline period, covering electrical demand at rack, row, pod and hall level, heat load to air and to liquid, facility water flow and temperatures, and fabric and storage utilisation. The capacity manager shall state telemetry sources, resolution, gaps and calibration status, and refresh the baseline at the baseline refresh interval and after material change. | 1) The baseline covers electrical, thermal (air and liquid), facility water, fabric and storage demand for each instance. 2) The baseline is derived from telemetry over at least the baseline period, with sources, resolution and gaps stated. 3) Metering used for electrical and thermal baselines has current calibration or accuracy verification. 4) Baseline values reconcile to an independent source for a sample (for example utility meter, UPS output, CDU heat-meter readings). 5) The baseline was refreshed within the interval and after each material change. | Baseline period [days] default 90 (Capability-profile parameter; illustrative, should include representative workload cycles) Baseline telemetry resolution [seconds] default 60 (Capability-profile parameter; illustrative, transient characterisation is addressed in MCF-CAP-014) Baseline refresh interval [months] default 3 (Capability-profile parameter; illustrative) | Demand baseline report with methods and sources; Telemetry extracts for the baseline period; Meter calibration or verification records; Independent reconciliation sample | ANALYSIS; RECONCILIATION; INSPECTION; REPERFORMANCE | 1) Obtain the baseline report and check coverage across domains. 2) Obtain raw telemetry and reperform aggregation for one hall or pod. 3) Review meter calibration and telemetry gap records. 4) Reconcile a sample of baseline values to independent sources. 5) Check refresh dates against the interval and change events. | DETECTIVE | OPERATION | AL4 | COMMISSION; OPERATE; CHANGE | NORMAL; MAINTENANCE | Applies to every in-service Capability Instance. For instances in design, MCF-CAP-015 forecasts substitute until in service. |  | CG-05; CG-06 | Headroom claimed from nameplate ratings while actual load is far higher; Liquid heat load not metered, so cooling headroom is guessed; Telemetry gaps conceal peak periods; Uncalibrated meters bias the baseline | CapacityAssertion; Resource; InfrastructureSystem | Read-only telemetry extraction; no meter is disconnected or tested under this control. | If telemetry gaps exceed 10% of the baseline period or calibration status is unknown for a primary meter, record a U5 or U6 UNKNOWN and limit the baseline to the covered portion. | ISO/IEC 30134 series (data centre key performance indicators); ISO 50001 (energy management systems); ASHRAE TC 9.9 thermal guidelines for data processing environments | MCF-CAP-014; MCF-CAP-015; MCF-CAP-017 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-CAP-014 | CAP | AI Capability, Service Outcome and Demand Management | CAP-04 | Demand and growth modelling | Peak and Transient Demand | Characterise the peak and fast-transient demand of AI workloads (synchronous training power swings at iteration and checkpoint boundaries, job start and stop steps, inrush on restart, rapid heat-load changes on liquid loops) so that UPS, generation, grid connection, protection and cooling control are sized and tuned for real dynamics. | The capacity manager, with the electrical and mechanical leads, shall characterise for each Capability Instance the peak demand and the transient demand profile, stating the maximum step change, ramp rate and repetition frequency of electrical load and heat load, measured at a resolution sufficient to resolve the transients, under representative workloads including job start, synchronous training, checkpointing and job failure. The capacity manager shall provide the characterisation to the POW and THM design owners and to the grid connection owner, and refresh it after any change in accelerator generation, workload type or power-management configuration. | 1) Peak electrical and thermal demand per pod and hall is stated with its measurement basis. 2) The transient profile states maximum step change, ramp rate and repetition frequency for electrical and heat load. 3) Measurements were taken at a resolution sufficient to resolve the stated transients and under the representative workload set (job start, synchronous training, checkpoint, job failure). 4) The characterisation was provided to POW and THM design owners and the grid connection owner, with recorded acknowledgement. 5) The characterisation was refreshed after each change in accelerator generation, workload type or power-management configuration. | Transient measurement resolution [ms] default 100 or finer (Capability-profile parameter; illustrative, must resolve the fastest step of interest) Maximum load step change [% of pod IT load] default measured; no default (Measured characteristic, not a design default) Maximum ramp rate [kW per second per pod] default measured; no default (Measured characteristic, not a design default) | Peak and transient characterisation report; High-resolution power-quality or meter captures for representative workloads; Heat-load and facility water temperature transient captures from CDUs or heat meters; Distribution records to POW, THM and grid connection owners; Workload schedule showing representative workloads during capture | ANALYSIS; INSPECTION; DOCUMENT_REVIEW; INQUIRY | 1) Obtain the characterisation report and check peak and transient attributes. 2) Examine raw captures and confirm resolution and workload coverage against the workload schedule. 3) Have an electrical specialist review the capture method and a mechanical specialist review heat-load transients. 4) Confirm distribution to POW, THM and grid connection owners. 5) Check refresh against change events. | DETECTIVE | OPERATION | AL4 | DESIGN; COMMISSION; OPERATE; CHANGE | NORMAL; TRANSITION; RECOVERY | Applies to every instance running synchronous distributed training or other workloads with coordinated load changes; for inference-only instances with smoothed load the characterisation may be limited to peak and start-up steps, with rationale. |  | CG-05; CG-06 | Synchronous training load steps cause UPS or generator instability; Grid connection ramp-rate condition breached; Upstream protection trips on restart inrush; CDU control loop hunts under rapid heat-load swings, causing temperature overshoot | CapacityAssertion; Resource; FailureMode; InfrastructureSystem | Connection of power-quality analysers to live switchgear is hazardous-energy work and shall be performed only by authorised electrical personnel under the site's safe system of work and permit, with arc-flash PPE appropriate to the incident-energy study. The assessor observes; the assessor does not connect instruments. Workload scheduling for captures is arranged by the platform owner on capacity they control. | If no capture at sufficient resolution exists, record a U1 UNKNOWN; average-interval telemetry shall not be used to infer the absence of transients. | IEC 61000-4-30 (power quality measurement methods); IEC 62040-3 (UPS performance and test requirements); ASHRAE TC 9.9 liquid cooling guidelines | MCF-CAP-013; MCF-CAP-017; MCF-CAP-016; MCF-GOV-017 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-CAP-015 | CAP | AI Capability, Service Outcome and Demand Management | CAP-04 | Demand and growth modelling | Growth Forecast | Forecast demand growth for each Capability Instance (accelerator count, power per accelerator, rack density, liquid-cooled fraction, fabric scale, storage capacity and throughput) over the planning horizon so that power, cooling, space and supply-chain lead times are committed before demand arrives. | The capacity manager shall maintain a growth forecast for each Capability Instance over the planning horizon stating expected accelerator deployments by generation, power per accelerator and rack, liquid-cooled fraction, fabric and storage scale, with the assumptions and their sources, an uncertainty range, and the date by which each infrastructure commitment must be made given supplier and utility lead times. The capability owner shall approve the forecast and review it against actuals at the forecast review interval. | 1) A forecast exists per instance covering accelerators, power per rack, liquid-cooled fraction, fabric and storage over the planning horizon. 2) Assumptions are stated with sources and an uncertainty range. 3) Commitment dates are derived from stated lead times for power (including grid connection), cooling plant, and long-lead equipment. 4) The forecast is approved by the capability owner and was compared with actuals at the review interval. 5) Forecast values at the upper end of the uncertainty range are compared with site power and cooling limits. | Planning horizon [months] default 36 (Capability-profile parameter; illustrative) Forecast review interval [months] default 6 (Capability-profile parameter; illustrative) | Approved growth forecast with assumptions and uncertainty; Lead-time register for utility and long-lead equipment; Forecast-versus-actual review records; Comparison to site limits | DOCUMENT_REVIEW; ANALYSIS; REPERFORMANCE | 1) Review forecast coverage, assumptions and uncertainty. 2) Reperform a commitment-date derivation from lead times. 3) Compare upper-range values with site limits. 4) Review forecast-versus-actual records. | DIRECTIVE | DESIGN | AL2 | PLAN; DESIGN; OPERATE | NORMAL | Applies to instances expected to grow within the planning horizon; static instances record 'no growth' as an approved forecast. |  |  | Accelerators delivered before liquid cooling capacity exists; Grid connection lead time exceeds forecast need; Rack density growth exceeds floor loading or busway rating; Forecast never compared with actuals | CapacityAssertion; CapabilityInstance; Resource | Desk review only; forecasts are commercially sensitive and handled under restriction. | If the source of a key assumption (for example power per accelerator for an unreleased generation) cannot be identified, record a U6 UNKNOWN and widen the uncertainty range. | ISO/IEC 30134 series (data centre key performance indicators); ISO 55000 series (asset management) - asset planning | MCF-CAP-013; MCF-CAP-016; MCF-CAP-017 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-CAP-016 | CAP | AI Capability, Service Outcome and Demand Management | CAP-04 | Demand and growth modelling | Scenario Demand | Characterise demand under adverse and recovery scenarios (simultaneous restart after power loss, checkpoint-restore storage bursts, failover of load to surviving halls, cooling recovery with high residual heat) and validate it in exercise, so that recovery does not itself overload power, cooling, fabric or storage. | The capacity manager, with the resilience lead, shall model for each Capability Instance the demand on power, cooling, fabric and storage during the declared recovery and failover scenarios (including restart inrush, checkpoint-restore read bursts, re-scheduling storms and transfer of load to surviving fault domains), shall define the staging that keeps demand within supply during recovery, and shall validate the model and staging in at least one recovery exercise per exercise interval. | 1) Recovery and failover scenarios are listed with modelled demand on power, cooling, fabric and storage. 2) Restart inrush, checkpoint-restore bursts and re-scheduling load are included where applicable. 3) A staging plan keeps modelled demand within available supply in each recovery step. 4) At least one recovery exercise in the interval measured actual demand against the model and staging. 5) Differences between measured and modelled demand were analysed and the model or staging updated. | Scenario demand exercise interval [months] default 12 (Capability-profile parameter; illustrative) Restart staging group size [% of instance accelerators per step] default 25 (Capability-profile parameter; illustrative) | Scenario demand model; Recovery staging plan; Exercise record with measured demand; Model-versus-measured analysis and updates | ANALYSIS; SCENARIO_EXERCISE; DOCUMENT_REVIEW; OBSERVATION | 1) Review the scenario list and modelled demand by domain. 2) Check staging plan against available supply per step. 3) Examine the exercise record and measured demand; observe an exercise if one is scheduled. 4) Compare measured with modelled demand and review the resulting updates. | RECOVERY | RESILIENCE | AL5 | DESIGN; COMMISSION; OPERATE; CHANGE | RECOVERY; TRANSITION; DEGRADED | Applies to instances whose recovery outcomes require restoration of more than one fault domain or of large accelerator populations; small single-rack instances may record NOT_APPLICABLE with rationale. |  | CG-10; CG-05 | Simultaneous restart of all racks trips upstream breakers; Checkpoint restore saturates the storage system and extends RTO; Failover of load to a surviving hall exceeds its cooling capacity; Scheduler re-queue storm overloads the control plane | FailureScenario; CapacityAssertion; OperatingState; TestRecord | Recovery exercises that energise or de-energise equipment, restart cooling plant or perform restart of accelerator populations are hazardous-energy and service-affecting activities: they require written authorisation from the capability owner and facility operator, a method statement with abort criteria and initial-state verification, permits under the site safe system of work, and the safety authority's right to stop. Assessors observe and do not operate equipment. | If no exercise has measured recovery demand, the RESILIENCE claim is UNKNOWN (U1); the model alone supports only a DESIGN-level statement. | ISO 22301 (business continuity management systems) - exercising and testing; ISO 22398 (guidelines for exercises); IEC 62040-3 (UPS performance and test requirements) | MCF-CAP-008; MCF-CAP-014; MCF-CAP-019; MCF-CAP-020 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-CAP-017 | CAP | AI Capability, Service Outcome and Demand Management | CAP-05 | Operating envelope | Load Envelope | Define and enforce the electrical and thermal load envelope of each Capability Instance (maximum IT load per rack, row, pod and hall; maximum liquid heat load per CDU loop; power per accelerator) and ensure mechanisms prevent load from exceeding it. | The capability architect shall define, for each Capability Instance, the load envelope: maximum IT power per rack, row, pod and hall, maximum heat load per CDU or liquid loop, and permitted power per accelerator, each derived from the lowest-rated element in the power and cooling path in the declared redundancy state. The AI platform owner and facility operator shall implement enforcement (power capping, admission control for new racks or jobs, alarm thresholds) and shall verify that configured limits equal the envelope. | 1) The envelope states rack, row, pod, hall and CDU loop limits and power per accelerator. 2) Each limit is derived from the lowest-rated element in its path in the declared redundancy state, with the derivation recorded. 3) Enforcement mechanisms (power capping, admission control, alarm thresholds) are configured at or below the envelope. 4) Configured limits reconcile to the envelope for a sample of racks, pods and loops. 5) Envelope exceedances in the period, if any, were alarmed and actioned. | Design margin below lowest-rated element [% of rating] default 10 (Capability-profile parameter; illustrative) | Load envelope definition with derivations; Power-capping and admission-control configuration export; BMS/EPMS alarm threshold configuration; Exceedance alarm and action records | RECONCILIATION; INSPECTION; ANALYSIS; DOCUMENT_REVIEW | 1) Review envelope limits and derivations against path element ratings. 2) Export enforcement configurations and alarm thresholds. 3) Reconcile a sample of configured limits to the envelope. 4) Review exceedance alarms and actions in the period. | PREVENTIVE | IMPLEMENTATION | AL3 | DESIGN; COMMISSION; OPERATE; CHANGE | NORMAL; DEGRADED; MAINTENANCE | Applies to every in-service Capability Instance. |  | CG-05; CG-06 | Rack load exceeds busway or PDU rating; CDU loop heat load exceeds capacity in N state after a pump failure; Power capping disabled for a benchmark and not restored; New racks deployed without envelope check | CapacityAssertion; Safeguard; InfrastructureSystem | Read-only configuration export; capping and admission control are not tested by overloading equipment. | If the rating of a path element cannot be established, record a U1 UNKNOWN against the derived limit and treat the envelope for that path as unverified. | IEC 60364 series (low-voltage electrical installations); ASHRAE TC 9.9 liquid cooling guidelines; ISO/IEC 22237 series (data centre facilities and infrastructures) | MCF-CAP-013; MCF-CAP-014; MCF-CAP-018; MCF-CAP-020 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-CAP-018 | CAP | AI Capability, Service Outcome and Demand Management | CAP-05 | Operating envelope | Environmental Envelope | Define the environmental envelope the AI equipment requires (air inlet temperature and humidity, facility water and technology cooling system supply temperature, flow and pressure, coolant quality) by reference to OEM specifications and recognised thermal guidelines, and ensure setpoints and alarms enforce it. | The capability architect shall define, for each Capability Instance, the environmental envelope covering air inlet temperature and humidity, technology cooling system and facility water supply temperature, minimum flow and differential pressure, and coolant quality, derived from accelerator and server OEM specifications and the applicable ASHRAE TC 9.9 classes. The facility operator shall configure BMS and CDU setpoints and alarm thresholds within the envelope and shall reconcile them to the envelope after every OEM specification revision. | 1) The envelope covers air temperature and humidity, liquid supply temperature, flow, differential pressure and coolant quality. 2) Each envelope value cites the OEM specification or ASHRAE TC 9.9 class from which it is derived. 3) BMS and CDU setpoints and alarm thresholds for a sample of zones and loops lie within the envelope. 4) Setpoints were reconciled after each OEM specification revision in the period. 5) Where OEM limits differ across equipment sharing a loop, the most restrictive limit is applied. | Air inlet temperature range [degC] default 18-27 (ASHRAE TC 9.9 recommended envelope for air-cooled IT; OEM limits prevail where stricter) Technology cooling system supply temperature upper limit [degC] default per OEM specification (OEM specification; no generic default) | Environmental envelope definition with sources; OEM specification extracts; BMS and CDU setpoint and alarm configuration export; Reconciliation records after OEM revisions | RECONCILIATION; INSPECTION; DOCUMENT_REVIEW | 1) Review envelope values and their sources. 2) Export BMS and CDU setpoints and alarm thresholds. 3) Reconcile a sample of zones and loops to the envelope, applying the most restrictive OEM limit. 4) Check reconciliation after OEM revisions. | PREVENTIVE | IMPLEMENTATION | AL3 | DESIGN; COMMISSION; OPERATE; CHANGE | NORMAL; DEGRADED | Applies to every in-service Capability Instance; liquid-cooling criteria apply where liquid cooling is used. |  | CG-06 | Facility water supply temperature raised for efficiency beyond accelerator OEM limits; Flow alarm threshold below OEM minimum; Mixed-generation loop set to the less restrictive limit; Humidity outside envelope causing condensation risk on cold plates | OperatingState; Safeguard; InfrastructureSystem | Read-only export of BMS and CDU configuration; no setpoint is changed during assessment. | If an OEM specification is unavailable for installed equipment, record a U1 UNKNOWN against the affected envelope value; a generic guideline value shall not be substituted without approval. | ASHRAE TC 9.9 thermal guidelines for data processing environments; ASHRAE TC 9.9 liquid cooling guidelines; ISO/IEC 22237 series (data centre facilities and infrastructures) - environmental control | MCF-CAP-017; MCF-CAP-019; MCF-CAP-006 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-CAP-019 | CAP | AI Capability, Service Outcome and Demand Management | CAP-05 | Operating envelope | Duration Limits | Establish and validate how long each Capability Instance can sustain its outcomes in each degraded condition (UPS autonomy at actual load, thermal ride-through of liquid loops and rooms on loss of cooling, fuel autonomy, time on reduced redundancy) so that response and recovery actions are timed within real limits. | The capability architect shall state, for each Capability Instance, duration limits for each declared degraded condition: battery autonomy at measured load, thermal ride-through time before equipment limits are reached on loss of chilled or facility water, generator fuel autonomy, and maximum time on reduced redundancy. The facility operator shall validate each limit by test, measurement or validated model at the duration validation interval and after material change, and shall align alarms and runbooks to the validated limits. | 1) Duration limits are stated for each declared degraded condition, including UPS autonomy, thermal ride-through, fuel autonomy and reduced-redundancy time. 2) Each limit is validated by test, measured event or validated model at current load. 3) Thermal ride-through validation accounts for the actual liquid-cooled heat load and thermal mass of the loops. 4) Alarms and runbooks trigger actions with sufficient margin before each validated limit. 5) Validation is within the interval and after material change. | Duration validation interval [months] default 12 (Capability-profile parameter; illustrative) Thermal ride-through on loss of facility water [minutes] default validated value; no default (Validated characteristic, not a design default) Response margin before limit [% of validated duration] default 50 (Capability-profile parameter; illustrative) | Duration limit statement; UPS autonomy test or discharge record at measured load; Thermal ride-through test, event record or validated model; Fuel autonomy calculation with measured consumption; Alarm and runbook timing extracts | TEST; ANALYSIS; DOCUMENT_REVIEW; OBSERVATION | 1) Review stated limits for completeness across degraded conditions. 2) Examine validation evidence for each limit and its load basis. 3) Have a mechanical specialist review thermal ride-through validation against liquid heat load and loop thermal mass. 4) Compare alarm and runbook timings with validated limits and margin. 5) Observe a scheduled validation test where one occurs in the assessment window. | PREVENTIVE | EFFECTIVENESS | AL5 | COMMISSION; OPERATE; CHANGE | DEGRADED; EMERGENCY; MAINTENANCE | Applies to every in-service instance; fuel autonomy is not applicable where no on-site generation exists, with rationale. |  | CG-05; CG-06; CG-10 | UPS autonomy at today's AI load is a fraction of the design value; Liquid-cooled racks exceed thermal limits within seconds of facility water loss, faster than runbook response; Fuel autonomy calculated from nameplate consumption; Extended operation on N redundancy unnoticed | OperatingState; CapacityAssertion; TestRecord; Safeguard | UPS discharge and cooling-interruption tests are hazardous and service-affecting: they require written authorisation from the facility operator and capability owner, an engineered method statement with initial-state verification, abort criteria and restoration steps, load banks or protected test loads where possible, permits under the site safe system of work, and a safety authority able to stop the test. Thermal ride-through on production accelerators shall not be tested by deliberately stopping cooling; a calibrated model or measured event is used instead. | If a limit has never been validated at current load, record a U3 (stale) or U1 UNKNOWN; design values shall not be presented as validated. | IEC 62040-3 (UPS performance and test requirements); IEEE 1188 (maintenance and testing of VRLA batteries); ISO 8528 series (reciprocating engine generating sets); ASHRAE TC 9.9 liquid cooling guidelines | MCF-CAP-016; MCF-CAP-018; MCF-CAP-020; MCF-CAP-010 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-CAP-020 | CAP | AI Capability, Service Outcome and Demand Management | CAP-05 | Operating envelope | State-Specific Limits | Define and enforce limits that apply only in non-normal operating states (maintenance with reduced redundancy, degraded cooling, emergency, recovery, transition) so that permitted load, activities and changes are restricted when margins are smaller. | The capability architect shall define for each Capability Instance the limits applying in each non-normal operating state, including maximum permitted IT load, prohibited activities (for example concurrent maintenance on both power paths, firmware rollouts, large job starts), required approvals and maximum duration. The facility operator and AI platform owner shall implement these limits in maintenance permits, change freezes, scheduler policies and power-capping profiles, and shall record state entry and exit. | 1) State-specific limits are defined for MAINTENANCE, DEGRADED, EMERGENCY, RECOVERY and TRANSITION states. 2) Limits include permitted load, prohibited activities, approvals and maximum duration. 3) Maintenance permits, change freezes, scheduler policies and capping profiles implement the limits. 4) State entry and exit events in the period are recorded. 5) For a sample of non-normal state periods, telemetry and change records show the limits were respected. | Maximum IT load in reduced-redundancy maintenance [% of normal envelope] default per redundancy study; no default (Derived from POW/THM redundancy studies) | State-specific limit definitions; Maintenance permits and change freeze records; Scheduler and capping profile configuration for non-normal states; State entry/exit log; Telemetry and change records for sampled state periods | DOCUMENT_REVIEW; SAMPLING; ANALYSIS; RECONCILIATION | 1) Review limit definitions for each non-normal state. 2) Inspect implementation in permits, freezes, scheduler policies and capping profiles. 3) Sample non-normal state periods from the log. 4) Analyse telemetry and change records for each sampled period against the limits. | PREVENTIVE | OPERATION | AL4 | DESIGN; OPERATE; CHANGE | MAINTENANCE; DEGRADED; EMERGENCY; RECOVERY; TRANSITION | Applies to every in-service instance. |  | CG-09; CG-10 | Full AI load run during maintenance on one power path, so a second fault drops the hall; Firmware rollout during degraded cooling; Large job start during recovery overloads restored supply; Maintenance state left open beyond its duration | OperatingState; Safeguard; FaultDomain | Record and telemetry review only; no state transition is induced. | If state entry and exit cannot be reconstructed for a period, record a U5 UNKNOWN for that period. | ISO/IEC 22237 series (data centre facilities and infrastructures) - operational information; ISO/IEC 20000-1 (service management system) - change management | MCF-CAP-017; MCF-CAP-019; MCF-CAP-012; MCF-CAP-016 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-CAP-021 | CAP | AI Capability, Service Outcome and Demand Management | CAP-06 | Capability lifecycle and change | Design-to-Operation Traceability | Ensure that design intent (Service Outcomes, envelopes, redundancy, fault domains) is traceable through build and commissioning into the operating configuration, so that differences between designed, installed, commissioned and operated states are visible. | The capability architect shall maintain traceability from each Service Outcome and envelope to design requirements, to as-built records, to commissioning results and to the current operating configuration for each Capability Instance, recording deviations at each stage with disposition. The facility operator and AI platform owner shall provide current configuration evidence for reconciliation at the traceability reconciliation interval. | 1) Traceability links exist from Service Outcomes and envelopes to design requirements, as-built records, commissioning results and operating configuration. 2) Deviations at each stage are recorded with disposition. 3) A sample traced end to end shows no undisclosed deviation between design and operating configuration. 4) Reconciliation to current configuration is within the interval. 5) Designed, installed, commissioned and operated states are recorded distinctly, not overwritten. | Traceability reconciliation interval [months] default 12 (Capability-profile parameter; illustrative) | Traceability matrix or graph extract; Design requirement records; As-built records; Commissioning results; Current configuration exports; Deviation register | RECONCILIATION; SAMPLING; DOCUMENT_REVIEW; INSPECTION | 1) Obtain the traceability matrix or graph extract. 2) Select samples across domains and trace each from outcome to operating configuration. 3) Compare deviations found with the deviation register. 4) Confirm states are recorded distinctly and reconciliation is within interval. | DETECTIVE | IMPLEMENTATION | AL3 | DESIGN; BUILD; COMMISSION; OPERATE | NORMAL | Applies to every instance assessed at AL3 or above. |  | CG-02 | Redundancy designed as 2N but operated as N+1 after an undocumented change; As-built CDU configuration differs from design; Commissioning results overwritten by later configuration; Design envelope not carried into operating limits | ArchitectureSnapshot; ServiceOutcome; InfrastructureSystem; TestRecord | Read-only configuration exports; site inspection under escort without operating equipment. | If any stage record (design, as-built, commissioning) is missing for a sampled trace, record a U1 UNKNOWN for that stage and do not infer it from the adjacent stage. | ISO/IEC/IEEE 15288 (system life cycle processes); ISO/IEC/IEEE 42010 (architecture description); ASHRAE Guideline 0 (the commissioning process) | MCF-CAP-004; MCF-CAP-022; MCF-GOV-010 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-CAP-022 | CAP | AI Capability, Service Outcome and Demand Management | CAP-06 | Capability lifecycle and change | Commissioning Acceptance | Ensure that a Capability Instance, or an expansion of it, is accepted into service only after integrated commissioning demonstrates that the combined power, cooling, control, compute, storage and network systems deliver the Service Outcomes under normal and declared degraded conditions. | The commissioning manager shall plan and execute integrated systems testing for each new or expanded Capability Instance that exercises power, cooling, control systems, compute, storage and fabric together at representative load, including declared failure transfers (for example loss of a UPS module, CDU pump failover, loss of a fabric link) and their effect on Service Outcomes. The capability owner shall sign acceptance only when acceptance criteria tied to Service Outcomes are met or deviations are dispositioned, and shall record the accepted configuration baseline. | 1) An integrated test plan exists with acceptance criteria traced to Service Outcomes and envelopes. 2) Tests were executed at representative load, including heat load to liquid loops where liquid cooled. 3) Declared failure transfers were exercised and their effect on Service Outcomes measured. 4) Every failed or deferred test has a disposition approved by the capability owner before acceptance. 5) Acceptance was signed by the capability owner and the accepted configuration baseline recorded. 6) Commissioning results are retained as E4 evidence with test conditions and anomalies. | Commissioning test load [% of design IT load] default 100 (Capability-profile parameter; illustrative, using load banks or representative workloads) | Integrated test plan with acceptance criteria; Executed test scripts with results, conditions and anomalies; Failure-transfer test records; Deviation dispositions; Signed acceptance and accepted configuration baseline | DOCUMENT_REVIEW; TEST; OBSERVATION; RECONCILIATION | 1) Review the test plan and trace acceptance criteria to Service Outcomes. 2) Examine executed scripts for load, conditions and anomalies. 3) Examine failure-transfer tests and measured outcome effects. 4) Review deviation dispositions and acceptance signature. 5) Reconcile accepted baseline to current configuration; observe commissioning if in progress. | PREVENTIVE | EFFECTIVENESS | AL5 | COMMISSION; CHANGE | NORMAL; DEGRADED; TRANSITION | Applies to every new Capability Instance and every expansion or major reconfiguration; for capability in a colocation facility, facility-level commissioning by the provider is assessed through MCF-SUP controls and integrated testing remains required at the capability boundary. |  | CG-02; CG-08; CG-14 | Systems commissioned individually but never together under heat load; CDU failover untested at full liquid load; Acceptance signed with open critical tests; Accepted baseline not recorded, so later drift is undetectable | TestRecord; CapabilityInstance; ArchitectureSnapshot; ServiceOutcome | Integrated systems tests involve energised switching, load banks, pressurised liquid loops and induced failures: they require an approved commissioning method statement, initial-state verification, abort criteria, isolation and permits under the site safe system of work, competent operators, and a safety authority with stop authority. Assessors observe from a designated position and do not operate equipment. | If test records lack conditions (load, state, configuration), record a U8 UNKNOWN against the affected test; the result shall not be used as effectiveness evidence. | ASHRAE Guideline 0 (the commissioning process); ASHRAE Standard 202 (commissioning process for buildings and systems); ISO/IEC 22237 series (data centre facilities and infrastructures); IEC 62040-3 (UPS performance and test requirements) | MCF-CAP-021; MCF-CAP-003; MCF-CAP-023 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-CAP-023 | CAP | AI Capability, Service Outcome and Demand Management | CAP-06 | Capability lifecycle and change | Material Change Impact | Ensure that every proposed change that could affect a Capability Instance's Service Outcomes, envelopes, fault domains or dependencies (accelerator refresh, density increase, cooling conversion, fabric expansion, provider change) is assessed for capability impact, validated after implementation and used to trigger reassessment. | The capability owner shall ensure that every change classified as material for a Capability Instance has a capability impact assessment before approval that identifies affected Service Outcomes, envelopes, fault domains, dependencies, controls, gates and evidence; defines post-change validation; and identifies assurance claims to be suspended or reassessed. The change authority shall not approve a material change without the impact assessment, and the capability owner shall confirm post-change validation before the change is closed. | 1) Materiality criteria for capability changes are defined and applied to every change in the period. 2) Every material change in the sample had a capability impact assessment before approval identifying outcomes, envelopes, fault domains, dependencies, controls, gates and evidence. 3) Every material change in the sample had post-change validation confirmed by the capability owner before closure. 4) Assurance claims identified as affected were suspended or scheduled for reassessment. 5) A sample of changes classified non-material shows no misclassification. |  | Change materiality criteria; Change log for the period with materiality classification; Capability impact assessments for sampled material changes; Post-change validation records; Reassessment or suspension records triggered | SAMPLING; DOCUMENT_REVIEW; RECONCILIATION; ANALYSIS | 1) Review materiality criteria and their application across the change log. 2) Sample material changes and verify impact assessments preceded approval. 3) Verify post-change validation before closure. 4) Trace affected claims to suspension or reassessment records. 5) Sample non-material changes and test classification. | PREVENTIVE | OPERATION | AL4 | CHANGE; OPERATE | NORMAL; TRANSITION; MAINTENANCE | Applies to every change affecting an in-scope Capability Instance, whether initiated by the owner, operator or a provider. | CG-14 | CG-01 | Accelerator refresh raises rack power beyond the cooling envelope without assessment; Conversion from air to liquid cooling not treated as material; Provider changes a shared dependency without notification; Change closed without validation; Prior assurance relied on after material change | Event; ReassessmentTrigger; CapabilityInstance; Action | Record review only; post-change validation tests are assessed under the relevant domain controls with their own safety requirements. | If changes made by providers cannot be enumerated, record a U10 UNKNOWN (dependency unknown) against the provider's changes and treat CG-14 as UNKNOWN for affected dependencies. | ISO/IEC 20000-1 (service management system) - change management; ISO/IEC/IEEE 15288 (system life cycle processes); ISO 55000 series (asset management) | MCF-EVA-022; MCF-GOV-011; MCF-CAP-022; MCF-CAP-024 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-CAP-024 | CAP | AI Capability, Service Outcome and Demand Management | CAP-06 | Capability lifecycle and change | Retirement Control | Ensure that retiring all or part of a Capability Instance (decommissioning racks, draining liquid loops, removing storage, ending a provider service) is controlled so that remaining outcomes, data protection and safety are not compromised and records are updated. | The capability owner shall approve a retirement plan for each retirement of capability or infrastructure that identifies remaining Service Outcomes affected, dependencies to be removed or transferred, data sanitisation of storage media and accelerator memory, safe isolation and draining of liquid loops and disposal of batteries and coolant, and updates to the capability register, architecture snapshot and assurance graph. The facility operator shall confirm completion of each step with evidence. | 1) Each retirement in the period had an approved plan covering affected outcomes, dependencies, data sanitisation, safe isolation and disposal, and record updates. 2) Data sanitisation of retired storage media is evidenced to the required sanitisation level. 3) Liquid loops were isolated and drained, and batteries and coolant disposed of under safe-work and environmental requirements. 4) Capability register, architecture snapshot and assurance graph were updated within the record update time. 5) Remaining Service Outcomes were verified after retirement. | Record update time after retirement [working days] default 10 (Capability-profile parameter; illustrative) | Approved retirement plans; Data sanitisation certificates or records; Isolation, draining and disposal records; Register, snapshot and graph update records; Post-retirement outcome verification | DOCUMENT_REVIEW; RECONCILIATION; SAMPLING; INSPECTION | 1) List retirements in the period and obtain plans. 2) Reconcile sanitisation records to retired asset serial numbers. 3) Review isolation, draining and disposal records. 4) Verify record updates and post-retirement outcome verification. | PREVENTIVE | IMPLEMENTATION | AL3 | DECOMMISSION; CHANGE | SHUTDOWN; TRANSITION | Applies whenever capability or infrastructure supporting an in-scope instance is retired; not applicable in a period with no retirements. |  | CG-14; CG-02; CG-04 | Storage media containing model weights leave site unsanitised; Shared loop drained while still serving adjacent racks; Retired equipment remains in the architecture snapshot; Removal of a shared PDU drops a remaining rack | AssetInstance; CapabilityInstance; ArchitectureSnapshot; Event | Isolation and draining of liquid loops and removal of batteries are hazardous activities performed only by authorised personnel under permit and lock-out/tag-out; the assessor reviews records and, if observing, does so from a safe position without handling equipment or fluids. | If sanitisation evidence cannot be matched to an asset serial number, record a U6 UNKNOWN for that asset and report it as a potential data exposure. | NIST SP 800-88 (guidelines for media sanitization); IEEE 2883 (standard for sanitizing storage); ISO/IEC 27040 (storage security) | MCF-CAP-023; MCF-CAP-001; MCF-CAP-004 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-DEP-001 | DEP | Dependency, Concentration and External Reliance Management | DEP-01 | Dependency discovery | Asset-to-Function Mapping | Every Required Function of the declared Capability Instance is traceable to the specific InfrastructureSystems and AssetInstances that implement it in each declared operating state, so that the consequence of losing, maintaining or changing any asset is known before it happens. | The capability owner shall maintain a versioned asset-to-function map that links each Required Function to the InfrastructureSystems and AssetInstances (including redundant and standby units) that implement it, stated separately for each declared operating state. The facility operator shall reconcile the map against the as-built asset register and current configuration at least at the interval set in the capability profile and after every material change, and shall record every asset that cannot be mapped, or every function with no identified implementing asset, as an UNKNOWN Record. | 1) Every Required Function in the assessment boundary has at least one IMPLEMENTED_BY relationship to an InfrastructureSystem, and every InfrastructureSystem resolves to identified AssetInstances. 2) Mappings are stated per operating state; at minimum NORMAL, MAINTENANCE (each planned maintenance configuration of a redundant path) and DEGRADED are distinguished where the implementing set differs. 3) A reconciliation sample of physical assets (by asset tag and location) and configuration items matches the map with no unexplained discrepancy above the profile tolerance. 4) Assets present in the as-built register but not mapped to any function are listed and dispositioned (mapped, excluded with rationale, or UNKNOWN). 5) The map is versioned, carries an effective date, and was re-validated after each material change recorded in the change log for the period. | Mapping completeness for critical Required Functions [% of functions with verified mapping] default 100 (Illustrative; any unmapped critical function defeats dependency visibility, so the profile normally sets 100%.) Reconciliation sample size [assets per InfrastructureSystem] default 10 or all if fewer (Illustrative; set by AIDCF-009 sampling rules and population size.) Reconciliation interval [months] default 12 (Illustrative; shorten for estates with high deployment churn such as accelerator cluster expansion.) | Current versioned asset-to-function map (export from CMDB/DCIM or dependency graph) with effective date and owner.; As-built asset register extract for the boundary (asset tag, model, location, serial) at the same date.; Single-line diagrams, P&IDs and network topology exports used to derive the map.; Reconciliation record for the sample: asset-by-asset match/mismatch with resolution.; List of unmapped assets and unmapped functions with disposition. | DOCUMENT_REVIEW; RECONCILIATION; INSPECTION; SAMPLING | 1) Obtain the Required Function list for the Capability Instance and the current asset-to-function map with its version and effective date. 2) Check that every Required Function has implementing systems and assets per declared operating state; list gaps. 3) Select a reconciliation sample per InfrastructureSystem using AIDCF-009 sampling rules, weighted towards assets in recent changes. 4) Verify sampled assets by walk-down or authoritative E2 export (tag, location, serial, model) against the map and as-built register. 5) Extract assets in the register that are not mapped and confirm their disposition. 6) Confirm map re-validation after each material change in the period by cross-referencing the change log. 7) Record Findings for mismatches and UNKNOWN Records for unmappable functions or assets. | PREVENTIVE | IMPLEMENTATION | AL3 | PLAN; DESIGN; BUILD; COMMISSION; OPERATE; CHANGE; DECOMMISSION | NORMAL; DEGRADED; MAINTENANCE; EMERGENCY; RECOVERY; TRANSITION | Applies to every assessment where a Capability Instance is declared. Not applicable only for a pure DESIGN-stage assessment where no asset yet exists; in that case MCF-DEP-003 and the design-stage dependency model carry the obligation. | CG-03 | CG-02 | Required Function silently implemented by an unregistered asset; Maintenance on an asset not known to support a function (scenario X04); Map drift after cluster expansion or rack moves; Redundant unit recorded but not physically present or not connected | RequiredFunction; InfrastructureSystem; AssetInstance; Dependency; OperatingState; ArchitectureSnapshot | Walk-downs in electrical rooms, plant spaces and liquid-cooled halls shall be escorted and follow site access and PPE rules; no covers, panels or enclosures shall be opened for verification without a permit issued under MCF-OPS-007. | Record an UNKNOWN Record (U10 Dependency unknown, or U5 Coverage gap) for each Required Function with no verifiable implementing asset and for each sampled asset whose function cannot be established; any such UNKNOWN on a critical Required Function is US4. | ISO/IEC/IEEE 42010 (architecture description); ISO 55001 (asset management systems); ISO/IEC 19770-1 (IT asset management); EN 50600-3-1 (data centre management and operational information) | MCF-DEP-002; MCF-DEP-003; MCF-DEP-017; MCF-OPS-017; MCF-CAP-004 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-DEP-002 | DEP | Dependency, Concentration and External Reliance Management | DEP-01 | Dependency discovery | Upstream Dependency Mapping | Every material upstream dependency of each Required Function is traced to the point where it leaves the assessment boundary and, where knowable, to the first shared upstream node, so that external and shared reliance is visible rather than assumed. | The capability owner shall maintain an upstream dependency graph for each Required Function that records, for every dependency, the provider, dependency type (electrical, thermal, hydraulic, network, control-system, timing/information, human/procedural, supplier/contractual, geographic, capacity), strength, applicable operating states and owner, following the AIDCF-003 dependency record schema. Tracing shall continue at least to the boundary exit point (for example the utility point of connection, carrier demarcation, facility-water flange, fuel delivery point, cloud or SaaS endpoint) and to the first known shared upstream node beyond it. The dependency owner shall record any trace that cannot be completed as an UNKNOWN Record. | 1) Each Required Function has an upstream graph covering all dependency classes in AIDCF-003 that apply; classes judged not applicable are stated with rationale. 2) Each dependency record has provider, type, strength, applicable states, owner and evidence populated, or the missing attribute is recorded as UNKNOWN. 3) External dependencies are traced to the boundary exit point and to the first known shared upstream node (for example grid substation or transmission circuit, carrier point of presence, cloud region, identity provider tenant). 4) Timing/information dependencies (DNS, NTP/PTP, DHCP/PXE, IPAM, certificate authorities, licence servers, identity providers) are included for compute, network, storage and control-system functions. 5) A sample of dependency records is corroborated by an independent source (contract, provider route record, configuration export or test). | Minimum trace depth beyond boundary [upstream nodes] default 1 (first shared upstream node) (Illustrative; deeper tracing is set in the profile where concentration risk is high.) Corroboration sample [% of external dependency records] default 25 (minimum 5 records) (Illustrative; set per AIDCF-009 sampling rules.) | Upstream dependency graph or register for each Required Function, with version and owner.; Utility connection agreement or point-of-connection diagram; carrier circuit and route records; facility-water and fuel supply records.; Configuration exports showing DNS, time, identity, licence and repository endpoints used by compute, network, storage and control systems.; Corroboration record for sampled dependencies.; UNKNOWN Records for traces that could not be completed. | DOCUMENT_REVIEW; ANALYSIS; RECONCILIATION; INQUIRY | 1) Select the Required Functions in scope and obtain their upstream graphs. 2) Check graph completeness against the AIDCF-003 dependency classes for each function; list omitted classes. 3) For external dependencies, confirm the boundary exit point and first shared upstream node from provider documents. 4) Extract configuration for timing, naming, identity, licensing and repository endpoints from a sample of compute, network, storage and BMS/EPMS systems and confirm each endpoint appears in the graph. 5) Corroborate the sampled records against independent evidence and record conflicts. 6) Record UNKNOWN Records for incomplete traces with US severity. | PREVENTIVE | IMPLEMENTATION | AL3 | PLAN; DESIGN; BUILD; COMMISSION; OPERATE; CHANGE; DECOMMISSION | NORMAL; DEGRADED; MAINTENANCE; EMERGENCY; RECOVERY; TRANSITION | Applies to every in-scope Required Function. Depth beyond the boundary may be limited by provider disclosure; that limitation is recorded, not treated as not applicable. | CG-03 | CG-15 | Hidden dependency on a shared upstream node (substation, carrier POP, cloud region); Unrecorded reliance on an external identity provider or licence server; Time-source dependency not recorded (scenario X13); Dependency on a provider assumed to be diverse but sharing a parent | Dependency; RequiredFunction; Resource; Interface; UnknownRecord | Configuration extraction shall use read-only accounts and approved export methods; no live query against BMS/EPMS or PLCs shall be made without authorisation from the control-system owner. | An incomplete upstream trace for a dependency of strength absolute or material is a U10 UNKNOWN Record of severity US4; an incomplete trace limited to supporting or recovery-only dependencies is US3 unless it affects a gate criterion. | AIDCF-003 dependency record schema; ISO 22317 (business impact analysis); IEC 61078 (reliability block diagrams); NIST SP 800-161r1 (cyber supply chain risk management) | MCF-DEP-001; MCF-DEP-004; MCF-DEP-009; MCF-DEP-010; MCF-DEP-012 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-DEP-003 | DEP | Dependency, Concentration and External Reliance Management | DEP-01 | Dependency discovery | Downstream Consequence Mapping | For each material asset, system and dependency, the Service Outcomes it affects and the time from its loss to outcome impact are known, so that prioritisation, maintenance planning and response are driven by consequence rather than by asset type. | The capability owner shall maintain a downstream consequence analysis that states, for each material InfrastructureSystem and dependency, the Service Outcomes affected by its loss or degradation, the propagation path, and the time-to-impact under declared load (for example UPS autonomy, thermal ride-through of liquid-cooled racks, checkpoint interval loss for training, inference latency tolerance). A competent engineer independent of the author shall review the analysis before approval. | 1) Each material system and dependency has recorded affected Service Outcomes and a propagation path using PROPAGATES_TO relationships. 2) Time-to-impact is stated with unit, load assumption and source (calculation, test or OEM data) for power, thermal and control dependencies. 3) Time-to-impact for AI workloads accounts for workload behaviour (for example training job failure on single-node loss within a synchronous collective, and the work lost since last checkpoint). 4) The analysis has been independently reviewed and approved, and its assumptions are listed. 5) The analysis is used: consequence classes appear in maintenance planning, alarm prioritisation and change risk assessment for a sample of records. | Thermal ride-through at declared rack load [seconds] default Site-specific (no default) (Derived from THM analysis and test; liquid-cooled high-density racks can have very short ride-through, so it is never assumed.) Maximum training work lost per interruption [minutes of cluster time] default Equal to checkpoint interval (illustrative 30) (Illustrative; set from the Service Outcome tolerance in CAP.) | Approved consequence analysis (FMEA-style table or graph) with assumptions.; Source calculations or test reports for time-to-impact values.; Independent review record.; Sample of maintenance plans, alarm priority records or change risk assessments showing use of consequence classes. | DOCUMENT_REVIEW; ANALYSIS; SAMPLING | 1) Obtain the consequence analysis, its assumptions and review record. 2) Check coverage against the material systems in the asset-to-function map (MCF-DEP-001). 3) Recompute or check a sample of time-to-impact values against their sources (UPS discharge data, thermal test, checkpoint configuration). 4) Trace a sample of maintenance, alarm and change records to confirm consequence classes are used. 5) Record Findings for unsupported time-to-impact values or uncovered systems. | DIRECTIVE | DESIGN | AL2 | DESIGN; COMMISSION; OPERATE; CHANGE | NORMAL; DEGRADED; MAINTENANCE; EMERGENCY | Applies to all in-scope Capability Instances. Where the Capability Instance has a single Service Outcome, the analysis may be simplified to propagation paths and time-to-impact. |  | CG-03; CG-09 | Consequence of a loss underestimated because ride-through was assumed rather than measured; Low-priority alarm on an asset with seconds-scale time-to-impact; Maintenance scheduled during a training run without checkpoint coordination | ServiceOutcome; FailureScenario; Dependency; InfrastructureSystem; FaultDomain | Desk-based analysis; where time-to-impact values require a test, the test is governed by the owning domain's control (POW/THM/RES) and not performed under this control. | Missing time-to-impact for a power, thermal or control dependency of a critical Required Function is a US3 UNKNOWN Record; it escalates to US4 if a CG-05, CG-06 or CG-10 criterion relies on that value. | IEC 60812 (FMEA); IEC 61025 (fault tree analysis); ISO 22317 (business impact analysis); ASHRAE TC 9.9 thermal guidelines for data processing environments | MCF-DEP-001; MCF-DEP-013; MCF-OPS-013; MCF-OPS-018; MCF-CAP-010 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-DEP-004 | DEP | Dependency, Concentration and External Reliance Management | DEP-01 | Dependency discovery | Recovery Dependency Mapping | Dependencies that are needed only, or mainly, during restoration are identified and available, and circular recovery dependencies are found and broken before an event rather than during it. | The recovery owner shall maintain a recovery dependency map for each Required Function covering recovery-only and recovery-critical dependencies (for example generator start batteries and fuel delivery, black-start sequence, BMS/EPMS server and network availability, out-of-band management network, DHCP/PXE and golden images, licence and entitlement servers, identity provider and break-glass credentials, OEM remote support, spares and specialist labour). The recovery owner shall analyse the map for circular dependencies and for recovery dependencies that share a fault domain with the failure they recover from, and shall record each such case with a resolution or an UNKNOWN Record. | 1) A recovery dependency map exists for each Required Function and states, for each dependency, whether it is recovery-only, and the operating states (RECOVERY, EMERGENCY, SHUTDOWN) in which it is needed. 2) A circular-dependency analysis has been performed (for example cooling controls require network, network requires power, power restoration sequence requires cooling controls) and each cycle is broken by a documented manual or independent path. 3) Each recovery dependency is checked for shared fault domain with the failure scenarios it is intended to recover from (for example golden-image repository hosted in the hall it restores). 4) Recovery-only external dependencies (OEM remote support, licence servers, cloud identity) have a verified offline or alternative path, or are recorded as UNKNOWN. 5) The map is consistent with the recovery sequences in RES-04 and the restoration procedures in POW/THM/CMP/STO/NET. | Maximum acceptable unresolved circular dependencies on critical functions [count] default 0 (Illustrative; any unresolved cycle on a critical function defeats recovery planning.) | Recovery dependency map per Required Function.; Circular-dependency analysis record with resolutions.; Configuration evidence of offline or alternative paths (for example local licence caches, cached credentials, local image mirrors, out-of-band network design).; Cross-reference to RES-04 recovery sequences. | DOCUMENT_REVIEW; ANALYSIS; RECONCILIATION; INQUIRY | 1) Obtain the recovery dependency maps and the RES-04 recovery sequences for in-scope functions. 2) Construct or review the dependency graph for the RECOVERY state and search for cycles. 3) For each recovery dependency, test for shared fault domain with the initiating scenario using the AIDCF-003 fault-domain taxonomy. 4) Verify by configuration evidence that declared offline or alternative paths exist. 5) Interview recovery owners on any dependency not represented in procedures. 6) Record Findings and UNKNOWN Records. | RECOVERY | IMPLEMENTATION | AL3 | DESIGN; COMMISSION; OPERATE; CHANGE | RECOVERY; EMERGENCY; SHUTDOWN; FAILED | Applies to every Capability Instance with a declared Recovery Outcome. Where no Recovery Outcome is declared, this is recorded as a CG-01 matter rather than treated as not applicable. |  | CG-03; CG-10 | Circular recovery dependency (cooling controls need network that needs cooled equipment); Golden image or configuration backup stored in the failed fault domain; Licence or entitlement server unreachable during recovery; Break-glass credentials depend on the failed identity provider; Recovery reintroduces corrupt configuration (scenario X15) | Dependency; FaultDomain; RequiredFunction; OperatingState; FailureScenario | Analysis is desk-based. Verification of offline paths shall not include disconnecting live services; any such test is performed under RES-05 with change approval. | A recovery dependency whose availability in the RECOVERY state cannot be established is a U10 UNKNOWN Record; it is US4 where it lies on the restoration path of a critical Required Function and a CG-10 criterion depends on it, otherwise US3. | ISO 22301 (business continuity management systems); ISO/IEC 27031 (ICT readiness for business continuity); NIST SP 800-34 (contingency planning) | MCF-RES-013; MCF-RES-014; MCF-POW-024; MCF-CMP-023; MCF-DEP-012 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-DEP-005 | DEP | Dependency, Concentration and External Reliance Management | DEP-02 | Shared and common-mode dependencies | Shared Source Analysis | Nominally redundant or diverse supplies are shown, on as-built evidence, not to share a source whose loss would defeat both, or the shared source is declared, owned and reflected in the resilience claim. | The facility owner shall analyse every redundant or diverse supply path that a resilience claim relies on (utility feeds, transformers, UPS paths, generator fuel, facility water, chilled-water plant, heat rejection, carrier circuits, cloud regions) for shared sources and record each pair as INDEPENDENT_OF only where as-built evidence supports independence for the stated hazard. Where a shared source exists, the facility owner shall record a SHARES_DEPENDENCY_WITH relationship, an owner and the residual exposure, and the capability owner shall reflect it in the resilience claim. | 1) Every redundancy claim used in CG-05, CG-06 or CG-08 evaluation has a corresponding shared-source analysis. 2) Independence claims are supported by as-built evidence (for example utility statement of separate grid supply points, separate fuel contracts and storage, separate water mains), not by design intent alone. 3) Shared sources found (for example both utility feeds from one grid substation, both fuel contracts with one distributor, both carriers using one upstream fibre) are recorded with owner and residual exposure. 4) The resilience claim for each affected Required Function is consistent with the recorded shared sources. | Upstream depth examined for shared source [levels] default To grid supply point / carrier POP / fuel terminal (Illustrative; profile sets depth based on the declared external hazard set.) | Shared-source analysis per redundancy claim.; Utility connection documentation identifying supply points; carrier route and POP documentation; fuel and water supply contracts.; Single-line and P&ID diagrams for internal sources.; Resilience claim records showing reflected shared sources. | DOCUMENT_REVIEW; ANALYSIS; RECONCILIATION; INSPECTION | 1) List every redundancy or diversity claim relied on for the Capability Instance. 2) For each, obtain the shared-source analysis and the supporting provider and as-built evidence. 3) Trace each path upstream and identify the first common node, if any. 4) Compare findings with the resilience claim and record inconsistencies. 5) Inspect accessible internal points (for example generator fuel interconnection, chilled-water headers) where documents conflict. | PREVENTIVE | IMPLEMENTATION | AL3 | DESIGN; BUILD; COMMISSION; OPERATE; CHANGE | NORMAL; MAINTENANCE; DEGRADED; EMERGENCY | Applies wherever a resilience or availability claim relies on redundancy or diversity. Not applicable to a Capability Instance that declares no redundancy (in which case the single source is the dependency and DEP-02 still records it). | CG-03 | CG-05; CG-06; CG-09 | Two utility feeds from the same grid substation lost together; A and B fuel supply from one distributor or terminal; Diverse carriers sharing one long-haul fibre; Redundant cooling plant sharing one water main or make-up water source | Dependency; FaultDomain; Resource; InfrastructureSystem; CapacityAssertion | Inspection of plant interconnections shall be non-intrusive; valves, breakers and isolators shall not be operated for verification. | Where independence of a pair cannot be established, the pair shall be treated as sharing a source for gate evaluation and an UNKNOWN Record (U10) raised; severity US4 when the pair underpins a CG-05 or CG-06 resilience criterion. | AIDCF-003 common-mode and concentration relationships; IEC 61508-6 (guidance on common cause failure); NUREG/CR-5485 (common-cause failure modelling guidelines) | MCF-DEP-006; MCF-DEP-007; MCF-DEP-009; MCF-POW-003; MCF-THM-016 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-DEP-006 | DEP | Dependency, Concentration and External Reliance Management | DEP-02 | Shared and common-mode dependencies | Common Controller Analysis | Redundant systems are not defeated together by a shared controller, management server, automation logic, firmware baseline or orchestration plane. | The control-system owner shall identify, for each redundant infrastructure pair or group, every shared control element (PLCs, BMS/EPMS servers, CDU controllers and their master/lead-lag logic, sequence-of-operation software, cluster managers and schedulers, fabric controllers, storage controllers, firmware and configuration sources, automation and AI agents) and record whether loss, malfunction or unsafe command of that element can affect more than one member of the group. The control-system owner shall either demonstrate independence, implement a safeguard (local autonomous control, fail-safe default, staggered firmware) or record the common controller as a declared common mode with owner. | 1) Each redundant group in POW, THM, CMP, STO and NET has a recorded common-controller analysis. 2) Controller failure behaviour (fail-last, fail-safe, fail-to-local) is stated from configuration or OEM evidence for each shared element. 3) Shared firmware or configuration sources are identified, and rollout to redundant members is staged (cross-reference MCF-SUP-015). 4) Each common controller that can affect more than one member has a safeguard or a recorded acceptance by the accountable owner. 5) Automation or AI agents with authority over more than one redundant member are recorded with their authority scope (cross-reference SEC-06). |  | Control architecture drawings (BMS/EPMS network and controller layout, CDU control topology, cluster/fabric management architecture).; Controller configuration exports showing failure mode settings.; Common-controller analysis record and acceptance decisions. | DOCUMENT_REVIEW; ANALYSIS; RECONCILIATION; INQUIRY | 1) Identify redundant groups from the asset-to-function map. 2) For each group, obtain control architecture and identify shared elements. 3) Obtain configuration or OEM evidence of failure behaviour for each shared element. 4) Check the safeguard or acceptance record for each shared element affecting multiple members. 5) Record Findings and UNKNOWN Records. | PREVENTIVE | IMPLEMENTATION | AL3 | DESIGN; BUILD; COMMISSION; OPERATE; CHANGE | NORMAL; MAINTENANCE; DEGRADED; FAILED | Applies to every redundant group of InfrastructureSystems controlled or managed by software or programmable controllers. |  | CG-03; CG-07; CG-09 | Single BMS server failure stops both chilled-water plants; CDU lead-lag controller fault stops all CDUs on a loop; Firmware rollout common-mode failure (scenario X08); Fabric controller fault isolates both rails; Automation acts on all redundant members at once | InfrastructureSystem; FaultDomain; Dependency; FailureMode | No controller shall be failed, isolated or forced to verify behaviour under this control; failure-behaviour tests are performed only under THM/POW/SEC test controls with authorisation from the control-system owner and the facility operator. | If controller failure behaviour cannot be established, record a U8 or U1 UNKNOWN Record; US4 where the redundant group supports a CG-05, CG-06 or CG-07 criterion. | IEC 62443-3-2 (security risk assessment for system design); IEC 61508-6 (guidance on common cause failure); ASHRAE Guideline 36 (sequences of operation for HVAC control) | MCF-DEP-005; MCF-SUP-015; MCF-THM-021; MCF-POW-021; MCF-SEC-021 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-DEP-007 | DEP | Dependency, Concentration and External Reliance Management | DEP-02 | Shared and common-mode dependencies | Shared Route Analysis | Physically diverse paths for power, fluid and telecommunications are verified on site and on provider route records not to converge in a shared trench, duct, riser, bridge, building entry, cable tray, pipe rack or fire zone. | The facility owner shall maintain route records for every path relied on for diversity (MV/LV cables, busways, fuel lines, chilled and facility water pipes, fibre between buildings and to carrier POPs, inter-hall fabric trunks) and shall identify every point where diverse routes converge or come within the separation distance set in the capability profile. The facility owner shall obtain route evidence from carriers and utilities for external routes, verify internal routes by inspection at least at the profile interval, and record each convergence point as a shared fault domain with owner. | 1) Route records exist for each diverse path and identify building entries, risers, trenches, bridges and fire zones traversed. 2) Convergence points and sub-separation sections are listed with location and the hazards that could affect both routes (fire, flood, excavation, vehicle impact). 3) External carrier routes are supported by carrier route documentation (KMZ, route maps or signed statements of diversity) to at least the first POP or regeneration site. 4) A sample of internal routes has been physically inspected within the interval and matches records. 5) Each convergence point has an owner and is reflected in the fault-domain model (RES-02) and resilience claims. | Minimum physical separation for diverse routes [m] default Site-specific (no default) (Set in capability profile with reference to fire-zone design and the separation guidance in the cabling standard adopted (for example ANSI/TIA-942 or EN 50600-2-4).) Route inspection interval [months] default 24 (Illustrative; shorter where third-party works or construction occur nearby.) | Route drawings for internal diverse paths with fire-zone overlay.; Carrier route documentation for each external circuit relied on for diversity.; Inspection record (dated, with photographs) for the sample.; Convergence point register with owners. | DOCUMENT_REVIEW; INSPECTION; RECONCILIATION; SAMPLING | 1) Obtain diverse path list and route records. 2) Overlay routes on site plans and fire zones; identify convergence points. 3) Obtain carrier and utility route evidence and check diversity to the first POP or supply point. 4) Inspect a sample of internal routes, prioritising building entries and risers. 5) Confirm convergence points are in the RES-02 fault-domain model. 6) Record Findings and UNKNOWN Records. | PREVENTIVE | IMPLEMENTATION | AL3 | DESIGN; BUILD; COMMISSION; OPERATE; CHANGE | NORMAL; MAINTENANCE; DEGRADED; EMERGENCY | Applies to all paths relied on for physical diversity. For colocation tenants, internal routes owned by the colocation provider are assessed through MCF-DEP-018 provider boundary evidence. | CG-03 | CG-09 | Fire disables paired infrastructure routes (scenario X09); Diverse carrier circuits in one duct cut by excavation; A and B busways in one riser; Supply and return water mains crossing in one trench | Interface; FaultDomain; Dependency; AssetInstance | Route inspection in risers, trenches and plant rooms shall follow confined-space and electrical safety rules; trench or manhole entry requires a permit under MCF-OPS-007 and confined-space controls. | Unverified diversity on a path relied on by a resilience claim shall be treated as shared for gate evaluation and recorded as U10 UNKNOWN; US4 where the path supports a CG-05, CG-06 or CG-08 criterion. | ANSI/TIA-942 (telecommunications infrastructure standard for data centres); EN 50600-2-4 (telecommunications cabling infrastructure); EN 50600-2-2 (power distribution) | MCF-DEP-005; MCF-DEP-010; MCF-NET-002; MCF-NET-020; MCF-RES-005 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-DEP-008 | DEP | Dependency, Concentration and External Reliance Management | DEP-02 | Shared and common-mode dependencies | Shared Human Dependency Analysis | Redundant technical systems are not made dependent on the same individual, team, shift, contractor or authorisation holder in a way that defeats redundancy during response, maintenance or recovery. | The operations manager shall analyse human and organisational dependencies for each Required Function, including authorised persons for HV/LV switching, refrigerant and liquid-cooling work, on-call specialists, OEM field engineers and maintenance contractors, and shall record where the same person, team or contractor is required to restore or operate more than one redundant member, or where response depends on fewer people than the emergency task analysis requires. The operations manager shall implement deputies, cross-authorisation or contractual capacity for each case or record it as a declared concentration with owner. | 1) Human/procedural dependencies are recorded for each Required Function using the AIDCF-003 dependency classes. 2) For each emergency procedure, the number of competent and authorised people required is compared with those available on shift and on call within the response time. 3) Cases where one contractor maintains both redundant members (for example A and B UPS systems or all generators) are identified and assessed. 4) Each identified shared human dependency has a mitigation or accepted concentration with owner. | Minimum authorised persons per critical switching task available within response time [persons] default 2 (Illustrative; reflects a two-person rule for HV switching common in safe systems of work; set from the site safety rules.) | Human dependency analysis per Required Function.; Authorisation register for hazardous tasks (cross-reference MCF-OPS-004).; Roster and on-call schedules for a representative period.; Maintenance contracts showing scope per system. | DOCUMENT_REVIEW; ANALYSIS; INQUIRY; SAMPLING | 1) Obtain emergency task analysis and the human dependency analysis. 2) Sample rosters and on-call schedules and compare with required authorised persons per task. 3) Review maintenance contracts for single-contractor coverage of redundant members. 4) Interview shift leads on response capacity for concurrent events. 5) Record Findings and accepted concentrations. | PREVENTIVE | DESIGN | AL2 | DESIGN; OPERATE; CHANGE | NORMAL; MAINTENANCE; EMERGENCY; RECOVERY | Applies to all staffed and contractor-supported operations in the boundary. |  | CG-03; CG-13 | Only one authorised HV switching person available at night; Same contractor fault affects maintenance of both UPS systems; Concurrent events exceed on-shift capacity; Key-person absence prevents recovery | Dependency; RequiredFunction; FaultDomain; Resource | Analysis only; no staffing reduction or simulated absence shall be imposed on live operations to test this control. | If rosters or authorisation records are unavailable for the sample period, record U1 UNKNOWN of severity US3; escalate to US4 if CG-04 safe-work criteria rely on two-person availability. | HSE HSG48 (reducing error and influencing behaviour); HSE HSG256 (managing shift work); Uptime Institute Tier Standard: Operational Sustainability | MCF-DEP-015; MCF-OPS-001; MCF-OPS-004; MCF-GOV-023 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-DEP-009 | DEP | Dependency, Concentration and External Reliance Management | DEP-03 | External providers and utilities | Utility Dependency | The utility services the Capability Instance relies on (grid electricity, water, fuel, and where applicable gas or district cooling) are contracted, sized and characterised for the declared demand, ramp schedule and operating states, including any curtailment, flexibility or interruptibility terms. | The facility owner shall maintain, for each utility dependency, the contractual and technical basis of supply: for grid electricity the connection agreement, firm and non-firm capacity, capacity reservation and energisation schedule, curtailment or flexible-connection terms, demand-response obligations, supply-point power quality characteristics and protection interface; for water the supply and discharge permits, contracted volume and restriction triggers; for fuel the supply contracts, priority status and delivery commitments. The facility owner shall reconcile contracted firm capacity against declared demand (including growth commitments from CAP-04) for each operating state and record any shortfall, non-firm reliance or undisclosed term as a Finding or UNKNOWN Record. | 1) A current utility connection agreement exists for each grid supply, with firm and any non-firm capacity, energisation dates and curtailment terms identified. 2) Contracted firm capacity is equal to or greater than the declared demand in each operating state, or the gap is covered by an evidenced on-site measure and declared in the capability profile. 3) Capacity reservations and staged energisation milestones match the capability growth forecast; slippage is tracked. 4) Curtailment, flexible-connection and demand-response obligations are mapped to Service Outcome effects and to operating procedures. 5) Water and fuel supply contracts state volume, priority and delivery lead time, and are consistent with POW fuel autonomy and THM/ENV water continuity analyses. 6) Supply-point power quality data (for example voltage dips and interruptions) is available for the preceding period or recorded as UNKNOWN. | Firm capacity margin over declared peak demand [% of declared peak] default 10 (Illustrative; set in the capability profile from load growth uncertainty and utility terms.) Minimum fuel resupply commitment under emergency [hours from call-off to delivery] default Site-specific (no default) (Set from POW fuel autonomy (MCF-POW-007/008) so that autonomy exceeds the committed resupply time with margin.) Power quality history reviewed [months] default 12 (Illustrative; longer history improves estimate of event frequency.) | Grid connection agreement and any variation, capacity reservation and energisation schedule.; Utility-provided supply characteristics (fault level, protection settings at interface, declared power quality).; Demand reconciliation by operating state.; Water supply and discharge permits; fuel supply contracts with emergency priority terms.; Power quality monitoring records at the point of connection (EPMS or utility). | DOCUMENT_REVIEW; RECONCILIATION; ANALYSIS; INQUIRY | 1) Obtain connection agreements, permits and fuel/water contracts. 2) Extract firm/non-firm capacity, curtailment and demand-response terms. 3) Reconcile contracted capacity with declared demand for each operating state and the growth forecast. 4) Check consistency with POW fuel autonomy and THM/ENV water analyses. 5) Review power quality records at the point of connection for the period. 6) Record Findings and UNKNOWN Records. | PREVENTIVE | IMPLEMENTATION | AL3 | PLAN; DESIGN; BUILD; COMMISSION; OPERATE; CHANGE | NORMAL; MAINTENANCE; DEGRADED; EMERGENCY; TRANSITION | Applies to every site supplying the Capability Instance. In colocation, the colocation provider's utility evidence is obtained through MCF-DEP-018; a tenant that cannot obtain it records UNKNOWN. | CG-03 | CG-05 | Capability expansion energised against non-firm capacity without declaration; Curtailment event not reflected in operating procedures; Energisation delay strands installed compute (scenario X17); Fuel resupply slower than autonomy under regional emergency; Water restriction reduces heat rejection (scenario X10) | Dependency; Resource; CapacityAssertion; Interface; OperatingState | Document and data review only; no switching, metering intervention or protection testing at the utility interface shall be performed under this control. | Undisclosed firm capacity or curtailment terms for a grid supply relied on by the Capability Instance is a U2 or U10 UNKNOWN Record of severity US4 (affects CG-03 and a CG-05 criterion). | EN 50160 (voltage characteristics of public distribution networks); IEC 61000-4-30 (power quality measurement methods); IEEE 1159 (monitoring electric power quality); NFPA 110 (emergency and standby power systems); Applicable network operator connection agreement and grid code (jurisdiction-specific) | MCF-POW-001; MCF-POW-002; MCF-POW-008; MCF-THM-015; MCF-CAP-015 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-DEP-010 | DEP | Dependency, Concentration and External Reliance Management | DEP-03 | External providers and utilities | Telecom Dependency | External connectivity (internet transit, data-centre interconnect, wavelength or dark-fibre services, carrier-neutral cross-connects, out-of-band and management circuits) is provided by identified carriers over verified diverse routes with known service levels, so that connectivity Service Outcomes and remote management do not rest on unrecorded single carriers or paths. | The network owner shall maintain a register of every external telecommunications circuit in scope, recording carrier, service type, A/Z ends, building entry, meet-me room and cross-connect identifiers, route diversity evidence, upstream carrier (where a reseller is used), service levels and fault escalation. The network owner shall verify that the circuits relied on for each connectivity outcome and for out-of-band management satisfy the declared diversity (carrier, route, entry, POP) and shall record shared elements and reseller dependencies as Findings or UNKNOWN Records. | 1) Every external circuit relied on by a Service Outcome or management path is in the register with carrier, route and demarcation identifiers. 2) Declared carrier diversity accounts for resale and wholesale relationships (the underlying network operator is identified). 3) Building entries and meet-me rooms for diverse circuits are distinct, or the shared element is recorded (cross-reference MCF-DEP-007). 4) Out-of-band management connectivity does not depend on the same carrier and path as the production connectivity it is meant to back up. 5) Carrier service levels (availability, time to repair) are recorded and compared with the connectivity Service Outcome tolerance. | Minimum number of independent carriers for production connectivity [carriers] default 2 (Illustrative; set by the connectivity Service Outcome.) Carrier time-to-repair commitment [hours] default 4 (Illustrative; compare against outcome tolerance.) | External circuit register.; Carrier order forms and service descriptions; reseller disclosure of underlying carrier.; Route diversity documentation (see MCF-DEP-007).; Meet-me room and cross-connect records.; Out-of-band management design. | DOCUMENT_REVIEW; RECONCILIATION; ANALYSIS; INSPECTION | 1) Obtain the circuit register and connectivity Service Outcomes. 2) Reconcile register to router/switch configuration (interfaces, BGP neighbours) for a sample. 3) Identify underlying carriers and check claimed diversity. 4) Inspect meet-me room cross-connect records for diverse circuits. 5) Compare carrier service levels with outcome tolerance. 6) Record Findings and UNKNOWN Records. | PREVENTIVE | IMPLEMENTATION | AL3 | DESIGN; BUILD; COMMISSION; OPERATE; CHANGE | NORMAL; MAINTENANCE; DEGRADED; EMERGENCY; RECOVERY | Applies wherever a Service Outcome or management/recovery path depends on external connectivity. Fully air-gapped environments record the air-gap boundary instead. | CG-03 | CG-10 | Two 'diverse' carriers reselling one underlying fibre; Out-of-band circuit on same carrier as production; Single meet-me room for all external circuits; Carrier repair time exceeds outcome tolerance | Dependency; Interface; Resource; FaultDomain | No circuit shall be disconnected, shut or failed over to verify diversity under this control; failover testing is governed by NET and RES controls with change approval. | Undisclosed underlying carrier or route for a diversity-relied circuit is a U10 UNKNOWN Record; US4 where it underpins a connectivity Service Outcome assessed under CG-03 or CG-08. | ANSI/TIA-942 (telecommunications infrastructure standard for data centres); EN 50600-2-4 (telecommunications cabling infrastructure) | MCF-DEP-007; MCF-NET-002; MCF-NET-015; MCF-NET-019; MCF-DEP-021 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-DEP-011 | DEP | Dependency, Concentration and External Reliance Management | DEP-03 | External providers and utilities | OEM Dependency | Reliance on original equipment manufacturers and system integrators for the operation, support, repair and recovery of critical assets (accelerators and rack-scale systems, NICs/DPUs, switches and optics, storage, UPS, switchgear, generators, chillers, CDUs, BMS/EPMS) is identified per Required Function, including reliance that persists after installation such as entitlement, licensing, telemetry and remote diagnostics. | The capability owner shall maintain an OEM dependency register that records, for each critical asset class, the OEM and integrator, support entitlement and its expiry, RMA and advance-replacement terms, licence or entitlement mechanisms required for operation (including licence servers and online activation), telemetry or phone-home requirements, field-engineer coverage for the site, proprietary tools or software needed for diagnosis or recovery, and the functions that would be lost or degraded if OEM support were unavailable. The capability owner shall record each operating dependency on OEM-hosted services as an external dependency in the upstream graph (MCF-DEP-002). | 1) Every critical asset class in the asset-to-function map has an OEM dependency entry with current support entitlement and expiry. 2) Operating dependencies on OEM services (licence activation, entitlement checks, cloud management portals, remote diagnostics) are recorded with the effect of their loss on each Required Function. 3) Proprietary diagnostic or recovery tools are held on site or in an accessible repository with licences valid for emergency use. 4) Field-engineer coverage (response time, local presence, clearance requirements) is recorded and compared with recovery tolerances. 5) Entries are reconciled to contracts and to OEM portals for a sample of assets. | Support entitlement expiry warning [days before expiry] default 180 (Illustrative; allows renewal or replacement before entitlement lapses.) | OEM dependency register.; Support contracts and entitlement records for sampled assets.; Licence and activation design for software-licensed functions.; Evidence of local copies of proprietary tools. | DOCUMENT_REVIEW; RECONCILIATION; INQUIRY; SAMPLING | 1) Obtain the OEM dependency register and asset-to-function map. 2) Check coverage of critical asset classes. 3) Sample assets and verify entitlement against OEM records. 4) Review licence and telemetry dependencies for effect on operation if OEM services are unreachable. 5) Confirm local availability of proprietary tools. 6) Record Findings and UNKNOWN Records. | PREVENTIVE | IMPLEMENTATION | AL3 | PLAN; DESIGN; BUILD; OPERATE; CHANGE; DECOMMISSION | NORMAL; MAINTENANCE; DEGRADED; RECOVERY | Applies to all critical asset classes. Supplier due diligence and contract terms are assessed under SUP; this control records the dependency itself. |  | CG-03; CG-10 | Accelerator or switch feature stops after licence server unreachable; Loss of remote OEM support (scenario X18); Support entitlement lapsed unnoticed; Proprietary recovery tool unavailable during incident | Dependency; AssetInstance; Resource; InfrastructureSystem | Register and document review only; no licence server shall be blocked to test behaviour outside an approved RES-05 exercise. | An unknown entitlement status or an unrecorded OEM operating dependency for a critical asset class is a U10 UNKNOWN Record of severity US3, escalating to US4 if the dependency lies on a CG-10 restoration path. | ISO/IEC 27036-2 (supplier relationships: requirements); ISO 22318 (guidelines for supply chain continuity) | MCF-SUP-001; MCF-SUP-005; MCF-SUP-021; MCF-CMP-022; MCF-DEP-014 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-DEP-012 | DEP | Dependency, Concentration and External Reliance Management | DEP-03 | External providers and utilities | Cloud and Service Dependency | Dependencies on hyperscale cloud and SaaS control planes (identity providers, cloud-hosted DCIM/BMS analytics, cluster management and scheduling services, container and model registries, certificate authorities, DNS, ticketing and paging, OEM portals) are identified, their failure behaviour is known, and the infrastructure can continue to operate safely when they are unavailable. | The capability owner shall maintain a register of every cloud or SaaS service on which an in-scope Required Function, management path or recovery path depends, recording the provider, region/zone, control-plane and data-plane dependencies, authentication path, the effect on each function if the service is unavailable or degraded, and the local fallback mode. The control-system owner shall ensure that no facility safety or continuity function (power, cooling, fire, leak detection and their alarming) requires a cloud or SaaS service to operate, and shall record any exception with accountable acceptance. | 1) Every cloud/SaaS service used by in-scope functions is registered with provider, region and authentication path. 2) Failure behaviour on service unavailability is stated per function and is supported by provider documentation, configuration or test. 3) No facility safety or continuity control loop or critical alarm path depends on a cloud or SaaS service; exceptions are accepted by the accountable owner. 4) Identity dependencies (federated sign-on for operators, service accounts) have a documented local or break-glass path (cross-reference SEC-01). 5) Concentration in a single cloud provider or region across multiple functions is identified (cross-reference MCF-DEP-013/014). | Maximum dependency of safety or continuity loops on cloud/SaaS services [count] default 0 (Illustrative; profile may allow exceptions only with accountable acceptance.) | Cloud/SaaS dependency register.; Architecture diagrams for management and control planes.; Configuration evidence of local fallback (local controller logic, cached credentials, on-premises DNS/NTP).; Provider service descriptions and status-page history for the period. | DOCUMENT_REVIEW; ANALYSIS; RECONCILIATION; INQUIRY | 1) Obtain the register and management/control-plane architecture. 2) Reconcile register to egress firewall rules, DNS logs or configuration exports to find unregistered services. 3) For each service, obtain stated failure behaviour and check it against configuration evidence. 4) Confirm safety and continuity loops operate without cloud services. 5) Review provider incident history for events affecting operations. 6) Record Findings and UNKNOWN Records. | PREVENTIVE | IMPLEMENTATION | AL3 | DESIGN; BUILD; COMMISSION; OPERATE; CHANGE | NORMAL; DEGRADED; EMERGENCY; RECOVERY | Applies to all Capability Instances. In hybrid cloud/on-premises patterns, cloud-hosted compute is a separate Capability Instance boundary matter (MCF-DEP-017). | CG-03 | CG-15; CG-10 | Operators locked out when cloud identity provider fails (scenario X19); Cloud-hosted BMS analytics issuing setpoints with no local fallback; Cluster scheduler SaaS outage stops job admission; Container or model registry unavailable during recovery | Dependency; Interface; Resource; RequiredFunction | Reconciliation uses log and configuration review only; blocking egress to test fallback is permitted only within an approved exercise with the facility operator's authorisation. | Unknown failure behaviour of a cloud/SaaS service on a management or control path of a critical function is a U10 UNKNOWN Record of severity US4. | ISO/IEC 22123-1 (cloud computing vocabulary); ISO/IEC 19086-1 (cloud service level agreement framework); ISO/IEC 27017 (security controls for cloud services); CSA Cloud Controls Matrix | MCF-DEP-002; MCF-DEP-004; MCF-SEC-001; MCF-SEC-004; MCF-NET-024 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-DEP-013 | DEP | Dependency, Concentration and External Reliance Management | DEP-04 | Concentration and substitutability | Capacity Concentration | The share of AI capability concentrated in any single fault domain (site, building, hall, power train, UPS system, cooling loop or CDU group, scale-up domain, fabric pod, storage cluster) is quantified and kept within the impact tolerance of the Service Outcome. | The capability owner shall calculate, for each declared fault domain, the proportion of the Capability Instance's usable capacity (for example accelerators, storage throughput, network bandwidth) that would be lost on its failure, and shall compare it with the concentration limit derived from the Service Outcome impact tolerance (CAP-03). Where a fault domain exceeds the limit, the capability owner shall record it as a CONCENTRATES relationship and either reduce the concentration, provide alternative capacity (RES-03) or obtain risk acceptance from the accountable owner. | 1) Concentration is calculated for every fault domain in the RES-02 model, using current deployment data. 2) The concentration limit is derived from and traceable to the Service Outcome impact tolerance. 3) Fault domains exceeding the limit have an approved treatment or acceptance. 4) Calculations account for job topology: training jobs spanning several fault domains are counted as lost if any spanned domain fails, unless elastic recovery is evidenced. | Maximum share of usable capability in one fault domain [% of usable capacity] default Site-specific (no default) (Derived from the CAP-03 impact tolerance; there is no universal value.) | Concentration analysis per fault domain.; Deployment inventory and job placement data.; Impact tolerance reference.; Treatment or acceptance records. | ANALYSIS; DOCUMENT_REVIEW; RECONCILIATION | 1) Obtain fault-domain model and deployment data. 2) Recompute concentration for a sample of fault domains. 3) Compare with limits and check traceability to impact tolerance. 4) Review treatment or acceptance for exceedances. | DIRECTIVE | DESIGN | AL2 | PLAN; DESIGN; OPERATE; CHANGE | NORMAL; MAINTENANCE; DEGRADED | Applies to all Capability Instances with more than one fault domain; a single-fault-domain capability records 100% concentration and its acceptance. |  | CG-03; CG-09 | Majority of training capacity on one UPS system; All inference replicas in one hall; Large capability concentration exceeding tolerance | FaultDomain; CapacityAssertion; CapabilityInstance; ServiceOutcome | Desk-based analysis of deployment and placement data; no workload shall be moved or drained to test concentration. | If job placement or fault-domain labels are unavailable, record U1 UNKNOWN of severity US3 and treat the largest plausible concentration as the working value. | ISO 31000 (risk management); Regulation (EU) 2022/2554 (DORA), ICT concentration risk provisions — informative for financial-sector users | MCF-RES-005; MCF-RES-007; MCF-RES-010; MCF-CAP-010; MCF-CMP-008 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-DEP-014 | DEP | Dependency, Concentration and External Reliance Management | DEP-04 | Concentration and substitutability | Supplier Concentration | Single-source and sole-source reliance for critical products and services, including concentration at sub-tier (shared factories, components or logistics routes) and concentration in one firmware or software lineage, is identified and treated. | The procurement lead shall maintain a supplier concentration analysis covering critical asset classes and services (accelerators and rack-scale systems, high-speed optics, switch silicon, storage media, transformers, MV/LV switchgear, UPS, generators, CDUs and pumps, chillers, BMS/EPMS platforms, maintenance contractors, specialist labour). For each, the procurement lead shall record whether supply is single-source (one qualified supplier available) or sole-source (only one supplier exists), the qualification time for an alternative, and known sub-tier concentration, and shall agree a treatment with the capability owner. | 1) Each critical asset class and service has a recorded sourcing status (multi-, single-, sole-source). 2) Sub-tier concentration known from MCF-SUP-004 is incorporated (for example two transformer brands sharing one core-steel supplier). 3) Qualification time for an alternative supplier is estimated with basis. 4) Each single- or sole-source item has an agreed treatment (dual qualification, strategic stock, framework agreement, design change) or acceptance. | Maximum share of a critical asset class from one supplier [% of installed base] default Site-specific (no default) (Set in capability profile; standardisation benefits must be weighed against common-mode exposure.) | Supplier concentration analysis.; Approved supplier list.; Sub-tier disclosures (from SUP-01).; Treatment and acceptance records. | DOCUMENT_REVIEW; ANALYSIS; INQUIRY | 1) Obtain the concentration analysis and approved supplier list. 2) Check coverage of critical asset classes and services. 3) Verify sourcing status for a sample against market information and supplier disclosures. 4) Review treatments and acceptances. | DIRECTIVE | DESIGN | AL2 | PLAN; DESIGN; OPERATE; CHANGE | NORMAL; RECOVERY | Applies to all critical asset classes and services. |  | CG-03 | Sole-source accelerator allocation cut; One transformer supplier for all units with multi-year lead time; Single firmware lineage across all switches; Single contractor holds all specialist knowledge | Dependency; Resource; AssetInstance | Desk-based analysis; supplier enquiries shall not disclose site-sensitive architecture beyond what the supplier already holds under contract. | Unknown sourcing status for a critical class is US3; escalate to US4 where the class lies on a CG-10 restoration path with no strategic spare. | ISO 22318 (guidelines for supply chain continuity); NIST SP 800-161r1 (cyber supply chain risk management); ISO 28000 (security and resilience: supply chain security management) | MCF-SUP-004; MCF-SUP-018; MCF-DEP-016; MCF-DEP-011 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-DEP-015 | DEP | Dependency, Concentration and External Reliance Management | DEP-04 | Concentration and substitutability | Knowledge Concentration | Knowledge essential to operate, maintain and recover critical systems (control logic, sequences of operation, protection philosophy, fabric configuration and tuning, storage recovery procedures, proprietary scripts) is not held by a single person or a single external party without a documented and tested transfer path. | The operations manager shall identify knowledge items essential to each Required Function and record their holders, documentation status and accessibility. For each item held by fewer people than the profile minimum or held only by an external party, the operations manager shall implement documentation, cross-training or contractual access (including escrow of control logic and configuration where proprietary) and shall verify transfer by a practical demonstration. | 1) Knowledge items essential to each Required Function are listed with holders. 2) Items below the minimum holder count have a documented treatment and target date. 3) Proprietary control logic and configuration for BMS/EPMS/CDU/PLC systems is held by the owner or in escrow, in a usable form. 4) At least one transfer per critical item has been demonstrated by a second holder performing the task or a walkthrough. | Minimum independent holders per critical knowledge item [persons] default 2 (Illustrative; external parties count only where contractually available within response time.) | Knowledge concentration register.; Documentation inventory and storage location.; Escrow or ownership evidence for control logic.; Demonstration records. | DOCUMENT_REVIEW; INQUIRY; OBSERVATION | 1) Obtain register and documentation inventory. 2) Interview holders to test completeness. 3) Verify escrow or ownership of control logic. 4) Observe or review demonstration records. | PREVENTIVE | DESIGN | AL2 | COMMISSION; OPERATE; CHANGE | NORMAL; EMERGENCY; RECOVERY | Applies to all critical systems; most material for proprietary control systems and bespoke automation. |  | CG-13; CG-10 | Only one engineer can modify CDU control logic; Integrator holds the only copy of PLC source; Fabric tuning undocumented | Resource; Dependency; RequiredFunction | Demonstrations shall use simulators, test benches or walkthroughs; no live control-logic change for demonstration purposes. | Unknown holder count or inaccessible control logic for a critical system is US3; escalate to US4 where a CG-10 recovery step depends on it. | ISO 30401 (knowledge management systems); IEC 62443-2-4 (security requirements for IACS service providers) | MCF-DEP-008; MCF-OPS-004; MCF-SUP-008; MCF-GOV-023 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-DEP-016 | DEP | Dependency, Concentration and External Reliance Management | DEP-04 | Concentration and substitutability | Substitution Readiness | For each material concentration or single external dependency, a substitute (alternative carrier path, alternate fuel supplier, mobile generation, temporary chillers or heat rejection, alternate OEM or qualified refurbished stock, alternate cloud region or provider, alternate capacity) can be brought into service within the time the Service Outcome tolerance allows, and this has been demonstrated. | The capability owner shall define a substitution plan for each concentration or single dependency recorded under DEP-02 to DEP-04, stating the substitute, prerequisites (connection points, permits, contracts, qualification), activation authority and time-to-substitute. The capability owner shall validate each plan by test, exercise or documented precedent at the profile interval, and shall record the demonstrated time-to-substitute against tolerance. | 1) Each recorded concentration or single external dependency has a substitution plan or an accepted no-substitute position. 2) Physical prerequisites (for example generator and chiller connection points, temporary fuel connections, spare fibre) exist and have been inspected. 3) Contractual prerequisites (call-off agreements, standby contracts) are current. 4) Each plan has been validated within the interval and demonstrated time-to-substitute is within tolerance, or the gap is recorded. 5) Lessons from validation have been incorporated. | Substitution validation interval [months] default 24 (Illustrative; shorter for dependencies with high event frequency.) Time-to-substitute margin [% of tolerance] default 75 (demonstrated time no more than 75% of tolerance) (Illustrative; provides margin for real-event degradation.) | Substitution plans.; Inspection records for physical prerequisites.; Current call-off or standby contracts.; Test, exercise or precedent records with timing. | DOCUMENT_REVIEW; INSPECTION; SCENARIO_EXERCISE; TEST | 1) Obtain concentration and single-dependency records and corresponding plans. 2) Inspect physical prerequisites for a sample. 3) Verify contracts are current. 4) Review validation records and compare demonstrated times to tolerance. 5) Where proportionate, witness a substitution exercise. | RECOVERY | EFFECTIVENESS | AL5 | DESIGN; OPERATE; CHANGE | DEGRADED; EMERGENCY; RECOVERY | Applies to every material concentration or single external dependency; not applicable where an accepted no-substitute position exists and is reflected in the decision. |  | CG-10; CG-03 | Temporary generator connection point missing or incompatible; Call-off contract expired; Substitute takes longer than tolerance; Alternate region lacks capacity at the time of need | Dependency; Safeguard; TestRecord; FailureScenario | Substitution tests involving temporary generation, temporary chillers, fuel transfer or electrical connection are hazardous; they require a method statement (MCF-OPS-006), permit to work (MCF-OPS-007), change approval (MCF-OPS-018) and authorisation by the facility operator's authorised person. | A plan never validated is UNKNOWN for the EFFECTIVENESS claim (U5 coverage gap, US3); where the dependency is on a CG-10 restoration path, US4. | ISO 22301 (business continuity management systems); ISO 22318 (guidelines for supply chain continuity); NFPA 110 (emergency and standby power systems) | MCF-RES-010; MCF-RES-011; MCF-DEP-013; MCF-DEP-014; MCF-SUP-019 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-DEP-017 | DEP | Dependency, Concentration and External Reliance Management | DEP-05 | Boundary and interface control | Assessment Boundary | The assessment boundary is drawn so that every material dependency of the Capability Instance is either inside it and assessed, or outside it and explicitly recorded as an external dependency with owner, evidence and decision effect; nothing material is excluded silently. | The assurance lead shall define the assessment boundary for each Capability Instance by reference to the dependency graph (DEP-01), listing included systems, external dependencies crossing the boundary (with boundary interface, provider and evidence obtained), and exclusions with rationale and approver. The assurance lead shall reconcile the boundary with the asset-to-function map and upstream graph before fieldwork and after any material change, and shall treat any material dependency found outside the boundary and not recorded as a boundary defect. | 1) The boundary statement lists included systems, crossing dependencies and exclusions, each with identifier. 2) Every dependency in the DEP-01 graph with strength absolute or material is either inside the boundary or recorded as a crossing dependency. 3) Each exclusion has a rationale and an approver with authority (GOV-01), and its decision effect is stated. 4) Each crossing dependency has an evidence plan (what will be obtained from the provider and how it will be verified). 5) Boundary reconciliation was performed before fieldwork and after material changes in the period. |  | Approved boundary statement.; Reconciliation record against DEP-01 graph.; Exclusion approvals.; Evidence plan for crossing dependencies. | DOCUMENT_REVIEW; RECONCILIATION; ANALYSIS | 1) Obtain the boundary statement, dependency graph and asset-to-function map. 2) Reconcile each material dependency to boundary inclusion or crossing record. 3) Check exclusion rationale, approver and decision effect. 4) Check evidence plans for crossing dependencies. 5) Record boundary defects as Findings and unresolved items as UNKNOWN Records. | DIRECTIVE | IMPLEMENTATION | AL3 | PLAN; DESIGN; OPERATE; CHANGE | NORMAL; DEGRADED; MAINTENANCE; EMERGENCY; RECOVERY; TRANSITION | Applies to every assessment. | CG-02; CG-03 |  | Material dependency excluded without approval; Colocation provider infrastructure assumed in scope but not evidenced; Cloud control plane outside boundary but not recorded; Boundary drawn around compute only, ignoring facility dependencies | ArchitectureSnapshot; Dependency; Interface; CapabilityInstance; UnknownRecord | Desk-based. | A material dependency whose boundary status cannot be determined is a US5 Systemic UNKNOWN (it affects the boundary) and caps the decision at INCONCLUSIVE until resolved. | ISO/IEC/IEEE 15026-2 (assurance case); ISO/IEC/IEEE 42010 (architecture description); ISO 19011 (guidelines for auditing management systems) | MCF-DEP-001; MCF-DEP-002; MCF-DEP-018; MCF-EVA-010; MCF-CAP-004 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-DEP-018 | DEP | Dependency, Concentration and External Reliance Management | DEP-05 | Boundary and interface control | Provider Boundary | At every interface with a provider (colocation operator, utility, carrier, water or fuel supplier, cloud provider, managed-service or maintenance provider) the physical and logical demarcation point and the allocation of responsibility for operation, maintenance, monitoring, change, incident response and evidence are explicit for each lifecycle stage and operating state. | The capability owner shall maintain, for each provider interface, a demarcation record identifying the physical or logical demarcation point (for example HV metering point, tenant breaker in provider switchboard, facility-water flange or CDU primary connection, meet-me room patch panel, cloud API boundary) and a shared-responsibility record conforming to AIDCF-003 (IOT-REQ-051) for each function across lifecycle stages and operating states, including who may operate, who responds to alarms, who approves changes and who holds evidence. The capability owner shall obtain the provider's acceptance of each record and shall treat any function without a responsible and an accountable party as a responsibility gap. | 1) Each provider interface has a demarcation record with an identifiable physical or logical point. 2) Each shared function has a shared-responsibility record covering operation, maintenance, monitoring, change approval, incident response and evidence custody for NORMAL, MAINTENANCE, EMERGENCY and RECOVERY states. 3) The provider has accepted the record (signed, contractual schedule or equivalent). 4) Emergency authority across the boundary (for example who may shed tenant load or isolate a cooling loop) is explicit. 5) Responsibility gaps are recorded and dispositioned; contractual responsibility is not treated as proof of capability (IOT-REQ-052). |  | Demarcation records with drawings or photographs of demarcation points.; Shared-responsibility records.; Provider acceptance evidence.; Gap register. | DOCUMENT_REVIEW; INSPECTION; INQUIRY; RECONCILIATION | 1) List provider interfaces from the boundary statement. 2) Obtain demarcation and shared-responsibility records. 3) Inspect a sample of physical demarcation points. 4) Check states coverage and emergency authority. 5) Interview provider and owner staff on a sample of scenarios to test common understanding. 6) Record responsibility gaps. | DIRECTIVE | IMPLEMENTATION | AL3 | PLAN; BUILD; COMMISSION; OPERATE; CHANGE; DECOMMISSION | NORMAL; MAINTENANCE; DEGRADED; EMERGENCY; RECOVERY | Applies wherever any function in the boundary is performed or supported by a third party. | CG-13 | CG-03 | Colocation responsibility gap (scenario X14); Neither party responds to a CDU primary-side alarm; Provider changes upstream configuration without tenant approval; Evidence held by provider not available to assessor | Interface; Dependency; RequiredFunction; OperatingState | Inspection of demarcation points inside provider spaces requires provider escort and permission; no provider equipment shall be operated. | A critical function with no identifiable responsible or accountable party across a provider boundary is US4 (CG-13 criterion); an unaccepted but otherwise complete record is US3. | AIDCF-003 shared-responsibility record (IOT-REQ-051/052); EN 50600-3-1 (management and operational information); ISO/IEC 27036-3 (supplier relationships: ICT supply chain security) | MCF-DEP-017; MCF-DEP-019; MCF-GOV-006; MCF-OPS-002; MCF-SUP-005 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-DEP-019 | DEP | Dependency, Concentration and External Reliance Management | DEP-05 | Boundary and interface control | Tenant Boundary | In shared or multi-tenant facilities and platforms, one tenant's load, configuration, actions or failures cannot propagate to another beyond declared limits, and shared infrastructure capacity is allocated and enforced. | The platform or facility operator shall define for each shared resource (power path and UPS capacity, cooling loop and CDU capacity, coolant chemistry, fabric and storage, management plane) the per-tenant allocation, the enforcement mechanism (for example breaker sizing, power capping, flow limiting, QoS, quota) and the tenant obligations (load-step limits, coolant compatibility, change notification). The operator shall monitor tenant consumption against allocation and record exceedances as incidents. | 1) Each shared resource has per-tenant allocations recorded. 2) Enforcement mechanisms are implemented and evidenced by configuration. 3) Tenant obligations are in agreements and are monitored. 4) Exceedances in the period are recorded and handled as incidents. 5) Tenant change that could affect shared infrastructure (for example new rack-scale systems with large load steps) requires operator approval. | Per-tenant load-step limit [kW per second] default Site-specific (no default) (Derived from POW-05 load-step response analysis.) | Allocation records per shared resource.; Configuration evidence of enforcement.; Tenant agreements with obligations.; Consumption monitoring reports and exceedance incidents. | DOCUMENT_REVIEW; RECONCILIATION; ANALYSIS; SAMPLING | 1) Obtain shared resource list and allocations. 2) Verify enforcement configuration for a sample. 3) Review monitoring and exceedances. 4) Review tenant change approvals. | PREVENTIVE | IMPLEMENTATION | AL3 | DESIGN; BUILD; OPERATE; CHANGE | NORMAL; MAINTENANCE; DEGRADED | Applies only to multi-tenant or shared-platform patterns. Not applicable to single-tenant dedicated facilities, with that pattern recorded in the boundary statement. |  | CG-09; CG-13 | Tenant rack load step trips shared UPS; Incompatible coolant introduced by tenant contaminates shared loop; Tenant consumes reserved headroom; Tenant fabric misconfiguration affects shared spine | Interface; Resource; CapacityAssertion; FaultDomain | No enforcement mechanism shall be tested by deliberate exceedance on live shared infrastructure. | Unverifiable enforcement on a shared resource supporting more than one tenant is US3; US4 where it is a CG-09 containment boundary. | EN 50600-3-1 (management and operational information); ISO/IEC 27017 (cloud services security) | MCF-PHY-012; MCF-NET-012; MCF-DEP-018; MCF-OPS-023; MCF-THM-017 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-DEP-020 | DEP | Dependency, Concentration and External Reliance Management | DEP-05 | Boundary and interface control | Cross-Boundary Enforcement | The conditions agreed at each boundary interface (power drawn, coolant supply temperature and flow, water quality, network traffic and routes, access) are measured at the boundary and deviations are detected, escalated and resolved, so that interface contracts operate in practice rather than on paper. | The capability owner shall instrument each material boundary interface so that the agreed interface properties (per AIDCF-013 interface contracts) are measured at or near the demarcation point, shall set alarm thresholds for deviation, and shall route deviations to the responsible party under MCF-DEP-018 with escalation timelines. The capability owner shall review deviations and their resolution at the interval set in the capability profile. | 1) Each material boundary interface has measured properties defined with units and thresholds. 2) Measurement exists at or near the demarcation point and data is retained for the period. 3) Deviations in the period were alarmed, routed to the responsible party and resolved within escalation timelines. 4) Recurring deviations have been raised as problems (MCF-OPS-016). | Interface deviation review interval [months] default 1 (Illustrative.) | Interface property definitions and thresholds.; Boundary metering and telemetry data for the period.; Deviation alarms and tickets with resolution times.; Review records. | ANALYSIS; SAMPLING; DOCUMENT_REVIEW; RECONCILIATION | 1) Obtain interface property definitions. 2) Extract boundary telemetry for the period and identify deviations independently. 3) Reconcile independently identified deviations with alarms and tickets. 4) Check resolution times against escalation timelines. 5) Check problem records for recurrence. | DETECTIVE | OPERATION | AL4 | COMMISSION; OPERATE; CHANGE | NORMAL; MAINTENANCE; DEGRADED | Applies to material boundary interfaces where measurement is technically possible; where it is not, the gap is recorded as an UNKNOWN Record rather than not applicable. |  | CG-09; CG-15 | Coolant supply temperature from provider above agreed limit undetected; Tenant draws above allocated power without alarm; Upstream route change unnoticed | Interface; Event; Dependency; CapacityAssertion | Read-only telemetry extraction. | Missing boundary telemetry for a material interface is U1 UNKNOWN, US3; US4 where the interface is a CG-06 or CG-05 supply interface. | AIDCF-013 interface contracts; IEC 61000-4-30 (power quality measurement methods); ASHRAE TC 9.9 liquid cooling guidance | MCF-DEP-018; MCF-DEP-021; MCF-OPS-013; MCF-OPS-022 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-DEP-021 | DEP | Dependency, Concentration and External Reliance Management | DEP-06 | Dependency monitoring and review | Dependency Health Indicators | The health of each material external and shared dependency is observed continuously or periodically through defined indicators, so that deterioration is detected before it defeats a Service Outcome. | The operations manager shall define health indicators for each material dependency (for example utility voltage events and frequency deviations, fuel stock and delivery status, facility water pressure and quality, carrier circuit errors and availability, cloud/SaaS service status, OEM case backlog and RMA turnaround, spares stock against minimum) with thresholds and alarm routing into the NOC/BMS, and shall review indicator trends at the profile interval. | 1) Each material dependency has at least one defined health indicator with threshold. 2) Indicators are collected and visible to the NOC or BMS operators. 3) Threshold breaches in the period generated alarms or tickets and were acted on. 4) Trend reviews were held at the interval and recorded actions. | Dependency trend review interval [months] default 3 (Illustrative.) | Indicator definitions.; Dashboards or reports for the period.; Threshold breach tickets.; Trend review minutes. | DOCUMENT_REVIEW; ANALYSIS; SAMPLING; OBSERVATION | 1) Obtain indicator definitions and map to material dependencies. 2) Observe NOC/BMS visibility of indicators. 3) Sample threshold breaches and trace to action. 4) Review trend minutes. | DETECTIVE | OPERATION | AL4 | OPERATE; CHANGE | NORMAL; DEGRADED; MAINTENANCE | Applies to all material dependencies recorded under DEP-01 to DEP-03. |  | CG-03 | Fuel stock below minimum unnoticed; Carrier error rate rising before outage; OEM RMA backlog growing; Cloud identity degradation not visible to operators | Dependency; Event; Resource | Observation only. | No indicator for a material dependency is US3 for OPERATION claims. | ISO 22301 (business continuity management systems); EN 50600-3-1 (management and operational information) | MCF-DEP-020; MCF-DEP-022; MCF-OPS-013; MCF-SUP-017 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-DEP-022 | DEP | Dependency, Concentration and External Reliance Management | DEP-06 | Dependency monitoring and review | Provider Performance | Actual performance of each material provider against service levels and against the needs of the Service Outcome is measured and reviewed, and persistent shortfall leads to action. | The supplier manager shall measure each material provider's performance against contracted service levels (availability, response and restore times, RMA turnaround, notification timeliness, RCA quality) from owner-side records, review it with the provider at the profile interval, and escalate persistent or material shortfall to the capability owner for treatment. | 1) Measured performance from owner-side records exists for each material provider for the period. 2) Reviews were held at the interval with recorded actions. 3) Shortfall against service levels or Service Outcome needs was escalated and treated. 4) Provider RCAs for significant incidents were received and assessed. | Provider review interval [months] default 3 (Illustrative.) | Performance measurements.; Review minutes.; Escalation records.; Provider RCAs. | DOCUMENT_REVIEW; ANALYSIS; SAMPLING | 1) Obtain service levels and measurements. 2) Recompute a sample of measurements from tickets. 3) Review minutes and escalation records. 4) Assess RCAs. | DETECTIVE | OPERATION | AL4 | OPERATE; CHANGE | NORMAL; DEGRADED; RECOVERY | Applies to material providers. |  | CG-13 | Provider restore times exceed tolerance without escalation; Self-reported provider metrics mask shortfall; RCAs not received | Dependency; Event; Finding | Not applicable to physical testing; review only. | Absence of owner-side measurement is U1, US3 for OPERATION claims. | ISO/IEC 20000-1 (service management system requirements); ISO 44001 (collaborative business relationship management) | MCF-SUP-005; MCF-DEP-021; MCF-SUP-007 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-DEP-023 | DEP | Dependency, Concentration and External Reliance Management | DEP-06 | Dependency monitoring and review | Change Detection | Changes that alter the dependency graph, whether made internally or by providers (carrier reroute, utility network reconfiguration, cloud region or API change, OEM licensing or end-of-life notice, contractor change, new tenant), are detected and the dependency records and affected assessments are updated. | The dependency owner shall operate a change-detection process that combines internal change records (OPS-05), provider notifications, contract events and technical discovery (for example route and configuration diffs) to identify changes to material dependencies, and shall update the dependency graph and raise reassessment triggers within the time set in the capability profile. | 1) Sources of dependency change are defined (internal changes, provider notifications, contract events, discovery). 2) Changes in the period were reflected in the dependency graph within the profile time. 3) Each material dependency change raised a ReassessmentTrigger where required. 4) A sample of provider notifications reconciles to graph updates. | Maximum time to update dependency graph after detected change [working days] default 10 (Illustrative.) | Change-detection procedure.; Provider notifications for the period.; Graph version history.; ReassessmentTrigger records. | RECONCILIATION; SAMPLING; DOCUMENT_REVIEW | 1) Obtain procedure and sources. 2) Sample provider notifications and internal changes. 3) Trace to graph updates and reassessment triggers. 4) Measure update latency. | DETECTIVE | OPERATION | AL4 | OPERATE; CHANGE | NORMAL; TRANSITION; MAINTENANCE | Applies to all assessments with OPERATION claims on dependency controls. |  | CG-14; CG-03 | Carrier reroute merges diverse paths unnoticed; OEM licensing change not reflected; Contractor change removes authorised staff | Event; Dependency; ReassessmentTrigger | Review only. | Inability to show that provider notifications are received is U5, US3; escalate to US4 if a CG-03 critical dependency changed in the period without update. | ISO/IEC 20000-1 (service management system requirements); SAE EIA-649C (configuration management standard) | MCF-OPS-018; MCF-DEP-024; MCF-EVA-022 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-DEP-024 | DEP | Dependency, Concentration and External Reliance Management | DEP-06 | Dependency monitoring and review | Periodic Revalidation | The dependency graph, route records, provider demarcations and concentration analyses are revalidated against fresh evidence at a defined interval, so that dependency visibility does not decay between change events. | The dependency owner shall revalidate every material dependency record at the interval set in the capability profile by obtaining current evidence (walk-down, configuration export, provider statement or contract), shall mark records not revalidated within the interval as STALE, and shall treat stale records as UNKNOWN for assessment purposes. | 1) A revalidation schedule covering all material dependency records exists. 2) Records were revalidated within the interval, with evidence attached. 3) Stale records are flagged and treated as UNKNOWN. 4) Revalidation findings led to graph updates. | Revalidation interval for material dependencies [months] default 12 (Illustrative; shorter for high-churn dependencies (cloud services, carriers).) | Revalidation schedule.; Revalidation evidence per record.; Stale record list. | DOCUMENT_REVIEW; SAMPLING; RECONCILIATION | 1) Obtain schedule and record list. 2) Sample records and check revalidation date and evidence. 3) Confirm stale flagging and treatment. 4) Check resulting updates. | DETECTIVE | OPERATION | AL4 | OPERATE | NORMAL; MAINTENANCE | Applies to all material dependency records. |  | CG-03 | Dependency graph accurate at build but stale years later; Provider demarcation changed without update | Dependency; EvidenceObject; ReassessmentTrigger | Walk-downs follow site safety rules as for MCF-DEP-001. | Stale material dependency records are U3 UNKNOWN; severity follows the dependency's gate role (US4 for CG-03 critical dependencies). | AIDCF-008 freshness rule; ISO 55001 (asset management systems) | MCF-DEP-023; MCF-EVA-021; MCF-DEP-001 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-PHY-001 | PHY | Physical Site, Building and Security Infrastructure | PHY-01 | Site and location resilience | Site Hazard Assessment | Establish that the natural and man-made hazards to which the site is exposed are identified, quantified against declared design levels and reflected in the design of facilities that host AI capability, so that no credible site-wide event exceeds the protection assumed by the architecture. | The facility owner shall maintain a site hazard assessment, prepared or reviewed by competent specialists, that quantifies flood (fluvial, pluvial, coastal and groundwater), seismic, wind, lightning, extreme-temperature, wildfire and subsidence hazards at the declared design exceedance levels. The facility owner shall record, for each hazard, the design level adopted, the protective measures relied on and the residual exposure, and shall reassess the hazards when hazard mapping, climate projections or the site layout change. | 1) A hazard assessment exists that covers every hazard family in AIDCF-004 Part V applicable to the site, with excluded hazards justified. 2) Each quantified hazard states the source data, return period or annual exceedance probability and the design level adopted for critical plant. 3) Critical plant (MV intake, transformers, switchgear, UPS, generators, fuel, heat rejection, CDUs) elevation and protection are shown to meet the adopted flood design level plus freeboard. 4) Seismic design category and non-structural component requirements derived from the local code are recorded and traced into PHY-02 anchorage requirements. 5) Residual exposures are recorded as risks with an owner and are reflected in the resilience scenarios. 6) The assessment is no older than the declared review interval and post-dates the last material change to hazard mapping or site layout. | Design flood annual exceedance probability for critical plant [% per year] default 0.1 (illustrative) (Capability profile; national flood-risk mapping commonly publishes 1% and 0.1% AEP extents) Freeboard above design flood level for critical plant [mm] default 300 (illustrative) (Capability profile; site flood-risk assessment) Hazard assessment review interval [months] default 36 (illustrative) (Capability profile) | Site hazard assessment report with hazard-by-hazard design levels and data sources; Flood-risk assessment and topographic survey showing critical plant finished floor levels; Seismic hazard determination and design category from the structural engineer of record; Lightning risk assessment (e.g. IEC 62305-2 method) and protection design; Risk register entries for residual site exposures with owners | DOCUMENT_REVIEW; ANALYSIS; INSPECTION | 1) Obtain the hazard assessment and confirm its date, author competence and hazard coverage. 2) Compare adopted design levels to the capability-profile parameters and to current public hazard data. 3) Walk down critical plant locations and verify finished floor and equipment plinth levels against survey. 4) Trace seismic and wind design levels into structural and anchorage design documents. 5) Confirm residual exposures appear in the risk register and in at least one resilience scenario. | DIRECTIVE | DESIGN | AL2 | PLAN; DESIGN; CHANGE | NORMAL; EMERGENCY | Applies to every site in the assessment boundary, including colocation sites where the assessed party must obtain the provider's hazard assessment. Not applicable to purely logical capability with no physical site in the boundary. |  | CG-02; CG-03; CG-04 | Critical plant located below credible flood level; Seismic design level understated for non-structural components; Hazard assessment based on superseded mapping; Residual exposure not carried into resilience scenarios | Hazard; InfrastructureSystem; FailureScenario; Safeguard | Desk-based assessment; no hazardous testing. Site walk-downs follow the host site induction and are escorted in plant areas. | If the hazard assessment is absent or predates a material revision of hazard mapping, record a U1 or U3 UNKNOWN against the site and treat flood and seismic protection of critical plant as unverified for CG-02 and CG-04 evaluation. | ISO 31000 (risk management); IEC 62305 series (lightning protection); ASCE/SEI 7 or EN 1998 (seismic actions, per jurisdiction); EN 50600-2-1 (building construction); FM Global Property Loss Prevention Data Sheets (natural hazards) | MCF-PHY-002; MCF-PHY-007; MCF-ENV-023; MCF-RES-003 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-PHY-002 | PHY | Physical Site, Building and Security Infrastructure | PHY-01 | Site and location resilience | External Exposure | Ensure that threats and hazards originating outside the site boundary, including adjacent industrial activity, transport corridors, airspace, hostile vehicles and airborne contaminants, are characterised and mitigated so that they cannot disable redundant infrastructure together. | The facility owner shall identify external exposures within a defined radius of the site, including major-accident-hazard installations, pipelines, rail and road corridors carrying hazardous goods, flight paths, high-voltage corridors and sources of smoke or corrosive emissions. The facility owner shall specify perimeter protection (stand-off, hostile vehicle mitigation, blast and intrusion resistance) proportionate to the assessed threat, and shall show that no single external event can impair both redundant utility intakes, both generator yards or all heat-rejection plant. | 1) An external exposure register exists covering the declared radius, with each exposure's consequence path to site infrastructure described. 2) Hostile vehicle mitigation at the perimeter is rated to the vehicle mass and speed set in the threat assessment and covers all vehicle-accessible approaches to critical plant. 3) Redundant utility intakes, generator yards and heat-rejection plant are separated so that a single external event in the register cannot reach both. 4) Air intakes for halls and plant are located and protected against smoke, exhaust re-entrainment (including from the site's own generators) and corrosive emissions identified in the register. 5) Exposure changes in the surrounding area are monitored and the register is reviewed at the declared interval. | External exposure assessment radius [km] default 2 (illustrative) (Capability profile; threat assessment) Hostile vehicle mitigation rating [vehicle mass / impact speed] default 7,500 kg at 48 km/h (illustrative) (Threat assessment; rating per IWA 14-1 or PAS 68 test classification) External exposure review interval [months] default 12 (illustrative) (Capability profile) | External exposure register with distances and consequence paths; Security threat assessment and perimeter protection specification; Test certificates for installed hostile vehicle mitigation products; Site plan showing separation of redundant intakes, generator yards and heat rejection; Air-intake and exhaust plume study for generator exhaust re-entrainment | DOCUMENT_REVIEW; INSPECTION; ANALYSIS | 1) Review the exposure register and test it against public land-use and hazardous-installation data. 2) Inspect perimeter protection and match installed products to rated test certificates. 3) Overlay single external events (explosion overpressure contour, vehicle impact, smoke plume) on the site plan and check whether any reaches both redundant elements. 4) Review the exhaust re-entrainment study against current generator and intake positions. | PREVENTIVE | DESIGN | AL2 | PLAN; DESIGN; CHANGE | NORMAL; EMERGENCY | Applies to owned and leased sites; for colocation the assessed party relies on the provider's register and perimeter evidence. Not applicable where the site is wholly within a host facility whose perimeter is assessed as a separate boundary element. |  | CG-09; CG-03 | Single external explosion or fire affecting both redundant intakes; Vehicle-borne attack reaching transformer or generator yard; Generator exhaust drawn into hall air intakes during utility outage; New adjacent hazard not detected | Threat; Hazard; FaultDomain; Safeguard | Desk-based assessment; no hazardous testing. Site walk-downs follow the host site induction and are escorted in plant areas. | If separation of redundant intakes or generator yards against a registered external event cannot be demonstrated from drawings, record a U5 coverage UNKNOWN and carry it into the CG-09 evaluation as an untested containment boundary. | IWA 14-1 (vehicle security barriers); PAS 68 (hostile vehicle mitigation); EN 50600-2-5 (security systems); ISO/IEC 27002 (physical and environmental security) | MCF-PHY-001; MCF-PHY-009; MCF-DEP-007 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-PHY-003 | PHY | Physical Site, Building and Security Infrastructure | PHY-01 | Site and location resilience | Access and Logistics | Ensure that the site can receive the deliveries, emergency services and replacement equipment on which continuity and recovery of AI capability depend, including heavy dense racks, transformers and fuel, under normal and emergency conditions. | The facility operator shall maintain a logistics and access plan that defines routes and constraints for fuel delivery, emergency services, rack-scale IT deliveries and replacement of the largest plant items (transformers, generators, chillers, CDUs). The facility operator shall verify that loading docks, lifts, corridors, ramps and doors along each route are rated for the mass and dimensions of the heaviest declared item, and shall maintain an alternative access route for fuel and emergency services when the primary route is obstructed. | 1) Each route in the plan states the governing constraint (door clear opening, lift rating, ramp gradient, slab or dock rating) and the heaviest item it is verified for. 2) The heaviest declared fully populated rack (including integrated liquid-cooling manifolds) can be moved from dock to its final position without exceeding any route rating. 3) A replacement path exists for each transformer, generator and chiller that does not require de-energising the redundant counterpart. 4) At least the declared number of independent access routes for fuel tankers and fire appliances exists and has been driven or walked within the review period. 5) Logistics constraints are communicated to IT deployment teams before procurement of new rack types. | Heaviest declared delivered item on IT route (crated rack) [kg] default 3,000 (illustrative) (Capability profile; rack OEM shipping data) Independent access routes for fuel and emergency vehicles [count] default 2 (illustrative) (Capability profile; emergency services consultation) | Logistics and access plan with route constraints; Lift, dock leveller and slab rating certificates or structural statements; Plant replacement method statements for largest items; Records of route trials or delivery records for the heaviest rack type deployed; Fire-service access consultation records | DOCUMENT_REVIEW; INSPECTION; SAMPLING; OBSERVATION | 1) Review the plan and identify the governing constraint on each route. 2) Measure a sample of constraints (door openings, ramp gradients) and compare with the plan. 3) Compare the heaviest rack in the deployment pipeline with lift and route ratings. 4) Review plant replacement method statements for dependency on redundant counterparts. 5) Confirm the alternative fuel and emergency route is unobstructed on the day of inspection. | PREVENTIVE | OPERATION | AL4 | DESIGN; BUILD; OPERATE; CHANGE | NORMAL; DEGRADED; MAINTENANCE; EMERGENCY; RECOVERY; TRANSITION | Applies to all sites hosting rack-scale or liquid-cooled AI systems and to any site relying on fuel deliveries for autonomy. Reduced scope applies to colocation tenants, who verify only the IT delivery route and rely on provider evidence for plant and fuel routes. |  | CG-10 | Rack cannot be delivered without exceeding lift or slab rating; Transformer replacement requires outage of the redundant unit; Fuel tanker cannot reach fill point during flood or obstruction; Emergency services access blocked by deliveries | Resource; Dependency; InfrastructureSystem; CapacityAssertion | Inspection only. Route trials with loaded racks are conducted by trained movers under the equipment-movement procedure (MCF-PHY-018); assessors do not participate in heavy-item moves. | If route ratings for the heaviest declared rack cannot be established, record a U1 UNKNOWN and treat deployment of that rack type as unverified for PHY-02 structural claims. | EN 50600-2-1 (building construction); ANSI/TIA-942 (data centre infrastructure) | MCF-PHY-006; MCF-PHY-018; MCF-POW-008; MCF-SUP-019 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-PHY-004 | PHY | Physical Site, Building and Security Infrastructure | PHY-01 | Site and location resilience | Adjacent Risk | Ensure that risks arising from adjacent occupancies, shared structures and neighbouring tenants on the same campus or in the same building are identified and cannot propagate into the facility hosting the assessed capability. | The facility owner shall identify adjacent occupancies and shared building elements (party walls, roofs, risers, plant rooms, car parks and loading areas) and the hazards they present, including fire load, water, vibration, vehicle impact and uncontrolled access. The facility owner shall agree with neighbouring occupiers or the landlord the separation, notification and emergency-coordination arrangements for each adjacent risk, and shall record any adjacent risk that cannot be controlled as an accepted risk with an accountable owner. | 1) An adjacency register identifies every occupancy sharing a structural element, riser or plant space with the facility. 2) Each adjacent risk has a recorded separation measure (fire rating, physical barrier, drainage, vibration isolation) or an approved risk acceptance. 3) Notification arrangements exist for adjacent works (hot works, roof works, demolition) that could affect the facility. 4) Emergency coordination with adjacent occupiers is documented, including shared alarms and evacuation interfaces. | Adjacent-risk register review interval [months] default 12 (illustrative) (Capability profile) | Adjacency register with shared elements and hazards; Landlord or neighbour agreements covering notification of works; Fire strategy extracts for party walls and shared risers; Risk acceptances for uncontrolled adjacent risks | DOCUMENT_REVIEW; INQUIRY; INSPECTION | 1) Obtain the adjacency register and verify it against building plans and site walk-down. 2) Check each shared riser and plant space for third-party equipment or access. 3) Review agreements and evidence that notification of adjacent works has operated. 4) Confirm uncontrolled risks have approved acceptance by the accountable owner. | DIRECTIVE | DESIGN | AL2 | PLAN; DESIGN; OPERATE; CHANGE | NORMAL; MAINTENANCE; EMERGENCY | Applies to multi-occupancy buildings, campuses and colocation facilities. A standalone single-occupier building with no shared structure records the determination and is otherwise not applicable. |  | CG-03 | Fire in adjacent occupancy breaches party wall; Water from neighbour plant floods hall; Uncoordinated hot works in shared riser; Neighbour access through shared roof | Hazard; Dependency; FaultDomain | Desk-based assessment; no hazardous testing. Site walk-downs follow the host site induction and are escorted in plant areas. | Where adjacent occupancies cannot be determined (for example landlord refuses disclosure), record a U2 UNKNOWN and treat the shared element as an unverified fault domain. | EN 50600-2-1 (building construction); NFPA 101 (life safety code) or national building regulations | MCF-PHY-010; MCF-PHY-012; MCF-DEP-018 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-PHY-005 | PHY | Physical Site, Building and Security Infrastructure | PHY-02 | Building and structural integrity | Structural Capacity | Demonstrate that floor slabs, raised floors, roofs and supports can carry the loads imposed by dense AI racks, liquid-filled cooling systems, battery systems and rooftop heat-rejection plant, with margin, for the declared deployment. | The facility owner shall hold a structural capacity statement from the structural engineer of record that states the uniformly distributed and concentrated load capacity of each data hall, plant room, battery room and roof area. The facility owner shall ensure the statement accounts for operating (wet) mass of liquid-cooled racks, CDUs, manifolds, coolant distribution pipework and immersion tanks, and shall require a structural re-check before any deployment that raises planned load above the declared utilisation threshold. | 1) Structural capacity is stated for every area hosting IT, power, battery or cooling equipment, in kN/m² distributed and kN concentrated. 2) The load model uses operating mass including coolant, not dry shipping mass, for liquid-cooled equipment and pipework. 3) Roof and plant-deck capacity covers heat-rejection plant at operating weight, including any additions for AI expansion. 4) Raised-floor pedestals and panels, where used, are rated for rolling and concentrated loads of the heaviest rack during movement. 5) Planned load per area is below the utilisation threshold, or a structural re-check is on file. | Design uniformly distributed live load, data hall [kN/m²] default 20 (illustrative) (Structural engineer of record; capability profile for dense liquid-cooled racks) Planned-load utilisation threshold requiring structural re-check [% of rated capacity] default 80 (illustrative) (Capability profile) | Structural capacity statement or drawings with load capacities per area; Load schedule with operating mass of racks, CDUs, pipework and battery systems; Raised-floor system rating certificates (where raised floor used); Structural re-check reports for deployments above threshold | DOCUMENT_REVIEW; ANALYSIS; RECONCILIATION | 1) Obtain the structural statement and confirm author competence and date. 2) Rebuild the planned load per area from the rack and plant schedule using operating mass. 3) Compare planned load with capacity and with the utilisation threshold. 4) Verify re-check reports exist where thresholds are exceeded. | PREVENTIVE | DESIGN | AL2 | DESIGN; BUILD; CHANGE | NORMAL; MAINTENANCE | Applies to all facilities and to colocation suites where the tenant's equipment imposes load; the tenant obtains the provider's rated capacity and supplies its own load schedule. |  | CG-02; CG-04 | Slab overstressed by wet mass of liquid-cooled racks; Roof overloaded by added dry coolers; Raised floor pedestal failure under rolling load; Load model based on dry mass | CapacityAssertion; InfrastructureSystem; Hazard | Desk-based assessment; no hazardous testing. Site walk-downs follow the host site induction and are escorted in plant areas. | If the load schedule cannot be reconciled to installed equipment, record a U5 UNKNOWN and treat structural adequacy for the affected area as unverified. | EN 1991 (actions on structures) or ASCE/SEI 7 (minimum design loads); EN 50600-2-1 (building construction) | MCF-PHY-006; MCF-PHY-018; MCF-THM-009 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-PHY-006 | PHY | Physical Site, Building and Security Infrastructure | PHY-02 | Building and structural integrity | Rack Loading | Ensure that as-installed rack positions do not exceed the floor, raised-floor and rack-frame ratings for the actual mass of installed equipment, including liquid in manifolds and cold plates. | The facility operator shall maintain a rack-position load register recording the operating mass of every rack and the rated capacity of its position. The facility operator shall verify rack mass at installation for each new rack type, shall prevent installation where the position rating would be exceeded, and shall reconcile the register to installed equipment at the declared interval. | 1) The load register covers every occupied rack position in the assessed halls. 2) For each rack type, operating mass is evidenced by OEM data or weighing, including coolant. 3) No position exceeds its rated capacity; any exceedance has a structural engineer's acceptance. 4) A sample of positions reconciles to installed equipment during inspection. 5) Installation workflow blocks commissioning of a rack whose mass is not recorded. | Maximum operating mass per rack position [kg] default 2,000 (illustrative) (Structural capacity statement; capability profile) Rack-load reconciliation sample [% of positions] default 10 (illustrative) (Assessment sampling plan) | Rack-position load register; OEM mass data or weighing records for each rack type; Installation records showing load check; Inspection reconciliation sample results | RECONCILIATION; SAMPLING; INSPECTION | 1) Select a sample of positions across halls, weighted to the densest rows. 2) Compare installed equipment to the register and recompute mass. 3) Compare with position rating and identify exceedances. 4) Review the installation workflow for the mass check gate. | PREVENTIVE | IMPLEMENTATION | AL3 | BUILD; COMMISSION; OPERATE; CHANGE | NORMAL; MAINTENANCE | Applies to all halls hosting AI racks. Not applicable to areas with only network or low-mass equipment where the register shows ample margin. |  | CG-04; CG-14 | Position overloaded after mid-life densification; Rack frame rating exceeded; Register not updated after rack swap | AssetInstance; CapacityAssertion | Inspection only; assessors do not move or open racks. Weighing is performed by the operator's trained staff using rated equipment. | If more than the sampled tolerance of positions cannot be reconciled, record a U5 UNKNOWN for the hall and limit the PHY-005 conclusion to reconciled areas. | EN 50600-2-1 (building construction); Rack OEM installation guides | MCF-PHY-005; MCF-PHY-018; MCF-CMP-003 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-PHY-007 | PHY | Physical Site, Building and Security Infrastructure | PHY-02 | Building and structural integrity | Anchorage and Vibration | Ensure that racks, CDUs, battery systems, tanks, switchgear and suspended services are restrained against seismic and operational loads, and that vibration from rotating plant does not degrade IT or storage equipment. | The facility owner shall specify and install anchorage and bracing for racks, CDUs, battery cabinets, fuel and water tanks, switchgear, busway and overhead cable and pipe supports to the seismic design level determined in MCF-PHY-001. The facility operator shall isolate generators, chillers and pumps so that vibration transmitted to IT spaces remains within the most restrictive OEM limit for installed equipment, and shall verify installed anchorage by inspection at commissioning and after changes. | 1) Anchorage design for each equipment class references the site seismic design level. 2) A sample inspection finds installed anchors and bracing matching the design for the sampled items. 3) Overhead busway, cable tray and liquid-cooling manifolds have bracing compatible with the design level. 4) Vibration isolation is installed on rotating plant and measured transmitted vibration in IT spaces is within the declared limit. 5) Seismic flexibility is provided at liquid pipework connections to racks and CDUs where the design level requires it. | Transmitted vibration limit at IT equipment [mm/s RMS] default per most restrictive OEM specification (OEM installation requirements) | Anchorage and bracing design calculations or details; Commissioning inspection records for anchorage; Vibration survey report for IT spaces with plant running; Photographic inspection sample | DOCUMENT_REVIEW; INSPECTION; SAMPLING | 1) Trace seismic design level into anchorage design per equipment class. 2) Inspect a sample of racks, CDUs, battery cabinets and tanks for anchors and bracing. 3) Review vibration survey conditions and results against limits. 4) Check flexible connections on liquid pipework at rack and CDU interfaces. | PREVENTIVE | IMPLEMENTATION | AL3 | DESIGN; BUILD; COMMISSION; CHANGE | NORMAL; EMERGENCY | Seismic elements apply where the local code assigns a seismic design category requiring non-structural restraint; vibration elements apply to all sites with rotating plant. |  | CG-09 | Battery cabinet overturn in seismic event; Rigid pipe connection fracture releasing coolant; Storage throughput degradation from transmitted vibration | AssetInstance; Hazard; Safeguard | Visual inspection only; no load testing of anchors by assessors. Inspection in energised rooms follows site electrical-safety rules and keeps outside arc-flash boundaries. | If anchorage design is unavailable for battery or tank systems, record a U1 UNKNOWN and carry it into CG-09 as an unverified containment element. | ASCE/SEI 7 or EN 1998 (non-structural seismic provisions); Equipment OEM installation guides | MCF-PHY-001; MCF-PHY-005; MCF-THM-011 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-PHY-008 | PHY | Physical Site, Building and Security Infrastructure | PHY-02 | Building and structural integrity | Building Envelope | Ensure the building envelope keeps water, wind-driven rain, dust and uncontrolled air out of IT and plant spaces and maintains the enclosure integrity on which gaseous suppression and air management depend. | The facility operator shall inspect roofs, roof penetrations, gutters, façades, louvres and doors at the declared interval and after severe weather, shall correct defects within a risk-based period, and shall prohibit water-bearing services and roof drainage from passing over IT and electrical rooms unless they are contained and monitored. | 1) Envelope inspection records exist at the declared interval and after each severe-weather warning. 2) No uncontained water-bearing pipe or roof drain passes over IT or electrical rooms. 3) Open envelope defects are tracked with risk-based target dates and none affecting IT spaces is overdue. 4) Water ingress events in the last 12 months have root cause and corrective action recorded. | Envelope inspection interval [months] default 6 (illustrative) (Capability profile; roofing guidance) | Envelope inspection records; Defect log with dates; Incident records for water ingress; Drawings showing services over IT and electrical rooms | DOCUMENT_REVIEW; INSPECTION; OBSERVATION | 1) Review inspection and defect records for completeness against the interval. 2) Inspect ceilings of IT and electrical rooms for water marks and uncontained services. 3) Review water ingress incidents and closure of actions. | PREVENTIVE | OPERATION | AL4 | BUILD; OPERATE | NORMAL; MAINTENANCE; EMERGENCY | Applies to all enclosed facilities, including modular and containerised units; colocation tenants rely on provider evidence. |  | CG-06 | Roof leak onto energised switchgear; Louvre failure admitting wind-driven rain; Envelope leakage defeating suppression hold time | InfrastructureSystem; Hazard; Safeguard | Roof access only under the site's work-at-height permit with edge protection; assessors do not access fragile roofs. | If envelope inspection records are missing for more than one interval, record a U1 UNKNOWN; the control result is UNKNOWN for OPERATION claims. | EN 50600-2-1 (building construction) | MCF-PHY-011; MCF-PHY-022; MCF-ENV-023 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-PHY-009 | PHY | Physical Site, Building and Security Infrastructure | PHY-03 | Physical zoning and segregation | Security Zones | Ensure that the site is divided into layered security zones whose protection increases towards the most critical assets, including power and cooling plant as well as IT halls, so that access to any asset that can disable AI capability requires passing proportionate barriers. | The security manager shall define a zoning model with at least perimeter, building, secure-corridor, critical-space and rack/cage levels, and shall assign every critical asset (MV intake, switchgear, UPS and battery rooms, generator yard, fuel, heat rejection, CDU and pump rooms, meet-me rooms, data halls, control rooms) to a zone. The security manager shall ensure each zone boundary has physical barriers, access control and detection appropriate to the zone and that critical plant zones are protected no less than the IT halls they serve. | 1) A zoning plan assigns every critical asset in the boundary to a zone with stated protection measures. 2) Power, cooling and fuel plant zones have access control and intrusion detection at least equivalent to the data halls they serve. 3) Zone boundaries are continuous (no bypass via ceiling voids, raised floors, risers or louvres) in the sampled areas. 4) Access to critical-space zones requires multi-factor authentication and anti-tailgating measures. 5) The zoning model is reconciled to the current floor plan and security system configuration. | Authentication factors at critical-space zone entry [count] default 2 (illustrative) (Capability profile; threat assessment) | Zoning plan with asset assignment; Access-control system zone and reader configuration export; Barrier specifications and intrusion detection layout; Inspection notes for zone continuity | DOCUMENT_REVIEW; RECONCILIATION; INSPECTION | 1) Map each critical asset from the architecture to a zone in the plan. 2) Reconcile zone readers and doors in the access-control export to the plan. 3) Inspect a sample of zone boundaries for bypass routes through voids and risers. 4) Compare plant-zone protection with data-hall protection. | PREVENTIVE | IMPLEMENTATION | AL3 | DESIGN; BUILD; OPERATE; CHANGE | NORMAL; DEGRADED; MAINTENANCE; EMERGENCY; RECOVERY; TRANSITION | Applies to all physical sites in the boundary. Colocation tenants assess the zones they control and rely on provider evidence for shared zones. |  | CG-15; CG-09 | Generator yard protected only by perimeter fence; Ceiling void bypasses hall boundary; Zoning plan out of date with hall extension | FaultDomain; Safeguard; Threat; InfrastructureSystem | Inspection only. Above-ceiling and below-floor checks are performed by facilities staff under permit; assessors do not lift floor tiles in live halls. | If a critical plant area cannot be assigned to a zone or its boundary inspected, record a U5 UNKNOWN against that asset and treat its physical protection as unverified. | EN 50600-2-5 (security systems); ISO/IEC 27002 (physical security perimeters); ANSI/TIA-942 (data centre infrastructure) | MCF-PHY-013; MCF-PHY-015; MCF-SEC-009 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-PHY-010 | PHY | Physical Site, Building and Security Infrastructure | PHY-03 | Physical zoning and segregation | Fire Zones | Ensure that fire compartmentation separates redundant power, cooling and network paths so that a single fire cannot disable both halves of a redundant system, and limits fire and smoke spread between IT, battery, electrical and plant spaces. | The facility owner shall define fire compartments in the fire strategy so that A and B power paths, redundant UPS and battery rooms, redundant cooling plant and diverse network routes are in separate compartments or are protected by fire-rated enclosures of the declared rating. The facility operator shall maintain fire-stopping of every penetration through compartment boundaries and shall inspect a sample of penetrations at the declared interval and after works. | 1) The fire strategy identifies compartments and their fire-resistance ratings. 2) An overlay of redundant paths on compartments shows no single compartment containing both redundant elements of any path, or a rated enclosure where they share one. 3) Lithium-ion battery rooms (UPS or BESS) are separate compartments of at least the declared rating. 4) A sample of penetrations inspected shows intact, certified fire-stopping matching the tested system. 5) Penetrations created by works in the last 12 months have fire-stopping completion records. | Fire resistance between compartments holding redundant paths [minutes] default 120 (illustrative) (Fire strategy; national building regulations; capability profile) Fire-stopping inspection sample per interval [% of penetrations] default 20 (illustrative) (Capability profile) | Fire strategy and compartmentation drawings; Overlay of redundant paths on compartments; Fire-stopping register with certified product data; Penetration inspection records; Works completion records for new penetrations | DOCUMENT_REVIEW; ANALYSIS; INSPECTION; SAMPLING | 1) Overlay A/B power, redundant cooling and diverse network routes from the architecture onto the compartment drawings. 2) Identify any compartment hosting both redundant elements and check for rated enclosures. 3) Inspect a sample of penetrations against the fire-stopping register. 4) Review works records for penetrations created since the last inspection. | PREVENTIVE | IMPLEMENTATION | AL3 | DESIGN; BUILD; OPERATE; CHANGE | NORMAL; MAINTENANCE; EMERGENCY | Applies to all facilities. In modular or containerised deployments, compartments are the modules and the overlay shows separation between modules hosting redundant elements. | CG-09 | CG-04 | Single fire disables both A and B paths in a shared riser (AIDCF-004 X09); Unsealed penetration after cabling works; Battery fire spreads to adjacent UPS room | FaultDomain; Hazard; Safeguard; FailureScenario | Inspection only; no penetration is opened. Access to energised electrical rooms follows site electrical-safety rules. | If the redundant-path overlay cannot be produced, record a U5 UNKNOWN; CG-09 becomes UNKNOWN for fire as a common-mode initiator. | NFPA 75 (protection of IT equipment); NFPA 76 (fire protection of telecommunications facilities); EN 50600-2-1 (building construction); NFPA 855 (stationary energy storage systems) | MCF-PHY-021; MCF-POW-009; MCF-RES-006; MCF-NET-002 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-PHY-011 | PHY | Physical Site, Building and Security Infrastructure | PHY-03 | Physical zoning and segregation | Water Zones | Ensure that liquid-bearing systems, which are pervasive in liquid-cooled AI halls, are spatially and physically separated from electrical distribution and that any leak is contained, detected and drained before it reaches energised equipment. | The facility owner shall define water zones identifying all spaces where water, glycol, dielectric fluid or refrigerant-bearing pipework is present. The facility owner shall locate or protect electrical switchgear, UPS, busway and PDUs so that a leak from any pipe, joint, CDU, manifold or quick-disconnect cannot reach them uncontained, using routing above or below with drip trays, bunding, falls to drains and zoned leak detection that alarms and, where declared, initiates isolation. | 1) A water-zone plan shows every liquid-bearing route and its relation to electrical equipment. 2) No liquid joint or valve is located directly above switchgear, UPS, busway tap-off or PDU without containment. 3) Leak detection covers each containment area and alarms to a monitored location; where isolation is automatic, valve closure has been tested. 4) Drainage capacity for each zone is sized for the declared maximum credible leak rate. 5) Raised-floor or slab areas with liquid distribution have falls or barriers preventing migration to electrical zones. | Leak alarm to isolation time (automatic isolation zones) [s] default 60 (illustrative) (Capability profile; CDU OEM guidance) Maximum credible leak rate for drainage sizing [L/min] default per largest pipe and pump capacity in zone (Thermal design basis) | Water-zone plan overlaid on electrical layout; Leak detection layout and alarm configuration; Isolation valve functional test records; Drainage design calculation; Inspection photographs of containment under joints | DOCUMENT_REVIEW; INSPECTION; RECONCILIATION | 1) Overlay liquid routes on electrical layouts and list proximity conflicts. 2) Inspect each conflict for containment and leak detection. 3) Review alarm routing and isolation test records. 4) Check drainage falls and barriers in a sample of zones. | PREVENTIVE | IMPLEMENTATION | AL3 | DESIGN; BUILD; CHANGE | NORMAL; MAINTENANCE; DEGRADED | Applies to all spaces with liquid-bearing systems, including chilled-water air cooling. Most demanding for direct-to-chip and immersion halls. |  | CG-09; CG-04 | Quick-disconnect leak onto rack PDU; Glycol leak migrating under raised floor to busway; Leak detection alarm not routed; Drain overwhelmed by pump discharge | FaultDomain; Hazard; Safeguard; Interface | Assessors do not operate isolation valves. Functional tests of automatic isolation are performed by the operator under a method statement with the affected loop in a declared maintenance state. | If the overlay cannot be produced for a liquid-cooled hall, record a U5 UNKNOWN and carry it into THM leak-management and CG-09 evaluation. | ASHRAE TC 9.9 liquid cooling guidance; EN 50600-2-3 (environmental control) | MCF-THM-019; MCF-THM-020; MCF-PHY-010; MCF-POW-015 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-PHY-012 | PHY | Physical Site, Building and Security Infrastructure | PHY-03 | Physical zoning and segregation | Tenant Segregation | Ensure that, in shared or colocation facilities, each tenant's equipment and the shared infrastructure serving it are physically segregated and that responsibility for shared elements is explicit. | The facility provider shall physically segregate tenant spaces using cages, suites or dedicated halls with access restricted to authorised tenant personnel, and shall disclose to each tenant the shared infrastructure (power paths, cooling loops, meet-me rooms, risers) serving its space. The tenant shall map its capability to those shared elements and record provider and tenant responsibilities for each. | 1) Each tenant space is enclosed with access limited to that tenant and authorised provider staff. 2) The provider's disclosure lists the shared power, cooling and connectivity elements serving the tenant space. 3) A responsibility matrix covers each shared element, including maintenance switching notification. 4) Inspection finds no tenant equipment or cabling outside its space or in another tenant's space. |  | Provider disclosure of shared infrastructure; Responsibility matrix; Access lists for tenant spaces; Inspection notes | DOCUMENT_REVIEW; INSPECTION; INQUIRY | 1) Obtain disclosure and map shared elements to the tenant's capability architecture. 2) Inspect tenant space boundaries and shared cable routes. 3) Review the responsibility matrix for maintenance switching and incident notification. | PREVENTIVE | IMPLEMENTATION | AL3 | PLAN; BUILD; OPERATE; CHANGE | NORMAL; MAINTENANCE; EMERGENCY | Applies to colocation and multi-tenant facilities. Not applicable to single-tenant facilities, which record the determination. |  | CG-13; CG-02 | Undisclosed shared UPS serving multiple tenants; Neighbour tenant access to shared riser; Maintenance switching on shared path without tenant notification (AIDCF-004 X14) | Dependency; Interface; FaultDomain | Desk-based assessment; no hazardous testing. Site walk-downs follow the host site induction and are escorted in plant areas. | If the provider will not disclose shared elements, record a U2 UNKNOWN and a U10 dependency UNKNOWN for the affected power and cooling paths. | EN 50600-1 (general concepts); ISO/IEC 27002 (physical security) | MCF-DEP-019; MCF-DEP-018; MCF-PHY-009 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-PHY-013 | PHY | Physical Site, Building and Security Infrastructure | PHY-04 | Access and surveillance | Identity-Based Access | Ensure physical access to critical zones is granted to identified individuals on a need basis, is promptly revoked, and is recorded so that every entry to a critical space can be attributed. | The security manager shall operate a physical access control system that grants access to critical-space zones only to named individuals with approved business need, enforces multi-factor authentication at those zones, revokes access within the declared latency when a person leaves or changes role, and reviews critical-zone access rights at the declared interval. The security manager shall integrate leaver events from the authoritative HR or contractor source. | 1) Access rights to critical zones are traceable to an approval for every sampled holder. 2) Leavers in the sample period had critical-zone access revoked within the declared latency. 3) Access reviews for critical zones were completed at the declared interval with removals actioned. 4) Shared or generic credentials do not grant critical-zone access. 5) Access events are retained and time-synchronised for the declared period. | Critical-zone access review interval [days] default 90 (illustrative) (Capability profile) Leaver revocation latency [hours] default 4 (illustrative) (Capability profile) | Access-control system user and rights export; Approval records for sampled holders; HR/contractor leaver list reconciled to revocation logs; Access review sign-offs; Access event log sample | RECONCILIATION; SAMPLING; DOCUMENT_REVIEW | 1) Export critical-zone rights under observation and sample holders. 2) Trace each sampled holder to an approval. 3) Reconcile leavers in the period to revocation timestamps. 4) Review access-review evidence and removal actions. | PREVENTIVE | OPERATION | AL4 | OPERATE; CHANGE | NORMAL; DEGRADED; MAINTENANCE; EMERGENCY; RECOVERY; TRANSITION | Applies wherever the assessed party controls physical access; colocation tenants assess the provider's process for their space through provider evidence. |  | CG-15 | Leaver retains access to switchgear room; Contractor credential shared; Access rights accumulate | Safeguard; Threat; EvidenceObject | Desk-based assessment; no hazardous testing. Site walk-downs follow the host site induction and are escorted in plant areas. | If the leaver population cannot be obtained, record a U2 UNKNOWN; the OPERATION claim is UNKNOWN. | EN 50600-2-5 (security systems); ISO/IEC 27002 (physical entry controls); IEC 60839-11 (electronic access control systems) | MCF-PHY-009; MCF-PHY-014; MCF-SEC-001 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-PHY-014 | PHY | Physical Site, Building and Security Infrastructure | PHY-04 | Access and surveillance | Visitor Control | Ensure that visitors, vendors and contractors, including OEM field engineers servicing accelerator systems, are identified, authorised, escorted and supervised in critical spaces. | The security manager shall require pre-registration, identity verification and host approval for every visitor, shall issue time-limited credentials, and shall require escort in critical-space zones at no more than the declared visitor-to-escort ratio. The facility operator shall link contractor attendance in plant spaces to an approved work order or permit. | 1) Every sampled visitor entry has pre-registration, ID verification and host approval. 2) Visitor credentials expire at the end of the approved visit. 3) Escort ratio in critical zones did not exceed the declared value in sampled visits. 4) Contractor entries to plant spaces trace to an approved work order or permit. | Maximum visitors per escort in critical zones [ratio] default 3:1 (illustrative) (Capability profile) | Visitor management records; Credential issue and expiry logs; Work orders linked to contractor entries; Observation of a visitor process | SAMPLING; OBSERVATION; RECONCILIATION | 1) Sample visitor entries to critical zones. 2) Trace each to pre-registration, ID check and approval. 3) Reconcile contractor entries to work orders. 4) Observe a visitor journey. | PREVENTIVE | OPERATION | AL4 | OPERATE | NORMAL; MAINTENANCE; EMERGENCY | Applies to all staffed sites. Unstaffed edge sites apply the work-order linkage element only. |  |  | Unescorted vendor in data hall; Contractor working without permit; Credential reused after visit | Safeguard; Threat | Desk-based assessment; no hazardous testing. Site walk-downs follow the host site induction and are escorted in plant areas. | If visitor records are incomplete for the sample, record a U1 UNKNOWN and a Finding. | ISO/IEC 27002 (physical entry controls); EN 50600-2-5 (security systems) | MCF-PHY-013; MCF-OPS-007; MCF-SUP-021 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-PHY-015 | PHY | Physical Site, Building and Security Infrastructure | PHY-04 | Access and surveillance | Surveillance Coverage | Ensure video surveillance covers entries to critical zones, critical plant and high-value asset areas at an image quality sufficient for the declared purpose, with retention and integrity supporting investigation. | The security manager shall define an operational requirement for each camera view stating its purpose (detect, observe, recognise or identify), shall install and maintain cameras to meet it, shall retain recordings for the declared period with integrity protection, and shall verify coverage after layout changes. | 1) An operational requirement lists each critical zone entry and plant area with its purpose category. 2) Sampled camera views meet the image quality for their declared purpose. 3) Recordings are retained for the declared period and the sample retrieves successfully. 4) Camera health monitoring alarms on loss of view and outages are corrected within the declared time. 5) Exported footage has integrity protection (hash or signed export). | Recording retention [days] default 90 (illustrative) (Capability profile; local privacy law limits) Pixel density for identification views [px/m] default 250 (IEC 62676-4 operational requirement categories) | Operational requirement document; Camera layout; Sample stills per view; Retention configuration; Camera health logs | INSPECTION; SAMPLING; TEST | 1) Review the operational requirement against the zoning plan. 2) Sample views and assess image quality against purpose. 3) Retrieve a recording at the end of the retention window. 4) Review camera health alarms and outage closure. | DETECTIVE | IMPLEMENTATION | AL3 | DESIGN; BUILD; OPERATE; CHANGE | NORMAL; DEGRADED; MAINTENANCE; EMERGENCY; RECOVERY; TRANSITION | Applies where surveillance is a declared safeguard; privacy law may limit retention and is recorded as a constraint. |  |  | Blind spot at generator yard gate; Recordings overwritten before investigation; Camera outage undetected | Safeguard; EvidenceObject | Desk-based assessment; no hazardous testing. Site walk-downs follow the host site induction and are escorted in plant areas. | If retrieval cannot be demonstrated, record a U8 method UNKNOWN for surveillance evidence. | IEC 62676 series (video surveillance systems); EN 50600-2-5 (security systems) | MCF-PHY-009; MCF-PHY-016; MCF-EVA-006 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-PHY-016 | PHY | Physical Site, Building and Security Infrastructure | PHY-04 | Access and surveillance | Alarm Response | Demonstrate that intrusion, forced-door, held-door and tamper alarms at critical zones are acknowledged and physically attended within declared times, including at night and when many alarms occur together. | The security manager shall define acknowledgement and attendance times for each alarm class in critical zones, shall staff and equip the response to meet them, and shall test response by unannounced exercises at the declared interval, including an exercise during concurrent facility alarms. | 1) Alarm classes and target acknowledgement and attendance times are defined. 2) Alarm records for the period show the targets were met for the declared percentage of alarms. 3) At least the declared number of unannounced exercises were run and met attendance targets. 4) One exercise tested response while other facility alarms were active. 5) Missed targets have root cause and corrective action. | Alarm acknowledgement time [s] default 60 (illustrative) (Capability profile) Attendance time at critical-zone alarm [minutes] default 5 (illustrative) (Capability profile) Unannounced response exercises [per year] default 4 (illustrative) (Capability profile) | Alarm response procedure; Alarm logs with acknowledgement and attendance times; Exercise records; Corrective action records | TEST; SCENARIO_EXERCISE; ANALYSIS | 1) Analyse alarm logs for acknowledgement and attendance times by class. 2) Review exercises for design, unannounced status and results. 3) Conduct or witness an unannounced exercise at a plant-zone door. 4) Review corrective actions for missed targets. | DETECTIVE | EFFECTIVENESS | AL5 | OPERATE | NORMAL; EMERGENCY; DEGRADED | Applies to staffed or remotely monitored sites. Unstaffed sites declare remote-response times and use the same criteria. |  |  | Forced-door alarm acknowledged but not attended; Alarm missed during facility alarm flood (AIDCF-004 X11) | Safeguard; TestRecord; Event | Exercises are coordinated with the control room supervisor so that the exercise is not mistaken for a real event requiring emergency services; no exercise triggers suppression or EPO circuits. | If attendance times are not recorded, record a U1 UNKNOWN; the EFFECTIVENESS claim is UNKNOWN. | EN 50131 series (intrusion and hold-up alarm systems); EN 50600-2-5 (security systems) | MCF-PHY-015; MCF-OPS-013; MCF-SEC-019 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-PHY-017 | PHY | Physical Site, Building and Security Infrastructure | PHY-05 | Asset movement and custody | Delivery Controls | Ensure inbound deliveries of high-value AI hardware, storage media and critical spares are received against an expected manifest, inspected for tampering and held under custody until accepted. | The facility operator shall receive critical deliveries only against an advance notice and purchase reference, shall inspect seals and packaging for tampering, shall record serial numbers at receipt and shall hold received items in a controlled store until they are accepted into the asset register. | 1) Sampled deliveries trace to advance notice and purchase reference. 2) Seal and packaging inspection is recorded for every sampled critical delivery. 3) Serial numbers recorded at receipt match the shipping manifest and the asset register. 4) Received items are stored in a controlled zone until acceptance. | Inbound critical shipments with seal inspection [%] default 100 (illustrative) (Capability profile) | Goods-in records; Seal inspection records; Asset register entries; Controlled-store access logs | SAMPLING; RECONCILIATION; OBSERVATION | 1) Sample critical deliveries. 2) Trace to notice, inspection, serials and register. 3) Observe the controlled store. | PREVENTIVE | OPERATION | AL4 | BUILD; OPERATE | NORMAL | Applies to sites receiving accelerators, storage media, network optics or critical spares. |  |  | Tampered accelerator module accepted; Serial mismatch undetected; Delivery left in unsecured dock | AssetInstance; Threat; Safeguard | Desk-based assessment; no hazardous testing. Site walk-downs follow the host site induction and are escorted in plant areas. | If receipt records cannot be reconciled to serials, record a U5 UNKNOWN and refer to SUP provenance controls. | ISO 28000 (security management for the supply chain); ISO/IEC 27002 (delivery and loading areas) | MCF-SUP-011; MCF-SUP-010; MCF-PHY-018 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-PHY-018 | PHY | Physical Site, Building and Security Infrastructure | PHY-05 | Asset movement and custody | Equipment Movement | Ensure movement of dense racks and heavy plant within the facility is planned, authorised and executed without exceeding route ratings, damaging live infrastructure or creating tip-over and crush hazards. | The facility operator shall require a move plan, approved by the facilities engineer, for every movement of a rack or plant item above the declared mass threshold, stating route, route ratings, equipment (skates, tuggers, lifting), crew competence and proximity to live services. The facility operator shall drain or isolate liquid-cooled racks where the OEM requires it before movement. | 1) Every sampled move above threshold has an approved move plan. 2) Move plans reference route ratings from MCF-PHY-003 and floor ratings from MCF-PHY-005. 3) Crew competence for heavy moves is evidenced. 4) Liquid-cooled racks were moved in the OEM-required fluid state. 5) Move incidents (floor damage, near misses) are recorded and investigated. | Rack or plant mass requiring an approved move plan [kg] default 1,500 (illustrative) (Capability profile) | Move plans; Crew training records; Incident records; Observation of a move | SAMPLING; DOCUMENT_REVIEW; OBSERVATION | 1) Sample moves from work orders. 2) Check move plans for route and floor rating references. 3) Verify crew competence and fluid-state compliance. 4) Observe a move where scheduled. | PREVENTIVE | OPERATION | AL4 | BUILD; OPERATE; CHANGE; DECOMMISSION | NORMAL; MAINTENANCE | Applies to sites deploying racks or plant above the mass threshold. |  | CG-04 | Rack tip-over on ramp; Raised floor collapse under rolling load; Coolant spill during move | Hazard; Safeguard; AssetInstance | Assessors observe moves from outside the exclusion zone set by the move supervisor and never assist. | If move plans are missing for the sample, record a U1 UNKNOWN and a Finding. | Rack OEM installation and relocation guides; National manual-handling and lifting regulations | MCF-PHY-003; MCF-PHY-006; MCF-OPS-006 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-PHY-019 | PHY | Physical Site, Building and Security Infrastructure | PHY-05 | Asset movement and custody | Media Custody | Ensure storage media holding training data, checkpoints or model weights are inventoried and in unbroken custody whenever they are removed from service, in transit, under repair or awaiting destruction. | The facility operator shall maintain a serialised inventory of data-bearing media outside production service, shall record each custody transfer with time, person and location, shall store media in a controlled container or room, and shall reconcile the inventory at the declared interval. The data owner shall define which media classes require encryption verification before leaving the controlled store. | 1) Every data-bearing device removed from service in the sample appears in the custody inventory. 2) Custody transfers are recorded without gaps from removal to final disposition. 3) Inventory reconciliation at the declared interval shows no unexplained missing media. 4) Failed drives returned to OEMs under RMA follow the data owner's rule (retain, sanitise or encrypt). | Media custody inventory reconciliation interval [days] default 30 (illustrative) (Capability profile) | Custody inventory; Transfer logs; Reconciliation records; RMA records with media disposition | RECONCILIATION; REPERFORMANCE; SAMPLING | 1) Sample drive removals from storage health and ticket records. 2) Trace each to the custody inventory and transfers. 3) Reperform a reconciliation of the controlled store. 4) Review RMA disposition against the data owner's rule. | PREVENTIVE | OPERATION | AL4 | OPERATE; DECOMMISSION | NORMAL; MAINTENANCE; RECOVERY | Applies to all data-bearing media in the boundary, including accelerator node local NVMe. |  |  | Drive with model weights shipped under RMA unencrypted; Media missing from store; Custody gap during transit | AssetInstance; Threat; EvidenceObject | Desk-based assessment; no hazardous testing. Site walk-downs follow the host site induction and are escorted in plant areas. | If any media cannot be accounted for, record a Finding; if the inventory cannot be reconciled, record a U5 UNKNOWN. | NIST SP 800-88 (media sanitisation); IEEE 2883 (storage sanitisation); ISO/IEC 27002 (media handling) | MCF-PHY-020; MCF-STO-024; MCF-STO-023 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-PHY-020 | PHY | Physical Site, Building and Security Infrastructure | PHY-05 | Asset movement and custody | Decommissioning Custody | Ensure that equipment leaving the facility at end of life, including accelerators, servers, storage and network devices, is sanitised or destroyed to the declared standard with verified certificates, and that decommissioning does not disturb live infrastructure. | The facility operator shall decommission equipment only under an approved decommissioning work order that identifies the asset, its data-bearing components, dependent power and cooling connections and the sanitisation or destruction method. The facility operator shall obtain a certificate per serial from any third-party disposal provider and shall reconcile certificates to the decommissioning list. | 1) Each sampled decommissioned asset has an approved work order. 2) Sanitisation or destruction method matches the data owner's classification. 3) Certificates exist per serial and reconcile to the decommissioning list. 4) Isolation of power and liquid connections followed the approved method statement. | Decommissioned data-bearing devices with per-serial certificate [%] default 100 (illustrative) (Capability profile) | Decommissioning work orders; Sanitisation or destruction certificates; Reconciliation of certificates to asset list; Isolation method statements | RECONCILIATION; SAMPLING; DOCUMENT_REVIEW | 1) Sample decommissioned assets from the register. 2) Trace each to work order, method and certificate. 3) Review isolation evidence for liquid-cooled equipment. | PREVENTIVE | OPERATION | AL4 | DECOMMISSION | NORMAL; MAINTENANCE | Applies to all decommissioning in the boundary. |  |  | Unsanitised drive leaves site; Wrong rack isolated during decommissioning; Certificate missing | AssetInstance; Safeguard | Assessors do not witness isolations inside arc-flash boundaries; liquid disconnection is observed from outside the drip zone. | If certificates cannot be reconciled, record a U1 UNKNOWN per unreconciled serial and a Finding. | NIST SP 800-88 (media sanitisation); IEEE 2883 (storage sanitisation) | MCF-PHY-019; MCF-ENV-020; MCF-CMP-024 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-PHY-021 | PHY | Physical Site, Building and Security Infrastructure | PHY-06 | Fire, life safety and emergency interfaces | Fire Detection | Demonstrate that fire detection in IT, electrical, battery and plant spaces detects incipient fires early enough for safe evacuation and for controlled response before a fire disables redundant infrastructure, accounting for high airflow and liquid-cooled hall conditions. | The fire safety manager shall provide detection designed for the airflow conditions of each space: very early warning aspirating smoke detection in high-airflow IT halls and electrical rooms, and off-gas or appropriate gas detection plus heat and smoke detection in lithium-ion battery rooms and enclosures. The fire safety manager shall test detection functionally at the declared interval, including smoke transport time for aspirating systems, and shall ensure alarms are received at a continuously staffed location. | 1) Detection design for each space states the detection type and how high airflow was accounted for. 2) Lithium-ion battery rooms and BESS enclosures have off-gas detection as specified by the battery safety assessment, in addition to smoke and heat detection. 3) Functional tests at the declared interval cover all detectors or sampling points, with aspirating transport times within the design value. 4) Detection alarms are received and acknowledged at a continuously staffed location, demonstrated in the period. 5) Impairments are recorded with compensating measures and closed within the declared time. 6) Acceptance or periodic inspection by the authority having jurisdiction or a certified inspector is current. | Aspirating detection maximum transport time [s] default per design; not greater than the EN 54-20 class limit (EN 54-20 (aspirating smoke detectors); system design) Detection functional test interval [months] default 12 (illustrative) (NFPA 72 or national fire code; capability profile) Maximum detection impairment duration without compensating measure [hours] default 0 (illustrative) (Capability profile) | Detection design and cause-and-effect matrix; Functional test reports with transport times; Battery safety assessment specifying off-gas detection; Alarm receipt records; Impairment log; AHJ or certified inspector reports | DOCUMENT_REVIEW; TEST; INSPECTION; OBSERVATION | 1) Review detection design for airflow and battery hazards. 2) Check test reports for coverage, transport times and defects. 3) Witness a smoke or transport-time test at a sampled point. 4) Verify alarm receipt and acknowledgement at the staffed location. 5) Review impairment records and compensating measures. | DETECTIVE | EFFECTIVENESS | AL5 | DESIGN; COMMISSION; OPERATE; CHANGE | NORMAL; DEGRADED; MAINTENANCE; EMERGENCY; RECOVERY; TRANSITION | Applies to all facilities. Colocation tenants rely on provider test evidence and witness where contractually permitted. | CG-04 | CG-09 | Smoke diluted by high airflow below detector threshold; Battery off-gas undetected before thermal runaway; Aspirating pipe blocked; Alarm not received during control-room outage | Safeguard; Hazard; TestRecord | Detection tests use approved test aerosols or smoke sources; the fire safety manager isolates suppression release and notifies the alarm receiving centre before testing, and restores after. No test is performed in a battery room during a known battery fault. | If functional test evidence for detection in a battery room or IT hall is missing or older than the interval, record a US4 UNKNOWN against CG-04; testing that depends on the room (for example load tests) is not authorised until resolved. | NFPA 72 (fire alarm and signalling); EN 54 series (fire detection and fire alarm systems); NFPA 75 (protection of IT equipment); NFPA 855 (stationary energy storage systems); FM Global Property Loss Prevention Data Sheets (data centres; energy storage) | MCF-PHY-022; MCF-PHY-010; MCF-POW-010; MCF-ENV-017 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-PHY-022 | PHY | Physical Site, Building and Security Infrastructure | PHY-06 | Fire, life safety and emergency interfaces | Suppression Interfaces | Demonstrate that suppression systems and their interfaces with power, cooling, ventilation and control systems act as designed, so that suppression is effective without causing an avoidable loss of AI capability or an unsafe condition. | The fire safety manager shall maintain a cause-and-effect matrix covering every interface between detection, suppression (sprinkler, pre-action, water mist, gaseous agent) and other systems, including HVAC shutdown, damper closure, CDU and pump behaviour, power isolation and door release. The fire safety manager shall test the matrix end to end at the declared interval, shall verify room integrity for gaseous systems by enclosure test, and shall confirm that fire-mode actions do not stop liquid cooling to unaffected areas unless the fire strategy requires it. | 1) A cause-and-effect matrix exists and matches the configured logic in the fire panel and BMS. 2) End-to-end interface tests at the declared interval demonstrate each output, with deviations closed. 3) Gaseous-agent rooms pass an enclosure integrity test demonstrating the design hold time. 4) Fire-mode effects on liquid cooling and CDUs are defined, and unaffected halls keep cooling in the test. 5) Suppression agent quantity and cylinder pressure are verified at the declared interval. 6) Water-based suppression in IT spaces is pre-action or otherwise protected against inadvertent discharge, where the fire strategy requires. | Gaseous agent design hold time [minutes] default 10 (illustrative) (NFPA 2001 or ISO 14520 design practice; fire engineer's design) Enclosure integrity test interval [months] default 12 (illustrative) (Capability profile; agent standard) | Cause-and-effect matrix; Fire panel and BMS logic exports; End-to-end interface test reports; Enclosure integrity test reports; Agent quantity and cylinder inspection records | DOCUMENT_REVIEW; RECONCILIATION; TEST; OBSERVATION | 1) Reconcile the matrix to fire panel and BMS logic exports. 2) Review end-to-end test reports for coverage and deviations. 3) Witness an interface test where scheduled, including CDU behaviour. 4) Review enclosure integrity results against design hold time. 5) Confirm agent inventory and cylinder inspections. | CORRECTIVE | EFFECTIVENESS | AL5 | DESIGN; COMMISSION; OPERATE; CHANGE | NORMAL; EMERGENCY; MAINTENANCE | Applies wherever suppression is installed; partial applicability where only sprinklers exist (enclosure test not applicable). | CG-04 | CG-06; CG-07 | Fire alarm stops all CDUs site-wide; Gaseous agent leaks out before hold time; Damper fails open; Inadvertent discharge damages storage (acoustic) or IT (water) | Safeguard; Interface; TestRecord; Hazard | End-to-end tests are performed with agent release physically disabled and verified disabled before testing; HVAC and CDU interlocks are tested under a method statement approved by the facility operator with thermal contingency in place. Gaseous rooms are cleared and posted before enclosure tests; no assessor is present during any live discharge. | If the matrix cannot be reconciled to configured logic, or no end-to-end test is current, record a US4 UNKNOWN against CG-04 and refer the cooling interlock gap to CG-06. | NFPA 2001 (clean agent systems); ISO 14520 series (gaseous fire-extinguishing systems); NFPA 13 (sprinkler systems); NFPA 75 (protection of IT equipment) | MCF-PHY-021; MCF-PHY-024; MCF-ENV-004; MCF-THM-021 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-PHY-023 | PHY | Physical Site, Building and Security Infrastructure | PHY-06 | Fire, life safety and emergency interfaces | Egress and Emergency Access | Ensure occupants of data halls, plant rooms and battery rooms can escape safely and emergency responders can gain access, including in dense hot-aisle/cold-aisle containment, liquid-cooled halls with overhead manifolds and spaces protected by gaseous agents. | The fire safety manager shall maintain egress routes from every occupied space within the travel distances of the fire strategy, shall ensure secured doors on escape routes release on fire alarm or by local override, shall provide pre-discharge warning and abort controls for gaseous systems, and shall provide emergency responders with plans, hazard information (batteries, refrigerants, coolants, arc-flash hazards) and access means. | 1) Travel distances and exit widths in sampled spaces meet the fire strategy, including inside containment. 2) Containment doors and escape-route doors release on fire alarm and by local override, demonstrated. 3) Gaseous-agent spaces have audible and visual pre-discharge warnings and abort controls at exits. 4) Emergency responder information packs exist and include battery, refrigerant and electrical hazards. 5) Egress routes are unobstructed during inspection. 6) Emergency lighting is tested at the declared interval. | Emergency lighting full-duration test interval [months] default 12 (illustrative) (National emergency lighting standard (e.g. EN 50172); capability profile) | Fire strategy egress plans; Door release test records; Pre-discharge warning test records; Responder information pack; Emergency lighting test records; Inspection notes | INSPECTION; DOCUMENT_REVIEW; TEST | 1) Walk egress routes from the furthest point in sampled halls and plant rooms. 2) Test a sample of containment and escape doors for release. 3) Review gaseous warning and abort tests. 4) Review the responder pack for current hazards. | PREVENTIVE | OPERATION | AL4 | DESIGN; COMMISSION; OPERATE; CHANGE | NORMAL; DEGRADED; MAINTENANCE; EMERGENCY; RECOVERY; TRANSITION | Applies to all occupied facilities. Unoccupied modular units declare responder access only. | CG-04 |  | Escape blocked by containment doors that lock on power loss; Responders unaware of lithium-ion BESS; Abort control unreachable | Safeguard; Hazard | Door release tests are coordinated with security so that zone protection is maintained; tests that drop fire alarm outputs follow the fire safety manager's isolation procedure. | If egress in containment or battery rooms cannot be verified, record a US4 UNKNOWN for CG-04. | NFPA 101 (life safety code) or national building regulations; EN 50172 (emergency escape lighting); NFPA 2001 (clean agent systems) | MCF-PHY-021; MCF-PHY-022; MCF-POW-013 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-PHY-024 | PHY | Physical Site, Building and Security Infrastructure | PHY-06 | Fire, life safety and emergency interfaces | Emergency Shutdown Governance | Ensure emergency power-off (EPO) and other emergency shutdown functions protect people and responders while being protected against inadvertent or malicious activation that would cause an uncontrolled shutdown of AI capability. | The facility owner shall define the scope of each emergency shutdown function (EPO, battery disconnect, fuel shut-off, CDU emergency stop) and the authority to activate it. The facility operator shall protect activation devices against inadvertent operation (covers, two-action operation, location), shall verify by test at the declared interval that each function isolates exactly its declared scope, and shall review any activation as a significant incident. | 1) Each emergency shutdown function has a documented scope, activation authority and legal basis (code requirement or fire strategy). 2) Activation devices have protection against inadvertent operation and are labelled with scope. 3) Functional tests at the declared interval show each function isolates exactly its declared scope (no more, no less). 4) Remote or software activation paths, where present, are identified and protected under SEC controls. 5) Activations in the period were investigated with lessons applied. | Emergency shutdown functional test interval [months] default 12 (illustrative) (Capability profile; applicable electrical code) | Emergency shutdown scope schedule; Activation device inspection; Functional test reports; Incident records for activations; Control logic exports for remote paths | DOCUMENT_REVIEW; INSPECTION; TEST | 1) Review scope schedule and legal basis. 2) Inspect a sample of activation devices for protection and labelling. 3) Review functional test evidence for scope correctness. 4) Identify remote activation paths and confirm protection. | DIRECTIVE | EFFECTIVENESS | AL5 | DESIGN; COMMISSION; OPERATE; CHANGE | NORMAL; DEGRADED; MAINTENANCE; EMERGENCY; RECOVERY; TRANSITION | Applies wherever EPO or emergency shutdown functions are installed; where codes do not require EPO and none is installed, battery and fuel shut-off elements still apply. | CG-04 | CG-07; CG-09 | Unprotected EPO button pressed in error; EPO scope wider than labelled; Remote EPO path reachable from IT network; Battery disconnect fails to isolate | Safeguard; Interface; Hazard; TestRecord | EPO and shutdown function tests are hazardous to capability: they are performed only during an approved shutdown window or with the load transferred, under a method statement approved by the facility owner's authorised engineer, with written authorisation and a rollback plan. Assessors witness and do not operate. | If the actual scope of an EPO function has never been verified by test, record a US4 UNKNOWN against CG-04 and an associated UNKNOWN on CG-09 for unbounded shutdown scope. | NFPA 70 (information technology equipment provisions); NFPA 75 (protection of IT equipment); IEC 60204-1 (emergency stop principles, by analogy) | MCF-PHY-022; MCF-POW-023; MCF-SEC-005 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-POW-001 | POW | Electrical Power Infrastructure and Energy Continuity | POW-01 | Utility and grid interface | Utility Capacity | Demonstrate that contracted and physically available utility import capacity covers the declared peak site demand, including AI training clusters at full power, cooling at design ambient and battery recharge after an outage, with margin and with a forecast that precedes deployments. | The facility owner shall hold a connection agreement stating firm import capacity and any non-firm or curtailable portions, and shall maintain a site demand model that sums IT load at declared accelerator power limits, cooling and mechanical load at design ambient, losses, and UPS/BESS recharge load. The facility owner shall show firm capacity exceeds modelled peak demand by the declared margin, shall compare modelled with metered peak demand at least quarterly, and shall not commission additional AI capacity that would erode the margin without an approved capacity increase or load-limiting measure. | 1) The connection agreement states firm import capacity, non-firm portions and any curtailment terms. 2) The demand model includes IT load at declared power limits, mechanical load at design ambient, distribution and conversion losses, and UPS/BESS recharge. 3) Firm capacity exceeds modelled peak demand by at least the declared margin. 4) Metered 15-minute or finer peak demand over the period is within the modelled value, or the model has been corrected. 5) Planned AI deployments in the next forecast horizon are included and a capacity gap, if any, has an approved remediation before deployment. 6) Transformer and incomer ratings in the as-built single-line diagram are consistent with the firm capacity and the demand model. | Margin of firm import capacity over modelled peak demand [% of firm capacity] default 10 (illustrative) (Capability profile) Demand forecast horizon [months] default 36 (illustrative) (Capability profile; utility lead times) Metered demand integration interval [minutes] default 15 or finer (Utility tariff metering practice; finer resolution needed to capture AI load dynamics) | Connection agreement and any curtailment/flexible connection terms; Site demand model with assumptions (accelerator power limits, PUE at design ambient, recharge); Metered demand data from the revenue or EPMS meters for the period; As-built single-line diagram with incomer and transformer ratings; Capacity forecast and approved remediation actions | DOCUMENT_REVIEW; ANALYSIS; RECONCILIATION | 1) Extract firm and non-firm capacity and curtailment terms from the agreement. 2) Rebuild the demand model from rack power limits, mechanical design data and recharge rates. 3) Compare with metered peaks at the finest available resolution. 4) Check margin and forecast deployments against firm capacity. 5) Reconcile incomer and transformer ratings on the single-line diagram. | PREVENTIVE | OPERATION | AL4 | PLAN; DESIGN; OPERATE; CHANGE | NORMAL; DEGRADED; RECOVERY | Applies to every site drawing utility power. For colocation tenants the provider's capacity allocation to the tenant's suite replaces the connection agreement. | CG-05 | CG-03 | Peak demand exceeds firm capacity during seasonal cooling peak; Recharge load after outage trips incomers; Non-firm capacity relied on for critical load; Deployment commissioned before capacity upgrade | CapacityAssertion; Dependency; Resource; InfrastructureSystem | Desk-based analysis and meter data export; no switching or measurement inside energised enclosures. | If metered peak demand for the cooling peak season is unavailable, record a U5 UNKNOWN; CG-05 becomes UNKNOWN for the capacity criterion until data for that season exists. | EN 50600-2-2 (power supply and distribution); Distribution or transmission network connection codes of the jurisdiction (e.g. EU Network Code on Demand Connection); IEC 60076 (power transformers) | MCF-POW-002; MCF-POW-004; MCF-POW-020; MCF-CAP-014 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-POW-002 | POW | Electrical Power Infrastructure and Energy Continuity | POW-01 | Utility and grid interface | Grid Quality | Establish the actual quality of the utility supply at the point of common coupling (voltage variations, dips, swells, interruptions, unbalance, flicker and harmonics) and confirm that the facility's ride-through and conversion equipment is specified for it. | The facility operator shall measure supply quality at each utility point of common coupling using power quality instruments conforming to IEC 61000-4-30 Class A, shall retain events and statistics for the declared period, and shall compare measured characteristics with the voltage characteristics assumed in the design basis and with the utility's declared characteristics. The facility operator shall report events that exceeded design assumptions to the electrical engineer responsible for MCF-POW-019 for evaluation. | 1) Class A power quality monitoring is installed at each utility point of common coupling. 2) Statistics for voltage magnitude, unbalance, flicker and harmonics are available for the period. 3) All dips, swells and interruptions in the period are logged with magnitude and duration. 4) Measured characteristics are compared with the design basis and the utility's declared characteristics. 5) Events outside design assumptions have an engineering evaluation. | Supply voltage variation assumed in design [% of nominal] default ±10 (illustrative) (EN 50160 voltage characteristics or utility declaration) Power quality data retention [months] default 24 (illustrative) (Capability profile) | Power quality instrument list and Class A certificates; PQ statistics and event logs; Design basis voltage assumptions; Utility declared characteristics or connection terms; Engineering evaluations of exceeding events | ANALYSIS; DOCUMENT_REVIEW; INSPECTION | 1) Confirm instrument class and location at each PCC. 2) Analyse event logs and statistics for the period. 3) Compare with design assumptions and utility declaration. 4) Review evaluations of exceeding events. | DETECTIVE | OPERATION | AL4 | COMMISSION; OPERATE | NORMAL; DEGRADED | Applies to sites with a direct utility connection. Colocation tenants obtain provider PQ data at the tenant's UPS input. |  | CG-05 | Frequent dips cause UPS battery cycling and premature ageing; Unbalance overheats transformers; Grid harmonics excite filter resonance | Resource; Event; Dependency | Instrument data is retrieved via EPMS; installation of portable PQ loggers inside energised panels is performed only by authorised persons under permit with appropriate PPE. | If no Class A data exists at the PCC, record a U1 UNKNOWN; ride-through claims under MCF-POW-019 are limited to design evidence. | IEC 61000-4-30 (power quality measurement methods); EN 50160 (voltage characteristics of public supply); IEEE 1159 (monitoring electric power quality) | MCF-POW-017; MCF-POW-019; MCF-POW-018 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-POW-003 | POW | Electrical Power Infrastructure and Energy Continuity | POW-01 | Utility and grid interface | Connection Reliability | Establish the real independence and reliability of the utility connection(s), including shared upstream substations, transmission circuits and protection schemes, so that claimed dual feeds are not a single upstream fault domain. | The facility owner shall obtain from the network operator the upstream topology of each utility feed to the first point of independent supply, and shall identify shared substations, busbars, circuits, rights-of-way and protection schemes. The facility owner shall record the historic interruption performance of each feed, and shall not describe feeds as independent in the design basis unless no shared upstream element is identified. | 1) Upstream topology to the first independent source point is documented for each feed. 2) Shared upstream elements (substation, bus, circuit, route, protection) are listed or explicitly none. 3) Interruption history for each feed over the declared period is recorded. 4) Design basis claims of feed independence are consistent with the shared-element list. 5) Residual common-mode exposures are reflected in generator and UPS autonomy sizing. | Interruption history period [years] default 5 (illustrative) (Capability profile; network operator data) | Network operator topology statement; Shared-element list; Interruption history; Design basis feed independence statement | DOCUMENT_REVIEW; ANALYSIS; INQUIRY | 1) Obtain topology and trace each feed upstream. 2) Identify shared elements and compare with design basis claims. 3) Review interruption history and correlation between feeds. | DIRECTIVE | DESIGN | AL2 | PLAN; DESIGN; CHANGE | NORMAL; DEGRADED; EMERGENCY | Applies to all utility-connected sites; most significant where the design basis claims dual independent feeds. |  | CG-03; CG-05; CG-09 | Two feeds from the same grid substation bus; Shared overhead route damaged by storm; Common intertrip scheme | Dependency; FaultDomain; InfrastructureSystem | Desk-based. | If the network operator does not provide upstream topology, record a U10 dependency UNKNOWN and treat feeds as one fault domain for CG-05 sizing. | IEEE 3006 series (power system reliability); EN 50600-2-2 (power supply and distribution) | MCF-POW-001; MCF-POW-004; MCF-DEP-005; MCF-DEP-009 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-POW-004 | POW | Electrical Power Infrastructure and Energy Continuity | POW-01 | Utility and grid interface | Utility Contingency | Ensure the facility can sustain declared outcomes through prolonged utility interruption, grid emergency instructions, curtailment and demand-response events, and can meet its grid connection obligations as a large load. | The facility owner shall maintain a utility contingency plan covering prolonged interruption, grid-operator curtailment or disconnection instructions, demand-response commitments and re-energisation constraints. The facility owner shall define, for each event type, which AI workloads are shed or throttled, how cooling and IT load are reduced in a controlled sequence, the decision authority, and the communications with the network operator, and shall exercise the plan at the declared interval. | 1) The plan covers prolonged outage, curtailment instruction, demand response and re-energisation. 2) Load-reduction steps identify workloads (by class or cluster), expected MW reduction and time to achieve it. 3) Workload throttling or checkpoint-and-pause is demonstrated in an exercise to achieve the declared reduction within the declared time. 4) Contractual obligations as a large load (notification, ride-through, ramp limits) are listed and mapped to procedures. 5) Decision authority and network-operator contacts are current. | Time to achieve declared load reduction on curtailment instruction [minutes] default 15 (illustrative) (Connection agreement; capability profile) Plan exercise interval [months] default 12 (illustrative) (Capability profile) | Utility contingency plan; Connection obligations list; Exercise records with achieved MW reduction and time; Contact and authority lists | DOCUMENT_REVIEW; SCENARIO_EXERCISE; ANALYSIS | 1) Review plan coverage against event types. 2) Trace load-reduction steps to scheduler or power-capping mechanisms. 3) Review or observe an exercise and compare achieved reduction with plan. 4) Check obligations mapping and contacts. | RECOVERY | RESILIENCE | AL5 | PLAN; OPERATE | EMERGENCY; DEGRADED; RECOVERY | Applies to sites with grid connection agreements that include curtailment, flexibility or large-load obligations, and to all sites for prolonged outage planning. |  | CG-05; CG-10 | Curtailment instruction cannot be met in time; Uncontrolled shedding loses training state; Re-energisation inrush violates connection limits | FailureScenario; Safeguard; Dependency; OperatingState | Exercises use workload throttling or scheduler controls; no electrical switching is performed for the exercise unless separately authorised under MCF-POW-023. | If the plan has never been exercised, record a U5 UNKNOWN; the RESILIENCE claim is UNKNOWN and supports design only. | EU Network Code on Demand Connection (Regulation (EU) 2016/1388); Network operator large-load connection requirements of the jurisdiction; ISO 22301 (business continuity management) | MCF-POW-001; MCF-POW-020; MCF-RES-002; MCF-CMP-010 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-POW-005 | POW | Electrical Power Infrastructure and Energy Continuity | POW-02 | Generation and fuel | Generator Capacity | Demonstrate that standby or prime generation can carry the declared critical load, including mechanical load and AI load dynamics, with the declared redundancy, at site design ambient and altitude, for the declared duration. | The facility owner shall size generation using the ISO 8528-1 rating class appropriate to the duty (for example data-centre continuous power where unlimited running hours at variable load are required) with derating for design ambient temperature, altitude and fuel. The facility owner shall verify by load-bank or real-load testing at commissioning and at the declared interval that each generator, and the paralleled system, carries its rated load at the declared redundancy with one unit out of service. | 1) Generator rating class and kW rating per ISO 8528-1 are recorded and are appropriate to the declared duty and running hours. 2) Derated capacity at site design ambient and altitude covers critical IT plus mechanical load with the declared redundancy (for example N+1) available. 3) Commissioning and periodic load-bank or real-load tests reached the declared load and duration for each unit and the paralleled system. 4) Generator capacity is reconciled to the current demand model in MCF-POW-001. 5) Radiator and air-intake performance at design ambient (including recirculation in the yard) is accounted for in derating. | Generator redundancy [topology] default N+1 (illustrative) (Capability profile; outcome tolerance) Site design ambient for generator derating [°C] default site extreme design value (ASHRAE climatic data, n-year return; illustrative n=20) (ASHRAE Handbook climatic design data; capability profile) Periodic load-bank test duration at rated load [hours] default 4 (illustrative) (NFPA 110 or national emergency power practice; capability profile) | Generator datasheets with ISO 8528 rating class; Derating calculation for ambient and altitude; Commissioning load-bank reports; Periodic load test records; Yard airflow/recirculation study | DOCUMENT_REVIEW; ANALYSIS; TEST; REPERFORMANCE | 1) Verify rating class and duty match. 2) Recompute derated capacity at design ambient and altitude. 3) Compare with demand model and redundancy with one unit out. 4) Review load test records for load, duration and anomalies. 5) Witness a load test where scheduled. | PREVENTIVE | EFFECTIVENESS | AL5 | DESIGN; COMMISSION; OPERATE; CHANGE | NORMAL; MAINTENANCE; EMERGENCY | Applies to sites with on-site generation for critical load. Not applicable where the declared outcome tolerance accepts loss on utility failure beyond UPS autonomy and this is approved. | CG-05 |  | Generators derate below load during heatwave; Prime-rated units used beyond rating class; Paralleled system cannot carry load with one unit out | CapacityAssertion; InfrastructureSystem; TestRecord | Hazardous-energy activity. Tests and switching are performed only by authorised persons under the site electrical safety rules, an approved method statement and permit to work, with written authorisation from the facility owner's authorised engineer; assessors witness from outside the arc-flash boundary and never operate equipment. Load-bank connection points are engineered; temporary cabling is inspected before energising. | If no load test at rated load exists within the interval, record a US4 UNKNOWN against CG-05. | ISO 8528 series (reciprocating engine generating sets); NFPA 110 (emergency and standby power systems); EN 50600-2-2 (power supply and distribution) | MCF-POW-006; MCF-POW-007; MCF-ENV-021; MCF-POW-020 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-POW-006 | POW | Electrical Power Infrastructure and Energy Continuity | POW-02 | Generation and fuel | Start Reliability | Demonstrate that generators start, synchronise and accept load within the time the UPS or BESS autonomy allows, on every demand, including after long standby periods and in cold or hot ambient. | The facility operator shall test each generator by monthly start and run tests at the declared load and by periodic transfer tests through the automatic transfer or paralleling controls, shall record start time, time to ready-to-load and anomalies, shall maintain starting systems (batteries or air, jacket-water heating, fuel priming), and shall treat any failed or delayed start as an incident with root cause analysis. | 1) Monthly start/run tests at the declared load and duration are recorded for every unit. 2) Recorded start-to-ready-to-load time is within the declared limit and within the UPS/BESS autonomy with margin. 3) Starting batteries or air systems, jacket-water heaters and fuel priming are maintained and monitored. 4) Failed or delayed starts in the period have root cause and corrective action. 5) Paralleling or transfer control sequences have been tested end to end at the declared interval. | Maximum start-to-load-acceptance time [s] default 10 (illustrative; NFPA 110 Type 10 defines 10 s) (NFPA 110 type classification; UPS autonomy) Monthly test load [% of nameplate] default 30 (illustrative) (NFPA 110 monthly exercise practice) Start reliability threshold for incident review [failed or delayed starts per year] default 0 (illustrative) (Capability profile) | Generator test logs with times; Controller event logs; Starting system maintenance records; Incident and RCA records; End-to-end transfer test reports | ANALYSIS; RECONCILIATION; TEST; SAMPLING | 1) Analyse twelve months of tests for completeness, timing and load. 2) Reconcile manual logs to controller event logs. 3) Review starting system maintenance and alarms. 4) Review failed or delayed starts and RCA. 5) Witness a monthly test where scheduled. | PREVENTIVE | OPERATION | AL4 | COMMISSION; OPERATE | NORMAL; MAINTENANCE; EMERGENCY | Applies to all critical-load generators. | CG-05 | CG-07 | Starting battery failure (AIDCF-004 X01); Fuel line air lock after maintenance; Paralleling controller fails to close breaker; Cold-start delay exceeds UPS autonomy | InfrastructureSystem; TestRecord; FailureMode; Event | Hazardous-energy activity. Tests and switching are performed only by authorised persons under the site electrical safety rules, an approved method statement and permit to work, with written authorisation from the facility owner's authorised engineer; assessors witness from outside the arc-flash boundary and never operate equipment. Transfer tests with live critical load require approval of the test window and confirmation that UPS/BESS autonomy and redundancy are healthy before starting. | If monthly test records are missing for any unit for more than one month, or controller logs cannot corroborate timing, record a US4 UNKNOWN against CG-05. | NFPA 110 (emergency and standby power systems); ISO 8528 series (generating sets) | MCF-POW-005; MCF-POW-011; MCF-POW-021; MCF-OPS-010 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-POW-007 | POW | Electrical Power Infrastructure and Energy Continuity | POW-02 | Generation and fuel | Fuel Autonomy | Demonstrate that on-site fuel stored, usable and of acceptable quality supports generation at the declared load for the declared autonomy, without relying on deliveries during that period. | The facility operator shall maintain usable on-site fuel (excluding unusable tank bottoms and day-tank minimums) sufficient for the declared autonomy at the declared load, using measured consumption curves, and shall keep the minimum stock level as an alarmed threshold. The facility operator shall test fuel quality at the declared interval against the applicable fuel specification, shall polish or replace fuel that fails, and shall maintain fuel transfer pumps and controls in a redundant configuration matching the generator redundancy. | 1) Usable fuel volume is calculated excluding unusable volumes and is at or above the minimum level for the declared autonomy at the declared load. 2) Consumption is based on measured or OEM curves at the declared load, not nameplate maximum only. 3) Fuel level telemetry with a minimum-stock alarm exists and is reconciled to dip or delivery records. 4) Fuel quality tests at the declared interval meet the fuel specification, or remediation is recorded. 5) Fuel transfer pumps, controls and piping have no single point of failure that disables more than the generator redundancy allows. 6) For renewable diesel (HVO) or blends, OEM approval and storage stability are documented. | On-site fuel autonomy at declared load [hours] default 48 (illustrative) (Capability profile; outcome tolerance and replenishment risk) Fuel quality test interval [months] default 6 (illustrative) (Capability profile; fuel specification (EN 590, ASTM D975 or EN 15940)) | Autonomy calculation with usable volumes and consumption curve; Fuel level telemetry and alarm configuration; Dip and delivery reconciliation; Fuel test certificates; Fuel system schematic showing pump redundancy | ANALYSIS; RECONCILIATION; DOCUMENT_REVIEW; INSPECTION | 1) Recompute usable volume and autonomy at declared load. 2) Reconcile telemetry to dips and deliveries. 3) Review fuel test certificates. 4) Trace fuel transfer system for single points of failure. | PREVENTIVE | OPERATION | AL4 | DESIGN; OPERATE; CHANGE | NORMAL; EMERGENCY; MAINTENANCE | Applies to sites with liquid-fuelled generation. Gas-fuelled sites substitute supply-pressure and pipeline-dependency evidence and are assessed under MCF-POW-008 for supply continuity. | CG-05 |  | Autonomy overstated by counting unusable volume; Microbial contamination blocks filters; Single transfer pump failure starves day tanks | Resource; CapacityAssertion; InfrastructureSystem | Fuel sampling follows the site's fuel handling procedure (ignition-source control, spill kit); assessors do not take samples. | If usable volume cannot be established, record a US4 UNKNOWN against CG-05 for autonomy. | NFPA 110 (emergency and standby power systems); NFPA 30 (flammable and combustible liquids); EN 590 / ASTM D975 / EN 15940 (fuel specifications) | MCF-POW-008; MCF-ENV-019; MCF-POW-005 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-POW-008 | POW | Electrical Power Infrastructure and Energy Continuity | POW-02 | Generation and fuel | Fuel Replenishment | Ensure that fuel can be replenished before on-site autonomy is exhausted during a regional emergency, when road access, supplier capacity and competing priority customers are constrained. | The facility owner shall hold fuel supply contracts with at least the declared number of independent suppliers, specifying guaranteed delivery lead time during declared emergencies, priority status and delivery capacity. The facility operator shall maintain a refuelling procedure that includes delivery while generators run, and shall exercise a delivery under emergency conditions or verify supplier capability at the declared interval. | 1) Contracts with the declared number of independent suppliers (not sharing a terminal) exist. 2) Guaranteed emergency lead time is shorter than on-site autonomy by the declared margin. 3) Supplier delivery capacity covers consumption at declared load for the outage duration being planned. 4) A refuelling-while-running procedure exists and has been performed or exercised. 5) Supplier capability was verified within the interval (exercise or real delivery record). | Guaranteed emergency resupply lead time [hours] default 12 (illustrative) (Supply contracts; capability profile) Independent fuel suppliers [count] default 2 (illustrative) (Capability profile) | Fuel supply contracts; Supplier terminal locations; Refuelling procedure; Delivery exercise or real delivery records | DOCUMENT_REVIEW; INQUIRY; SCENARIO_EXERCISE | 1) Review contracts for lead time, priority and capacity. 2) Check supplier independence (terminal, transport). 3) Compare lead time with autonomy. 4) Review or observe a delivery exercise. | RECOVERY | RESILIENCE | AL5 | PLAN; OPERATE | EMERGENCY; RECOVERY | Applies wherever declared outage tolerance exceeds on-site fuel autonomy. Where autonomy alone covers the declared outage scenario, the control is assessed at DESIGN depth only. |  | CG-05; CG-03; CG-10 | Both suppliers served from one terminal; Delivery blocked by flood; Supplier prioritises hospitals in regional emergency | Dependency; Resource; FailureScenario | Refuelling-while-running exercises follow the fuel handling procedure with fire watch; assessors observe from outside the delivery hazard zone. | If emergency lead time is not contractually defined, record a U10 dependency UNKNOWN and limit CG-05 conclusions to on-site autonomy. | NFPA 110 (emergency and standby power systems); ISO 22301 (business continuity management) | MCF-POW-007; MCF-PHY-003; MCF-SUP-019; MCF-DEP-014 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-POW-009 | POW | Electrical Power Infrastructure and Energy Continuity | POW-03 | UPS and energy storage | UPS Topology | Demonstrate that the as-built UPS and critical distribution topology (N, N+1, 2N, distributed or block redundant, or rack-level battery backup) delivers the declared Service Outcomes in every declared operating state, judged by failure analysis rather than by topology label. | The electrical engineer of record shall document the UPS topology and IEC 62040-3 performance classification of each system, and shall perform a failure analysis that, for every single component failure and every planned maintenance state, identifies the critical load that remains supported and the resulting loading of surviving modules. The facility owner shall reconcile the as-built single-line diagram to the analysis and shall not claim a redundancy level the analysis does not support for the declared load. | 1) The as-built single-line diagram reconciles to the installed UPS, static switch and distribution configuration in a site inspection sample. 2) Each UPS system's IEC 62040-3 classification (e.g. VFI) and operating mode (double conversion, eco-mode) is recorded. 3) A failure analysis covers every single UPS module, battery string, static switch and distribution board failure and every planned maintenance state. 4) In each analysed state, surviving modules remain within rating at the declared load including AI load swings; for distributed redundant designs, load reallocation after a failure is shown. 5) The redundancy claim stated in reports matches the analysis outcome at the current load. 6) Rack-level battery backup units, where used, are included and their interaction with upstream UPS is analysed. | Declared UPS redundancy [topology] default 2N or distributed redundant (illustrative) (Capability profile) Maximum normal-state loading of each path in a 2N design [% of path rating] default 45 (illustrative) (Capability profile; failure analysis) | As-built single-line diagram; UPS datasheets with IEC 62040-3 classification; Failure and maintenance-state analysis; Load data per UPS and path; Inspection reconciliation | RECONCILIATION; ANALYSIS; INSPECTION | 1) Reconcile single-line diagram to installed equipment in a sample. 2) Review failure analysis completeness against component and maintenance-state list. 3) Recompute surviving-module loading using current and peak AI load. 4) Compare redundancy claims in reports with analysis results. | PREVENTIVE | IMPLEMENTATION | AL3 | DESIGN; BUILD; COMMISSION; CHANGE | NORMAL; MAINTENANCE; DEGRADED; TRANSITION | Applies to all UPS-backed critical load. For AI clusters deliberately designed without UPS on accelerator load (relying on checkpointing), the analysis records that decision and its approval and remains applicable to cooling and control loads. | CG-05 | CG-09; CG-02 | Distributed redundant reserve consumed by growth; Maintenance state leaves load on single module; Topology label 2N but shared output switchboard; Eco-mode transfer exposes load to grid transients | ArchitectureSnapshot; FaultDomain; CapacityAssertion; InfrastructureSystem | Inspection only; panel covers are not removed. Load data is obtained from EPMS. | If the as-built single-line diagram cannot be reconciled, record a US4 UNKNOWN against CG-05 and a U5 against CG-02 architecture integrity. | IEC 62040-3 (UPS performance and test requirements); IEC 62040-1 (UPS safety); EN 50600-2-2 (power supply and distribution); IEEE 3006 series (reliability) | MCF-POW-011; MCF-POW-012; MCF-POW-020; MCF-RES-005 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-POW-010 | POW | Electrical Power Infrastructure and Energy Continuity | POW-03 | UPS and energy storage | Battery Condition | Ensure UPS, BESS and rack-level batteries retain the capacity assumed in runtime claims and that lithium-ion and lead-acid hazards (thermal runaway, off-gassing, hydrogen evolution) are detected and managed before they cause fire or loss of energy storage. | The facility operator shall monitor battery condition continuously (cell or block voltage, temperature, internal resistance or impedance, and for lithium-ion the battery management system state of health and alarms), shall perform capacity tests at the declared interval, and shall replace batteries at the end-of-life capacity threshold. The facility owner shall hold a battery safety assessment for each lithium-ion installation, using large-scale fire test data (for example UL 9540A) to set separation, ventilation, explosion control and detection, and shall maintain hydrogen ventilation for vented lead-acid rooms. | 1) Continuous battery monitoring covers every string or rack and alarms to a staffed location. 2) Capacity tests at the declared interval show every string above the end-of-life threshold, or replacement is scheduled before the next interval. 3) Lithium-ion BMS alarms (over-temperature, cell imbalance, communication loss) are configured, routed and acted on within the declared time. 4) A battery safety assessment exists for each lithium-ion installation and its required measures (separation, explosion control, off-gas detection, suppression) are installed. 5) Rack-level battery backup units are inventoried, monitored and included in the safety assessment. 6) Vented lead-acid rooms have ventilation sized for hydrogen evolution and it is interlocked or alarmed. | Battery end-of-life capacity threshold [% of rated capacity] default 80 (IEEE 450 / IEEE 1188 replacement criterion for lead-acid; OEM criterion for lithium-ion) Battery capacity test interval [months] default 12 (illustrative) (Capability profile; IEEE 450/1188) BMS critical alarm response time [minutes] default 15 (illustrative) (Capability profile) | Battery monitoring configuration and alarm routing; Capacity test reports; BMS alarm logs and responses; Battery safety assessment with UL 9540A or equivalent data; Ventilation design and tests for lead-acid rooms; Rack BBU inventory | ANALYSIS; DOCUMENT_REVIEW; INSPECTION; TEST | 1) Review monitoring coverage and alarm routing. 2) Analyse capacity test results against threshold. 3) Review BMS alarm handling in the period. 4) Review the battery safety assessment and inspect required measures. 5) Inventory rack BBUs and confirm monitoring. | DETECTIVE | OPERATION | AL4 | DESIGN; COMMISSION; OPERATE; CHANGE; DECOMMISSION | NORMAL; MAINTENANCE; DEGRADED; EMERGENCY | Applies to all battery energy storage supporting critical load, including UPS strings, BESS and rack-level BBUs. Supercapacitor-only systems apply monitoring and safety elements. | CG-04 | CG-05 | Lithium-ion thermal runaway propagating between racks; Hydrogen accumulation in lead-acid room; String capacity below runtime assumption; BMS communication loss hides cell fault | Hazard; AssetInstance; Safeguard; InfrastructureSystem | Discharge capacity tests are hazardous-energy activities and also reduce autonomy: they are performed by authorised persons under permit with the string isolated from critical load or with redundancy confirmed, written authorisation, and battery-hazard PPE. No test is performed on a lithium-ion string with an active BMS fault. | If no battery safety assessment exists for a lithium-ion installation, record a US4 UNKNOWN against CG-04; hazardous testing in that room is not authorised until resolved. | IEC 62619 (safety of industrial lithium batteries); IEC 62485 (safety of secondary battery installations); NFPA 855 (stationary energy storage systems); UL 9540 / UL 9540A (ESS safety and thermal runaway fire test method); IEEE 450 and IEEE 1188 (lead-acid battery maintenance) | MCF-POW-011; MCF-PHY-021; MCF-ENV-017; MCF-THM-019 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-POW-011 | POW | Electrical Power Infrastructure and Energy Continuity | POW-03 | UPS and energy storage | Runtime and Derating | Demonstrate that UPS and BESS runtime at the declared load, at end-of-life battery capacity and worst-case room temperature, exceeds the time needed for generators to accept load (or for orderly workload preservation where no generation exists) with margin. | The electrical engineer shall calculate runtime per UPS system at the declared load using end-of-life capacity and the battery temperature derating at the highest declared battery room temperature, and shall compare it with the generator start-to-load time and the time needed to checkpoint or gracefully pause AI workloads. The facility operator shall verify runtime by a discharge test at the declared interval and shall recalculate after load growth. | 1) Runtime calculations use end-of-life capacity, current declared load and worst-case battery temperature. 2) Calculated runtime exceeds generator start-to-load time plus the declared margin. 3) Where generation is absent or fails, runtime exceeds the time needed to complete declared workload preservation (checkpoint or pause) demonstrated by CMP/STO controls. 4) A discharge test at the declared interval confirmed runtime at or above calculation at a representative load. 5) Recalculation was performed after each load increase above the declared threshold. | Minimum UPS/BESS runtime at declared load, end of life [minutes] default 5 (illustrative) (Capability profile; generator start time and workload preservation time) Load growth threshold triggering runtime recalculation [% of declared load] default 10 (illustrative) (Capability profile) | Runtime calculation; Battery temperature records; Discharge test reports; Workload preservation timing evidence from CMP/STO; Recalculation records | ANALYSIS; REPERFORMANCE; TEST | 1) Reperform runtime calculation from current load and battery data. 2) Compare with generator start time and workload preservation time. 3) Review discharge test conditions and results. 4) Confirm recalculation after load increases. | PREVENTIVE | EFFECTIVENESS | AL5 | DESIGN; COMMISSION; OPERATE; CHANGE | NORMAL; EMERGENCY; MAINTENANCE | Applies to all UPS and BESS supporting critical load. | CG-05 |  | Runtime at end of life below generator start time; Battery room overheating reduces capacity; Load growth erodes runtime unnoticed (AIDCF-004 X01) | CapacityAssertion; TestRecord; InfrastructureSystem | Hazardous-energy activity. Tests and switching are performed only by authorised persons under the site electrical safety rules, an approved method statement and permit to work, with written authorisation from the facility owner's authorised engineer; assessors witness from outside the arc-flash boundary and never operate equipment. Discharge tests on live systems require confirmed redundancy and an abort criterion on minimum cell voltage. | If no discharge test exists within the interval, record a US4 UNKNOWN against CG-05; runtime claims are limited to calculation (DESIGN depth). | IEC 62040-3 (UPS performance); IEEE 485 / IEEE 1184 (battery sizing); IEEE 450 / IEEE 1188 | MCF-POW-010; MCF-POW-006; MCF-STO-017; MCF-CMP-010 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-POW-012 | POW | Electrical Power Infrastructure and Energy Continuity | POW-03 | UPS and energy storage | Bypass Exposure | Ensure that time spent with critical load on static or maintenance bypass, eco-mode or other unconditioned paths is known, minimised, authorised and accounted for in risk, because the load is then exposed directly to utility or generator disturbances. | The facility operator shall log every transfer of critical load to static bypass, maintenance bypass or eco-mode with start, end, cause and authorisation, shall alarm and escalate any unplanned bypass within the declared time, shall require approval for planned bypass and verify return to normal, and shall report cumulative bypass exposure per system at the declared interval. | 1) All bypass transfers in the period are logged with cause and authorisation, reconciled to UPS event logs. 2) Unplanned bypass alarms were escalated within the declared time. 3) Planned bypass had approval and a recorded return-to-normal verification. 4) Cumulative bypass exposure per system is reported and within the declared limit. 5) Eco-mode operation, if used, is evaluated against AI load dynamics and grid quality (MCF-POW-002). | Cumulative bypass exposure limit per UPS system [hours per year] default 24 (illustrative) (Capability profile) Unplanned bypass escalation time [minutes] default 15 (illustrative) (Capability profile) | UPS event logs; Bypass log; Approvals; Exposure reports; Eco-mode evaluation | RECONCILIATION; ANALYSIS | 1) Extract UPS event logs and reconcile to bypass log. 2) Check approvals and return-to-normal verification. 3) Compute cumulative exposure and compare with limit. | DETECTIVE | OPERATION | AL4 | OPERATE; CHANGE | NORMAL; MAINTENANCE; DEGRADED | Applies to all UPS systems with static or maintenance bypass. |  | CG-05; CG-09 | Bypass left active after maintenance; Unnoticed static bypass during generator operation; Eco-mode transfer fails during fast AI load swing | OperatingState; Event; FailureMode | Log review only; no bypass operation by or for the assessor. | If UPS event logs are unavailable for a system, record a U1 UNKNOWN; cumulative exposure for that system is UNKNOWN. | IEC 62040-3 (UPS performance); EN 50600-2-2 (power supply and distribution) | MCF-POW-009; MCF-POW-023; MCF-OPS-019 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-POW-013 | POW | Electrical Power Infrastructure and Energy Continuity | POW-04 | Distribution and protection | Switchgear Integrity | Ensure MV and LV switchgear, transformers and switchboards are maintained in a safe and serviceable condition and that arc-flash hazards are quantified, labelled, minimised and controlled for all persons working on or near them. | The electrical duty holder shall maintain a current arc-flash risk assessment (incident energy analysis) for all switchgear, switchboards, busway and PDUs, shall label equipment with incident energy or PPE category and boundaries, shall apply incident-energy reduction measures where assessed energy exceeds the declared threshold (for example maintenance switches, arc-flash relays, arc-resistant switchgear), and shall perform condition maintenance including infrared thermography, MV partial-discharge monitoring and breaker testing at the declared intervals. | 1) An arc-flash study exists for all equipment, reviewed within the declared interval and after changes to fault level or protection settings. 2) Equipment labels in a sample match the study. 3) Where incident energy exceeds the threshold, a reduction measure is installed and tested. 4) MV switchgear is arc-classified (IAC per IEC 62271-200) or has documented compensating controls. 5) Infrared thermography and MV partial-discharge results within the interval show no unresolved critical anomalies. 6) Breaker maintenance and trip testing are current per manufacturer and standard intervals. | Arc-flash study review interval [years] default 5 (NFPA 70E review requirement) Incident energy threshold requiring reduction measure [cal/cm²] default 8 (illustrative) (Capability profile; NFPA 70E / IEEE 1584 methodology) Infrared thermography interval [months] default 12 (illustrative) (NFPA 70B / capability profile) | Arc-flash study (IEEE 1584 method or equivalent); Label sample photographs; Incident-energy reduction test records; Switchgear IAC classification; Thermography and partial-discharge reports; Breaker test records | DOCUMENT_REVIEW; INSPECTION; SAMPLING; ANALYSIS | 1) Review study date, method, and inputs against current fault levels and settings. 2) Sample labels against the study. 3) Check high-energy locations for reduction measures and their tests. 4) Review thermography and partial-discharge findings and closure. 5) Review breaker maintenance records. | PREVENTIVE | OPERATION | AL4 | DESIGN; COMMISSION; OPERATE; CHANGE | NORMAL; MAINTENANCE | Applies to all electrical distribution equipment in the boundary operated or maintained by the assessed party; colocation tenants assess equipment within their suite. | CG-04 | CG-05 | Arc-flash injury due to outdated labels; Hot joint undetected leading to switchboard failure; MV cable termination partial discharge leading to flashover | Hazard; AssetInstance; Safeguard | Thermography is performed by authorised persons; where covers must be removed, energised-work justification and permit are required per NFPA 70E or national rules, or IR windows are used. Assessors do not open equipment. | If no arc-flash study exists or it predates a fault-level change, record a US4 UNKNOWN against CG-04; energised work on affected equipment is not authorised until resolved. | NFPA 70E (electrical safety in the workplace); IEEE 1584 (arc-flash hazard calculations); IEC 62271-200 (AC metal-enclosed switchgear); IEC 61439 (LV switchgear assemblies); NFPA 70B (electrical equipment maintenance) | MCF-POW-014; MCF-POW-023; MCF-POW-022 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-POW-014 | POW | Electrical Power Infrastructure and Energy Continuity | POW-04 | Distribution and protection | Selective Coordination | Ensure that protective devices are selective so that a fault is cleared by the device nearest to it, limiting loss of supply to the smallest fault domain, across utility, generator and UPS (inverter-limited) fault-current sources. | The electrical engineer of record shall maintain a short-circuit and protection coordination study covering every source configuration (utility, generator, UPS inverter, bypass) and the declared maintenance states, and shall demonstrate selectivity from the rack PDU branch up to the main incomers within the declared fault-current range. The facility operator shall ensure as-found protection settings match the study by periodic setting extraction and secondary injection testing. | 1) Short-circuit study covers all source configurations including inverter-limited fault current. 2) Coordination curves show selectivity between each upstream and downstream device pair for the declared range, or approved exceptions are listed. 3) Rack PDU and busway tap-off protection is selective with upstream devices for faults at the rack. 4) Extracted relay and trip-unit settings match the study for the sampled devices. 5) Secondary injection tests at the declared interval confirm trip characteristics. 6) Changes to settings since the last study are controlled under change management. | Protection setting extraction and comparison interval [months] default 24 (illustrative) (Capability profile) Permitted deviation of as-found settings from study [count] default 0 (illustrative) (Capability profile) | Short-circuit and coordination study; Coordination curves; Relay/trip unit setting exports; Secondary injection test reports; Change records for settings | DOCUMENT_REVIEW; RECONCILIATION; ANALYSIS; REPERFORMANCE | 1) Review study scope for all source configurations. 2) Check coordination curves for each critical device pair. 3) Compare extracted settings with study. 4) Review secondary injection results. 5) Review non-selective trip events in the period. | PREVENTIVE | IMPLEMENTATION | AL3 | DESIGN; COMMISSION; OPERATE; CHANGE | NORMAL; MAINTENANCE; EMERGENCY | Applies to all critical distribution. Partial applicability for colocation tenants: from the tenant's distribution boards downstream, with provider evidence upstream. | CG-09 | CG-05 | Rack fault trips upstream switchboard (AIDCF-004 protection miscoordination); Inverter-limited fault current fails to trip branch device; Setting drift after maintenance | FaultDomain; Safeguard; InfrastructureSystem | Hazardous-energy activity. Tests and switching are performed only by authorised persons under the site electrical safety rules, an approved method statement and permit to work, with written authorisation from the facility owner's authorised engineer; assessors witness from outside the arc-flash boundary and never operate equipment. Secondary injection requires isolation of trip outputs or an outage of the protected circuit. | If settings cannot be extracted or the study omits generator or UPS source configurations, record a US4 UNKNOWN against CG-09 for electrical fault containment. | IEC 60909 (short-circuit currents); IEC 60364 (LV electrical installations); IEEE 242 / IEEE 3004 series (protection and coordination); IEC 60947-2 (circuit-breakers) | MCF-POW-013; MCF-POW-015; MCF-RES-007; MCF-OPS-017 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-POW-015 | POW | Electrical Power Infrastructure and Energy Continuity | POW-04 | Distribution and protection | Busway and PDU Capacity | Ensure overhead busway, tap-off units, remote power panels and rack PDUs are rated for the continuous and peak load of dense AI racks, are balanced across phases, and keep capacity in failover states where one feed carries the full rack load. | The facility operator shall maintain a capacity register for every busway run, tap-off and rack PDU showing rating, continuous load limit, measured peak per phase and failover load (the load each feed must carry if its partner fails). The facility operator shall prevent provisioning that would cause failover load to exceed the continuous limit and shall correct phase imbalance above the declared threshold. | 1) The register covers every busway, tap-off and rack PDU serving AI racks. 2) Measured per-phase peak and calculated failover load are within the continuous load limit for every device. 3) Phase imbalance is below the declared threshold or a correction is scheduled. 4) Provisioning workflows check the register before new load is connected. 5) Busway joints are torque-checked or thermally surveyed at the declared interval. | Continuous load limit [% of device rating] default 80 (illustrative; for devices not rated for 100% continuous duty) (NFPA 70 / IEC 60364 continuous-load sizing conventions; device rating) Maximum phase imbalance at PDU/busway [%] default 10 (illustrative) (Capability profile) | Capacity register; EPMS per-phase peak data; Failover load calculations; Provisioning workflow evidence; Busway joint inspection records | ANALYSIS; RECONCILIATION; SAMPLING | 1) Extract per-phase peaks and pair A/B feeds. 2) Compute failover load and compare with continuous limit. 3) Check phase imbalance. 4) Sample provisioning records for register checks. | PREVENTIVE | OPERATION | AL4 | DESIGN; OPERATE; CHANGE | NORMAL; DEGRADED; MAINTENANCE | Applies to all critical distribution to AI racks. |  | CG-05; CG-14 | Failover overloads surviving PDU and trips rack; Phase imbalance overheats neutral; Loose busway joint fails under sustained high load | CapacityAssertion; AssetInstance; Interface | Data review only; joint inspections by authorised persons under permit. | If per-phase data is unavailable for a device class, record a U1 UNKNOWN and limit the claim to devices with data. | IEC 61439-6 (busbar trunking systems); IEC 60364 (LV installations); EN 50600-2-2 | MCF-POW-014; MCF-POW-021; MCF-CMP-003; MCF-OPS-021 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-POW-016 | POW | Electrical Power Infrastructure and Energy Continuity | POW-04 | Distribution and protection | Earthing and Bonding | Ensure that earthing, equipotential bonding and lightning protection protect people against electric shock, provide fault-current return for protective devices and limit noise and transient damage to IT equipment, including metallic liquid-cooling pipework. | The electrical engineer of record shall design the earthing system (system earthing type, earth electrodes, main earthing terminal, supplementary bonding) and the facility operator shall verify it by initial and periodic inspection and testing, including earth electrode resistance, protective conductor continuity, earth fault loop impedance and bonding of liquid-cooling pipework, manifolds, raised floors and cable containment. | 1) Earthing design documents the system earthing type and bonding scheme for each building. 2) Periodic inspection and test records within the interval show earth electrode resistance, continuity and fault loop impedance within design values. 3) Liquid-cooling pipework, manifolds and CDUs are bonded, verified in a sample. 4) Bonding between generator, transformer and building earthing is verified. 5) Defects are corrected before the circuit is returned to service or within the declared period. | Periodic inspection and test interval [years] default 5 (illustrative) (IEC 60364-6 / national wiring regulations; capability profile) | Earthing design; Periodic inspection and test reports; Bonding sample records; Defect records | DOCUMENT_REVIEW; INSPECTION; SAMPLING | 1) Review design and periodic test reports. 2) Inspect bonding of a sample of liquid-cooling and containment elements. 3) Check defect closure. | PREVENTIVE | IMPLEMENTATION | AL3 | DESIGN; BUILD; COMMISSION; OPERATE | NORMAL; MAINTENANCE | Applies to all electrical installations in the boundary. | CG-04 | CG-05 | Touch voltage on unbonded coolant manifold; High earth fault loop impedance prevents disconnection; Lightning surge damages IT through poor bonding | Safeguard; Hazard; InfrastructureSystem | Hazardous-energy activity. Tests and switching are performed only by authorised persons under the site electrical safety rules, an approved method statement and permit to work, with written authorisation from the facility owner's authorised engineer; assessors witness from outside the arc-flash boundary and never operate equipment. Earth electrode testing near energised substations follows the network operator's rules. | If no periodic inspection report is current, record a US4 UNKNOWN against CG-04 for shock protection. | IEC 60364 series (LV electrical installations); IEC 62305 series (lightning protection); IEEE 1100 (powering and grounding electronic equipment); EN 50310 (bonding in buildings with IT equipment) | MCF-POW-013; MCF-PHY-011; MCF-THM-011 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-POW-017 | POW | Electrical Power Infrastructure and Energy Continuity | POW-05 | Power quality and transient response | Voltage Quality | Ensure voltage delivered to critical IT and cooling loads stays within equipment tolerance in all source configurations, including on generator and during load swings from AI clusters. | The facility operator shall monitor voltage magnitude, unbalance and short-duration variations at UPS outputs, critical switchboards and a representative sample of rack PDUs, shall compare results with the tolerance of connected equipment (power supply unit specifications and the ITIC/CBEMA or SEMI F47 curves where adopted), and shall investigate excursions. | 1) Voltage monitoring exists at UPS outputs, critical switchboards and sampled rack PDUs. 2) Excursions outside the declared envelope are logged and investigated. 3) Voltage on generator operation was recorded during a test and within envelope. 4) Unbalance at critical boards is within the declared limit. | Steady-state voltage envelope at critical boards [% of nominal] default ±5 (illustrative) (Equipment PSU specifications; capability profile) Voltage unbalance limit [%] default 2 (illustrative) (EN 50160 / IEC 61000-2 compatibility levels) | Monitoring point list; Voltage statistics and excursion log; Generator-test voltage records; Investigation records | ANALYSIS; INSPECTION | 1) Confirm monitoring points. 2) Analyse statistics and excursions. 3) Review generator-test voltage records. | DETECTIVE | OPERATION | AL4 | COMMISSION; OPERATE | NORMAL; EMERGENCY; DEGRADED | Applies to all critical distribution. |  | CG-05 | Undervoltage on generator during AI ramp; Unbalance causing PSU derating | Resource; Event | Data review via EPMS. | If no monitoring exists at rack level, record a U5 UNKNOWN for rack-level voltage quality. | IEC 61000-2 series (compatibility levels); EN 50160; ITIC (CBEMA) curve application note; SEMI F47 (voltage sag immunity) | MCF-POW-002; MCF-POW-019; MCF-POW-021 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-POW-018 | POW | Electrical Power Infrastructure and Energy Continuity | POW-05 | Power quality and transient response | Harmonics | Ensure harmonic distortion from rectifier-based IT loads, UPS, VFDs and BESS inverters is within limits at the point of common coupling and internally, does not overheat transformers, neutrals or generators, and does not cause resonance with filters or power-factor correction. | The electrical engineer shall perform a harmonic study for the declared load mix covering utility and generator source configurations, and the facility operator shall measure voltage and current harmonics at the PCC and at critical boards. The facility owner shall keep harmonic emissions at the PCC within the limits of the connection agreement (for example IEEE 519 or the applicable IEC 61000-3 limits) and shall derate or specify transformers and generators for measured harmonic content. | 1) A harmonic study covers utility and generator configurations and capacitive or filter elements. 2) Measured voltage THD and current TDD at the PCC are within the applicable limits. 3) Transformer and generator ratings account for measured harmonic content (K-factor or derating). 4) Leading power factor from IT PSUs and filters at light load is evaluated against generator capability. 5) Neutral currents in 4-wire systems are measured and within conductor rating. | Voltage THD limit at PCC, 1 kV < V ≤ 69 kV [%] default 5 (IEEE 519 voltage distortion limits) Voltage THD limit at PCC, V ≤ 1 kV [%] default 8 (IEEE 519 voltage distortion limits) | Harmonic study; PCC harmonic measurements; Transformer and generator derating evidence; Neutral current measurements; Generator capability chart vs leading PF | DOCUMENT_REVIEW; ANALYSIS | 1) Review study scope and assumptions vs current load. 2) Compare PCC measurements with limits. 3) Check derating and leading-PF evaluation. 4) Review neutral currents. | PREVENTIVE | OPERATION | AL4 | DESIGN; COMMISSION; OPERATE | NORMAL; EMERGENCY | Applies to all sites; leading-PF element applies to generator-backed sites. |  | CG-05 | Generator AVR instability from leading PF at light load; Filter resonance amplifies harmonics; Transformer overheating | Resource; Hazard; InfrastructureSystem | Measurements via installed meters; portable instruments installed only by authorised persons under permit. | If generator-supplied harmonic and PF behaviour is unmeasured, record a U5 UNKNOWN and refer to MCF-POW-020. | IEEE 519 (harmonic control); IEC 61000-3 series (emission limits); IEC 61000-4-7 (harmonic measurement); ISO 8528 series | MCF-POW-002; MCF-POW-020; MCF-POW-005 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-POW-019 | POW | Electrical Power Infrastructure and Energy Continuity | POW-05 | Power quality and transient response | Transient Ride-Through | Demonstrate that critical IT, cooling and control loads ride through grid voltage dips, transfers between sources and switching transients without loss of service, and that the facility meets any fault ride-through obligations of its grid connection. | The electrical engineer shall define the ride-through envelope for each load class (IT, CDU and pump drives, chillers, controls), including source transfers (UPS to bypass, static transfer switch, ATS, generator synchronisation) and grid dips. The facility owner shall verify by commissioning and periodic transfer tests that loads remain online for transfers within the envelope, shall ensure mechanical loads not on UPS restart automatically within the thermal time constant, and shall document compliance with connection-agreement ride-through requirements. | 1) A ride-through envelope is documented for each load class, including STS and ATS transfer times. 2) Transfer tests demonstrate IT and UPS-backed cooling loads remained online. 3) Non-UPS cooling drives and chillers restart automatically within the thermal ride-through time established by THM controls, demonstrated in test. 4) Control systems (BMS, EPMS, CDU controllers) are UPS-backed and remain operational through transfers. 5) Grid-code ride-through obligations for the site as a large load are identified and evidence of compliance exists. 6) Real dip events in the period caused no unexpected load loss, or loss was investigated. | Static transfer switch transfer time [ms] default 4 (illustrative; within PSU hold-up) (STS OEM data; PSU hold-up specification) Maximum restart time for non-UPS cooling plant [s] default per thermal ride-through analysis (THM) (Thermal design basis) | Ride-through envelope; Transfer test reports with waveform captures; Restart test records; Control system power supply schematic; Grid-code compliance evidence; Dip event analysis | DOCUMENT_REVIEW; TEST; ANALYSIS | 1) Review envelope for completeness by load class. 2) Review transfer test waveforms and load continuity. 3) Review restart tests for non-UPS cooling against thermal ride-through time. 4) Check control system power supply. 5) Analyse real dip events. | PREVENTIVE | EFFECTIVENESS | AL5 | DESIGN; COMMISSION; OPERATE; CHANGE | NORMAL; TRANSITION; EMERGENCY; RECOVERY | Applies to all critical loads; grid-code element applies where the connection agreement contains ride-through obligations. | CG-05 | CG-06 | Chillers trip on dip and fail to restart (AIDCF-004 X02); STS transfer exceeds PSU hold-up; CDU controller reboots during transfer; Site trips off grid during fault, breaching obligations | Safeguard; TestRecord; OperatingState; FailureScenario | Hazardous-energy activity. Tests and switching are performed only by authorised persons under the site electrical safety rules, an approved method statement and permit to work, with written authorisation from the facility owner's authorised engineer; assessors witness from outside the arc-flash boundary and never operate equipment. Transfer tests on live critical load require confirmed healthy redundancy, an approved test window, thermal contingency, and abort criteria. | If transfer tests have never been performed with representative load, record a US4 UNKNOWN against CG-05; THM restart dependency is referred to CG-06. | IEC 62040-3 (UPS performance, output dynamic performance classification); SEMI F47 (voltage sag immunity); EU Network Code on Demand Connection; NFPA 110 | MCF-POW-017; MCF-POW-020; MCF-THM-024; MCF-THM-021 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-POW-020 | POW | Electrical Power Infrastructure and Energy Continuity | POW-05 | Power quality and transient response | Load-Step Response | Demonstrate that UPS, BESS, generators and the grid connection remain stable under the load steps and synchronous power oscillations produced by large accelerator clusters (collective compute/communication phases, job start and stop, checkpoint pauses and failure-driven drops), and that these dynamics are bounded within the capability of every source. | The facility owner shall characterise the power dynamics of each AI cluster (step magnitude, ramp rate, oscillation amplitude and frequency band), using measured data at sub-second resolution or the accelerator vendor's specified behaviour, and shall verify that UPS rectifier and inverter controls, BESS, generator governors and voltage regulators, and the grid connection tolerate them without instability, protective trips or breach of connection limits. Where they do not, the facility owner shall apply mitigation (accelerator power-smoothing or ramp-limit features, workload scheduling, energy-storage buffering) and shall verify it by test, including a load-step test on generator supply. | 1) Cluster power dynamics are characterised with step size, ramp rate and oscillation band, from measured data at sub-second resolution or vendor specification. 2) Generator load-acceptance capability (ISO 8528-5 performance class or test data) covers the characterised steps with frequency and voltage deviation within declared limits. 3) UPS and BESS behaviour under characterised oscillation is verified (no rectifier walk-in conflict, battery cycling within design, no transfer to bypass). 4) Grid-connection ramp and oscillation obligations are identified and measured behaviour at the PCC is within them. 5) A load-step or oscillation test on generator supply, using load banks programmed to the characterised profile or the cluster itself, shows stable operation. 6) Mitigations in use (power smoothing, ramp limits) are configured, under change control and monitored. | Maximum cluster power swing amplitude [% of cluster IT load] default 50 (illustrative) (Measured cluster data or accelerator vendor specification) Power oscillation frequency band of concern [Hz] default 0.1 to 20 (illustrative) (Cluster characterisation; generator and grid modal analysis) Maximum single load step on generator supply [% of generator rating] default per ISO 8528-5 class and test data (illustrative: 50) (ISO 8528-5 load acceptance performance classes) Measurement resolution for AI load dynamics [ms] default 100 or finer (illustrative) (Capability profile) | Cluster power-dynamics characterisation report; High-resolution power measurements at cluster and PCC; Generator load-acceptance data or test; UPS/BESS dynamic test records; Grid-connection obligation analysis; Mitigation configuration exports | ANALYSIS; TEST; DOCUMENT_REVIEW; RECONCILIATION | 1) Obtain characterisation and verify data resolution and coverage of job phases. 2) Compare characterised dynamics with generator, UPS and BESS capability. 3) Review grid-connection obligations against PCC measurements. 4) Review or witness the load-step or oscillation test on generator. 5) Verify mitigation configuration and change control. | PREVENTIVE | EFFECTIVENESS | AL5 | DESIGN; COMMISSION; OPERATE; CHANGE | NORMAL; EMERGENCY; TRANSITION | Applies to sites hosting synchronous training or large inference clusters whose aggregate power can change by more than a declared fraction of site load within seconds. Not applicable to sites where AI load is a small fraction of source capacity, recorded with the calculation. | CG-05 | CG-03 | Generator governor hunting under periodic training load; UPS transfers to bypass under swing; Forced oscillation at PCC breaches grid obligations; Synchronous job drop causes overfrequency on generator | Resource; CapacityAssertion; TestRecord; FailureScenario | Hazardous-energy activity. Tests and switching are performed only by authorised persons under the site electrical safety rules, an approved method statement and permit to work, with written authorisation from the facility owner's authorised engineer; assessors witness from outside the arc-flash boundary and never operate equipment. Tests on generator with real cluster load require approval from the capability owner, a checkpointed workload, and abort criteria on frequency and voltage; programmable load-bank tests are preferred. | If cluster dynamics are uncharacterised for a site where the applicability threshold is met, record a US4 UNKNOWN against CG-05; generator and UPS adequacy claims are limited to static load. | ISO 8528-5 (generating set load acceptance); IEC 62040-3 (UPS dynamic performance); Network operator large-load connection requirements of the jurisdiction; IEEE 2800 (inverter-based resource interconnection; for grid-forming BESS behaviour) | MCF-POW-005; MCF-POW-009; MCF-POW-001; MCF-CAP-014; MCF-CMP-017 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-POW-021 | POW | Electrical Power Infrastructure and Energy Continuity | POW-06 | Electrical monitoring, maintenance and recovery | EPMS Coverage | Ensure the electrical power monitoring system observes every critical node with accurate, time-synchronised data and alarms, functions independently of the systems it monitors, and is configured and protected as a critical control system. | The facility operator shall instrument every utility incomer, generator, UPS, STS, critical switchboard, busway and representative rack PDU with metering connected to the EPMS, shall synchronise device clocks to the declared accuracy for sequence-of-events analysis, shall configure alarms per an approved alarm philosophy, and shall power the EPMS and its network from protected supplies. The facility operator shall maintain the EPMS configuration under change control and its access under SEC controls. | 1) A point list reconciles EPMS devices to the as-built single-line diagram with no unmonitored critical node. 2) Clock synchronisation accuracy meets the declared value, demonstrated by sequence-of-events data. 3) Alarm configuration matches the alarm philosophy and critical alarms reach a staffed location. 4) EPMS servers, network and gateways are on UPS-backed supplies and remain available through transfers. 5) EPMS configuration and firmware are baselined and changes are controlled. 6) Data gaps in the period are below the declared threshold and are investigated. | Critical-node metering coverage [% of critical nodes] default 100 (illustrative) (Capability profile) Clock synchronisation accuracy for sequence of events [ms] default 1 (illustrative) (Capability profile; IEC 61850 time-sync practice) Maximum EPMS data gap per point [% of period] default 1 (illustrative) (Capability profile) | EPMS point list; As-built single-line diagram reconciliation; Sequence-of-events records; Alarm philosophy and configuration export; EPMS power and network schematic; Configuration baseline and change records; Data completeness report | RECONCILIATION; INSPECTION; ANALYSIS; TEST | 1) Reconcile EPMS point list to the single-line diagram. 2) Review sequence-of-events timing from a recent event. 3) Compare alarm configuration with philosophy and test a critical alarm path. 4) Review EPMS power and network resilience. 5) Review configuration baseline and change records. | DETECTIVE | IMPLEMENTATION | AL3 | DESIGN; COMMISSION; OPERATE; CHANGE | NORMAL; DEGRADED; MAINTENANCE; EMERGENCY; RECOVERY; TRANSITION | Applies to all sites with critical electrical infrastructure; colocation tenants assess provider EPMS data access and coverage of their feeds. | CG-07 | CG-05; CG-15 | Unmonitored switchboard hides overload; Clock drift prevents fault reconstruction; EPMS lost during transfer when needed most; Unauthorised EPMS configuration change | InfrastructureSystem; Safeguard; EvidenceObject; Interface | Alarm path tests use simulation or test points authorised by the facility operator; no protective device is operated. | If the point list cannot be reconciled to the single-line diagram, record a US4 UNKNOWN against CG-07; EPMS-derived evidence for other POW controls is downgraded to T2 until resolved. | IEC 61850 (communication for power utility automation); IEC 62443 series (industrial automation and control system security); EN 50600-2-6 (management and operational information); ISA-18.2 / IEC 62682 (alarm management) | MCF-SEC-005; MCF-OPS-013; MCF-POW-015; MCF-POW-024 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-POW-022 | POW | Electrical Power Infrastructure and Energy Continuity | POW-06 | Electrical monitoring, maintenance and recovery | Preventive Maintenance | Ensure electrical assets are maintained at intervals and to scopes that keep their reliability and safety within the assumptions of the design and resilience analysis, without maintenance itself introducing unmanaged risk. | The facility operator shall maintain a maintenance programme for each electrical asset class (switchgear, transformers, UPS, batteries, generators, ATS/STS, busway, PDUs, protection relays) with scopes and intervals based on manufacturer requirements and recognised maintenance practice, shall complete maintenance on time, and shall record deferrals with risk assessment and approval. | 1) Every critical electrical asset is in the maintenance system with scope and interval. 2) On-time completion in the period meets the declared percentage. 3) No critical maintenance is overdue beyond the declared tolerance without an approved deferral. 4) Deferrals have risk assessment and approval by the accountable engineer. 5) Findings from maintenance are tracked to closure. | On-time completion of critical electrical maintenance [%] default 95 (illustrative) (Capability profile) Maximum overdue period without approved deferral [days] default 30 (illustrative) (Capability profile) | Maintenance programme; Work order history; Deferral approvals; Findings tracking | RECONCILIATION; ANALYSIS; SAMPLING | 1) Reconcile asset register to maintenance programme. 2) Compute on-time completion. 3) Review overdue items and deferrals. 4) Sample findings to closure. | PREVENTIVE | OPERATION | AL4 | OPERATE | NORMAL; MAINTENANCE | Applies to all electrical assets operated or maintained by the assessed party. |  | CG-05 | Breaker fails to trip after missed maintenance; Deferred battery replacement; Maintenance-induced failure without method statement | AssetInstance; Safeguard; Action | Records review; observation of maintenance only from outside the work area. | If the maintenance system does not cover all critical assets, record a U5 UNKNOWN for uncovered assets. | NFPA 70B (electrical equipment maintenance); EN 50600-2-2; IEC 60300 (dependability management) | MCF-OPS-009; MCF-OPS-012; MCF-POW-013; MCF-POW-010 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-POW-023 | POW | Electrical Power Infrastructure and Energy Continuity | POW-06 | Electrical monitoring, maintenance and recovery | Switching Procedures | Ensure that every planned and emergency switching operation on critical distribution is performed to an approved, verified procedure by authorised persons, with hazardous energy controlled, so that switching neither injures people nor drops critical load. | The electrical duty holder shall require a method of procedure (MOP) for every planned switching operation on critical distribution, prepared from the current single-line diagram, checked by a second authorised person, and executed with step verification. The electrical duty holder shall maintain emergency operating procedures for foreseeable failures, shall apply lockout/tagout and permit-to-work for isolation, and shall authorise persons for switching by competence assessment. | 1) Every sampled planned switching operation has an approved MOP checked by a second authorised person. 2) MOP steps reference current single-line diagram revision and include hold points and rollback. 3) Emergency operating procedures exist for each failure in the UPS failure analysis (MCF-POW-009). 4) Isolations in the sample applied lockout/tagout with permit-to-work and test-before-touch. 5) Persons performing switching hold current authorisation for the voltage level and equipment. 6) Switching incidents in the period were investigated. | Planned critical switching with approved, peer-checked MOP [%] default 100 (illustrative) (Capability profile) | MOP sample; Emergency operating procedures; Permits and LOTO records; Authorisation register; Switching incident records | SAMPLING; DOCUMENT_REVIEW; OBSERVATION | 1) Sample planned switching operations. 2) Check MOP preparation, peer check and SLD revision. 3) Review EOP coverage against failure analysis. 4) Check permits, LOTO and authorisations. 5) Observe a switching operation where scheduled, from a safe position. | PREVENTIVE | OPERATION | AL4 | OPERATE; CHANGE | MAINTENANCE; EMERGENCY; TRANSITION; RECOVERY | Applies to all switching on critical distribution by the assessed party or its contractors. | CG-04 | CG-07; CG-14 | Wrong breaker opened drops live path; Backfeed from generator during isolation; Unauthorised person switches MV; MOP based on outdated drawing (AIDCF-004 X04) | Safeguard; Hazard; AssessmentProcedure; Action | Hazardous-energy activity. Tests and switching are performed only by authorised persons under the site electrical safety rules, an approved method statement and permit to work, with written authorisation from the facility owner's authorised engineer; assessors witness from outside the arc-flash boundary and never operate equipment. | If LOTO and permit records for sampled isolations cannot be produced, record a US4 UNKNOWN against CG-04. | NFPA 70E (electrical safety in the workplace); EN 50110 (operation of electrical installations); ISO 45001 (occupational health and safety) | MCF-OPS-008; MCF-OPS-007; MCF-OPS-006; MCF-POW-012 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-POW-024 | POW | Electrical Power Infrastructure and Energy Continuity | POW-06 | Electrical monitoring, maintenance and recovery | Black-Start and Restoration | Demonstrate that after a total loss of power the site can be restored from a dead state, in a safe and dependency-correct sequence (controls, cooling, then IT), within the declared recovery time, and that AI workloads can resume. | The facility owner shall maintain a black-start and restoration plan that defines the restoration sequence, the dependencies of each step (control power, EPMS/BMS availability, cooling restart, battery recharge limits, inrush and staged load pick-up on generator), the authority to proceed, and the hand-over to IT for workload restart. The facility owner shall exercise the plan at the declared interval, either by a full integrated test or by staged tests that together cover every step, and shall measure time to each milestone. | 1) A restoration sequence exists covering control power, EPMS/BMS, cooling, battery recharge and IT pick-up with dependencies. 2) Generator staged load pick-up respects load-acceptance limits including cooling motor inrush and IT power-on surge. 3) Restoration was exercised within the interval and measured milestones met declared times. 4) Manual operation is possible if EPMS/BMS is unavailable, with procedures and trained staff. 5) Hand-over criteria to IT and workload restart dependencies (storage, network, scheduler) are defined. | Restoration time from dead site to full critical load [hours] default 4 (illustrative) (Capability profile; recovery outcome) Black-start exercise interval [months] default 12 (illustrative) (Capability profile) | Restoration plan; Exercise or IST reports with milestone times; Manual operation procedures; Training records; Hand-over criteria | DOCUMENT_REVIEW; SCENARIO_EXERCISE; TEST; ANALYSIS | 1) Review sequence for dependency correctness. 2) Check staged pick-up against generator load acceptance. 3) Review exercise milestone times against declared values. 4) Verify manual operation procedures and training. 5) Check hand-over criteria with CMP/STO/NET restart dependencies. | RECOVERY | RESILIENCE | AL5 | COMMISSION; OPERATE; CHANGE | FAILED; RECOVERY; SHUTDOWN | Applies to all sites hosting critical AI capability. Colocation tenants assess the provider's plan and their own IT restart dependencies. | CG-10 | CG-05; CG-07 | Restoration blocked because BMS needs power it controls; Generator trips on simultaneous chiller restart; IT restarted before cooling stable; Battery recharge overloads generators | FailureScenario; Safeguard; TestRecord; Dependency | Black-start exercises are among the most hazardous tests: they require an approved test plan, written authorisation by the facility owner and capability owner, workloads drained or checkpointed, emergency services informed where required, and abort criteria. Staged tests are preferred where a full dead-site test is not authorised. | If restoration has never been exercised, record a US4 UNKNOWN against CG-10; the plan supports design only, not recoverability. | ISO 22301 (business continuity); NFPA 110; EN 50600-2-2 | MCF-RES-014; MCF-THM-024; MCF-STO-018; MCF-POW-021 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-THM-001 | THM | Cooling, Thermal and Fluid Infrastructure | THM-01 | Thermal architecture and capacity | Heat-Load Model | Establish an authoritative, versioned model of the heat that each fault domain must reject, split by heat-removal path (air, direct-to-chip liquid, rear-door, immersion), so that every downstream capacity, redundancy and recovery claim is tested against a defensible demand figure rather than nameplate or average IT power. | The thermal engineering authority shall maintain a versioned heat-load model for each Capability Instance that states, per hall, row, rack group and CDU or air-handling fault domain, the design and peak heat load in kW, the liquid-capture ratio by platform, residual heat to air, and the transient load profile of synchronous AI training. The facility owner shall approve the model and shall not accept capacity claims that are not traceable to the current model version. | 1) The model exists as a controlled, versioned document or dataset with a named owner and approval record dated within the review interval. 2) Heat load is apportioned to each fault domain (hall, row, rack group, CDU loop, CRAH zone) and the sum reconciles to the IT power model within the stated tolerance. 3) For each liquid-cooled platform, the liquid-capture ratio and residual air-side heat are taken from OEM thermal data or measurement and the source is cited. 4) The model includes a synchronous-load transient profile (step change and ramp rate) for training workloads, not only steady-state averages. 5) Non-IT heat (power conversion losses, lighting, envelope gain, CDU pump heat) is included or explicitly excluded with rationale. 6) Planned densification and the next approved deployment phase are represented as named scenarios. | Rack design heat load (liquid-cooled AI rack) [kW per rack] default 120 (illustrative) (Platform OEM thermal design data; site-specific) Liquid-capture ratio (direct-to-chip platform) [% of rack heat to liquid] default 80 (illustrative) (OEM thermal data or measured; varies by platform generation) Synchronous load step [% of fault-domain design load within 1 s] default 50 (illustrative) (Workload characterisation of synchronous training; to be measured) Model-to-measured reconciliation tolerance [% of measured heat load] default ±10 (illustrative) (Capability profile) | Current heat-load model with version, owner and approval signature; IT power model or rack power budget the heat-load model is reconciled to; OEM thermal design guides or datasheets for each deployed accelerator platform; Fault-domain allocation table (rack → CDU loop → CRAH zone → chilled-water or facility-water branch); Comparison of model against measured heat load for at least one operating hall where available | DOCUMENT_REVIEW; ANALYSIS; RECONCILIATION; INQUIRY | 1) Obtain the current model and confirm version, owner and approval. 2) Trace three sampled rack groups from OEM thermal data through the model to the fault-domain totals. 3) Reconcile total modelled heat to the IT power budget and to metered data where available. 4) Check that transient load and densification scenarios are represented. 5) Record deviations beyond tolerance as Findings and unresolved inputs as UNKNOWN Records. | DIRECTIVE | DESIGN | AL2 | PLAN; DESIGN; CHANGE | NORMAL; TRANSITION | Applies to every Capability Instance with in-scope heat-removal infrastructure. Not applicable only where the thermal infrastructure is wholly outside the assessment boundary and that exclusion is approved under CG-02. |  | CG-06; CG-01 | Capacity sized to average rather than peak synchronous load; Liquid-capture ratio overstated so residual air heat exceeds air-side capacity; Heat load not apportioned to fault domains, hiding local overload; Stale model after densification | CapacityAssertion; InfrastructureSystem; FaultDomain; ArchitectureSnapshot | Desk-based; no intrusive testing. Any metering added to validate the model is installed under the site change process. | If the liquid-capture ratio or transient profile for a deployed platform cannot be sourced, record a U1 UNKNOWN against this control and carry it to every capacity control that depends on that platform. | ASHRAE TC 9.9 Thermal Guidelines for Data Processing Environments; ASHRAE TC 9.9 Liquid Cooling Guidelines for Datacom Equipment Centers; AIDCF-013 (AI Data Centre Assurance Reference Architecture); ASHRAE Standard 90.4 (energy standard for data centres) | MCF-THM-002; MCF-THM-003; MCF-CAP-013; MCF-CAP-014 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-THM-002 | THM | Cooling, Thermal and Fluid Infrastructure | THM-01 | Thermal architecture and capacity | Design Capacity | Demonstrate that the installed and commissioned capacity of every stage of the heat-removal path (air, TCS, CDU, FWS, heat rejection) meets the current heat-load model at design conditions, so that the facility can actually remove the heat it is declared to support. | The thermal engineering authority shall demonstrate, for each heat-removal stage and fault domain, that commissioned capacity at design ambient and design supply temperatures is not less than the design heat load from MCF-THM-001 plus the approved margin. The facility operator shall hold the commissioning records and shall not admit IT load beyond the demonstrated capacity of the weakest stage in the path. | 1) A stage-by-stage capacity table exists (CRAH/fan wall, rear-door, CDU, TCS pumps, FWS pumps, chillers, dry coolers or towers) with rated and commissioned capacity at stated conditions. 2) The weakest stage in each path is identified and its commissioned capacity is ≥ design load plus margin. 3) Commissioning (functional and integrated systems tests) was performed at or extrapolated with documented method to design load using load banks or equivalent. 4) Capacity ratings are stated at the actual design supply temperature and ΔT, not catalogue nominal conditions. 5) Admitted IT load is reconciled to the demonstrated capacity and no fault domain exceeds it. | Design capacity margin above design heat load [%] default 10 (illustrative) (Capability profile; design authority) Commissioning load-bank test level [% of design heat load] default 100 (illustrative) (ASHRAE Guideline 0 practice; site commissioning plan) | Stage-by-stage capacity table with rated and commissioned figures; Integrated systems test (IST) or Level 5 commissioning report with load-bank data; Equipment performance data at design conditions; Current admitted-load register per fault domain | DOCUMENT_REVIEW; RECONCILIATION; ANALYSIS; INSPECTION | 1) Obtain the capacity table and commissioning reports for the sampled fault domains. 2) Verify test conditions (ambient, supply temperature, load level) against design conditions. 3) Identify the weakest stage in each path and compare with the heat-load model. 4) Reconcile admitted IT load per fault domain with demonstrated capacity. 5) Inspect nameplates of a sample of units against the capacity table. | PREVENTIVE | IMPLEMENTATION | AL3 | DESIGN; BUILD; COMMISSION; CHANGE | NORMAL; TRANSITION | Applies to all in-scope heat-removal stages. For colocation where the operator provides cooling as a service, applies to the provider-supplied evidence under the service interface. | CG-06 | CG-02 | Catalogue capacity assumed at non-design conditions; Weakest stage (often CDU or FWS pumps) unidentified; Load admitted above demonstrated capacity; Commissioning performed at partial load without valid extrapolation | CapacityAssertion; InfrastructureSystem; AssetInstance; TestRecord | Load-bank testing involves hazardous energy and high-temperature exhaust; it requires an approved commissioning plan, permit-to-work and the site authorising engineer's authority. Assessors observe or review; they do not operate plant. | If commissioning at design load cannot be evidenced for any stage, record UNKNOWN (U1 or U5) for that fault domain; the result cannot be CONFORMING on rated data alone. | ASHRAE Guideline 0 (the commissioning process); ASHRAE TC 9.9 Thermal Guidelines for Data Processing Environments; ASHRAE TC 9.9 Liquid Cooling Guidelines for Datacom Equipment Centers; Uptime Institute Tier Standard: Topology; ANSI/TIA-942 (telecommunications infrastructure standard for data centres) | MCF-THM-001; MCF-THM-003; MCF-THM-010; MCF-THM-013 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-THM-003 | THM | Cooling, Thermal and Fluid Infrastructure | THM-01 | Thermal architecture and capacity | Resilient Capacity | Ensure heat removal remains within the IT inlet and coolant envelopes when any single credible component, path or controller is lost, during maintenance, and through power-event transients (utility loss, UPS transfer, generator start, chiller restart). | The thermal engineering authority shall define the declared redundancy (for example N+1, 2N) for each heat-removal stage and shall demonstrate that, with the largest single unit or path out of service, capacity meets design load. The facility owner shall demonstrate thermal ride-through: that pumps, CDUs and controls needed to keep coolant moving are on continuous power, and that thermal storage or ride-through margin keeps TCS supply and IT inlet temperatures within limits until chillers or heat rejection restart. | 1) Declared redundancy per stage is documented and the N−1 capacity analysis shows design load is met with the largest unit lost. 2) Common-mode elements that defeat redundancy (shared header, single controller, common power board, single make-up water feed) are identified with treatment. 3) TCS and CDU pumps and their controls are supplied from UPS or equivalent continuous power, verified on the single-line diagram. 4) A ride-through analysis or test shows TCS supply temperature and IT inlet temperature stay within declared limits from loss of mechanical cooling until restart to capacity. 5) An integrated test (utility loss / generator transfer) recorded coolant temperature, flow and IT throttling during the transient. 6) Redundancy is maintained, or a documented risk acceptance applies, during planned maintenance of each stage. | Declared redundancy for CDU stage [configuration] default N+1 (illustrative) (Capability profile) Chiller restart-to-capacity time after power interruption [s] default 300 (illustrative) (Manufacturer rapid-restart data; verify by test) Thermal ride-through required [s] default 600 (illustrative) (Derived: restart time plus margin; capability profile) Maximum TCS supply temperature rise during transient [K] default 5 (illustrative) (OEM coolant inlet limit minus normal setpoint) | N−1 capacity analysis per stage; Single-line diagram extract showing pump/CDU/control power sources; Ride-through calculation including thermal-storage volume and pipework thermal mass; IST or black-building test record with time-stamped coolant temperature and flow traces; Maintenance-state redundancy matrix | ANALYSIS; DOCUMENT_REVIEW; TEST; SCENARIO_EXERCISE; RECONCILIATION | 1) Review the redundancy declaration and N−1 analysis for each stage. 2) Trace pump, CDU and controller power to UPS on the single-line diagram. 3) Review the ride-through calculation inputs (volume, ΔT, load) against current heat load. 4) Examine transient test traces for TCS supply temperature, flow and IT throttling events. 5) Compare maintenance-state redundancy matrix with the maintenance schedule. 6) Record common-mode elements without treatment as Findings. | PREVENTIVE | RESILIENCE | AL5 | DESIGN; COMMISSION; OPERATE; CHANGE | NORMAL; DEGRADED; MAINTENANCE; EMERGENCY; TRANSITION; RECOVERY | Applies wherever a Service Outcome requires continuity of heat removal through component loss or power events. A reduced scope applies where the outcome tolerates controlled shutdown, provided that tolerance is approved under CG-01. | CG-06 | CG-09; CG-05 | Redundancy defeated by shared header or controller; CDU or TCS pumps not on UPS, stopping coolant flow on utility loss; Chiller restart longer than ride-through, causing thermal trip; Redundancy lost during maintenance without compensating measure | FaultDomain; CapacityAssertion; FailureScenario; Safeguard; TestRecord | Utility-loss and transfer tests are hazardous and capability-affecting. Requires a permit-to-work and method statement approved by the site authorising engineer, the IT operator's agreement on load at risk, and a rollback plan. Prefer analysis and records of previous tests over new disruptive tests. | If no transient test or calibrated simulation exists for the current load, record a U5 coverage-gap UNKNOWN; CONFORMING requires transient evidence, not steady-state capacity alone. | Uptime Institute Tier Standard: Topology; ASHRAE TC 9.9 Thermal Guidelines for Data Processing Environments; ASHRAE TC 9.9 Liquid Cooling Guidelines for Datacom Equipment Centers; EN 50600-2-3 / ISO/IEC 22237-3 (data centre environmental control); ASHRAE Guideline 0 (the commissioning process); AIDCF-004 (Threat, Hazard and Failure Model) | MCF-THM-002; MCF-THM-024; MCF-POW-009; MCF-POW-019; MCF-DEP-005 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-THM-004 | THM | Cooling, Thermal and Fluid Infrastructure | THM-01 | Thermal architecture and capacity | Seasonal Derating | Ensure heat-rejection and economiser capacity is rated at the site's extreme design ambient conditions, including projected climate change, so that capacity claims hold through heatwaves and high wet-bulb periods. | The thermal engineering authority shall define design ambient dry-bulb and wet-bulb conditions from a stated climatic data source and return period, shall derate chillers, dry coolers and cooling towers to those conditions, and shall review the derating annually against observed extremes. The facility operator shall monitor available heat-rejection capacity against load during high-ambient periods and shall invoke load-management procedures before capacity is exceeded. | 1) Design ambient conditions are documented with source and return period (for example an extreme annual percentile from a named climatic dataset). 2) Heat-rejection equipment capacity is derated to design ambient with manufacturer data at those conditions. 3) Observed ambient extremes over the last 12 months (including any period above design ambient) are compared with the design basis. 4) Available capacity against load during the hottest observed period shows the declared margin was maintained. 5) A high-ambient procedure exists with trigger thresholds and load-management actions agreed with the AI platform operator. 6) A climate-projection allowance is defined for the asset life or its absence is recorded. | Design ambient dry-bulb [°C] default site-specific (illustrative: 0.4% annual extreme) (ASHRAE climatic design conditions or national equivalent) Design ambient wet-bulb (evaporative systems) [°C] default site-specific (ASHRAE climatic design conditions) Climate-change allowance on design ambient [K] default 2 (illustrative) (Capability profile; regional projections) High-ambient action threshold [% of derated capacity] default 90 (illustrative) (Capability profile) | Climatic design basis with source; Manufacturer capacity data at design ambient; 12 months of ambient and heat-rejection load telemetry; High-ambient operating procedure and records of its use | DOCUMENT_REVIEW; ANALYSIS; SAMPLING; INQUIRY | 1) Confirm the climatic design basis and its source. 2) Check derated capacity calculations against manufacturer data at design ambient. 3) Analyse telemetry for the hottest days in the period: load, available capacity, supply temperatures. 4) Review high-ambient procedure use and outcomes. 5) Record any period where margin fell below threshold as a Finding. | PREVENTIVE | OPERATION | AL4 | DESIGN; OPERATE; CHANGE | NORMAL; DEGRADED; EMERGENCY | Applies to all sites with ambient-dependent heat rejection. Not applicable to heat rejection to a source independent of ambient (for example a stable ground-water or district system), where MCF-THM-016 covers the dependency. | CG-06 | CG-03 | Capacity rated at nominal rather than extreme ambient; Recirculation of hot exhaust raising effective ambient at dry coolers; Fouled coils reducing capacity in summer; No load-management plan for heatwaves | CapacityAssertion; OperatingState; InfrastructureSystem; Hazard | Analysis of records only. High-ambient tests are not induced; any witnessed test during natural peak conditions follows the site permit-to-work. | If design ambient basis or peak-season data is unavailable, record UNKNOWN (U1/U5); do not infer peak-season adequacy from mild-season data. | ASHRAE Standard 169 / ASHRAE Handbook Fundamentals (climatic design conditions); ASHRAE TC 9.9 Thermal Guidelines for Data Processing Environments; EN 50600-2-3 / ISO/IEC 22237-3 (data centre environmental control); AIDCF-004 (Threat, Hazard and Failure Model) | MCF-THM-001; MCF-THM-013; MCF-THM-014; MCF-ENV-021 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-THM-005 | THM | Cooling, Thermal and Fluid Infrastructure | THM-02 | Air cooling systems | Airflow Management | Ensure cold supply air reaches IT inlets at the required temperature and volume without bypass or recirculation, including the residual air-side heat from liquid-cooled racks. | The facility operator shall maintain an airflow management regime (blanking, brush grommets, cable cut-out sealing, floor-tile or supply-diffuser placement, fan-wall or CRAH control) and shall verify by periodic measurement that IT inlet temperatures at the top, middle and bottom of sampled racks remain within the declared envelope and that bypass and recirculation are within declared limits. | 1) IT inlet temperature measurements at multiple heights across sampled racks are within the declared envelope for the period. 2) Supply/return temperature differential at air handlers is consistent with low bypass (within declared range). 3) A sample inspection finds blanking panels, cable sealing and tile/diffuser placement consistent with the airflow standard. 4) Residual air heat from liquid-cooled racks is included in airflow planning and measured in at least one hall. 5) Exceptions (hot spots, missing blanking) are ticketed and closed within the declared time. | IT inlet temperature envelope [°C] default 18–27 (ASHRAE TC 9.9 recommended envelope (classes A1–A4); site may adopt narrower OEM limits) Air-handler ΔT lower bound (bypass indicator) [K] default 8 (illustrative) (Capability profile) Hot-spot closure time [h] default 24 (illustrative) (Capability profile) | IT inlet temperature telemetry at multiple rack heights; Airflow standard and inspection checklist; Inspection records for sampled rows; Hot-spot tickets and closure records | OBSERVATION; INSPECTION; SAMPLING; ANALYSIS | 1) Select sample rows covering highest-density racks. 2) Analyse inlet telemetry by height for the period. 3) Walk the sampled rows and inspect blanking, sealing and containment interfaces. 4) Review hot-spot tickets for closure time. 5) Compare air-handler ΔT with the bypass indicator. | PREVENTIVE | OPERATION | AL4 | COMMISSION; OPERATE; CHANGE | NORMAL; MAINTENANCE | Applies wherever any IT heat is removed by air, including residual heat from liquid-cooled racks. Not applicable to fully immersion-cooled halls with no air-cooled IT. |  | CG-06 | Recirculation of exhaust air to inlets; Bypass air reducing effective capacity; Missing blanking after maintenance; Residual heat from liquid racks unplanned | InfrastructureSystem; AssetInstance; Safeguard | Non-intrusive: inspection without opening live electrical enclosures; follow hall access rules and hot-aisle heat-stress limits. | If inlet measurement is absent for high-density racks, record U5 UNKNOWN for those racks; do not rely on room-average temperatures. | ASHRAE TC 9.9 Thermal Guidelines for Data Processing Environments; EN 50600-2-3 / ISO/IEC 22237-3 (data centre environmental control); ANSI/TIA-942 (telecommunications infrastructure standard for data centres) | MCF-THM-006; MCF-THM-008; MCF-THM-001 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-THM-006 | THM | Cooling, Thermal and Fluid Infrastructure | THM-02 | Air cooling systems | Containment | Ensure hot-aisle or cold-aisle containment, chimney cabinets or rear-door heat exchangers are installed and maintained as designed so that supply and exhaust air streams remain separated, and that containment does not compromise fire detection, suppression or egress. | The facility operator shall install and maintain containment in accordance with the approved design, shall reconcile the as-built containment (doors, roof panels, end-of-row doors, rear-door heat exchangers) with the design, and shall demonstrate that fire detection and suppression coverage inside containment and the release of drop-away or fusible panels have been accepted by the fire-safety authority. | 1) As-built containment reconciles to the approved design for sampled rows. 2) Doors, roof panels and seals are present and closed in sampled rows. 3) Fire detection and suppression design covers the contained volume and has fire-safety authority acceptance. 4) Where rear-door heat exchangers are used, their water connections, leak detection and fan power are documented and their capacity matches rack heat. 5) Egress from contained aisles meets the site safety rules. | Maximum leakage area of containment [% of containment area] default declared by design (illustrative 2) (Design authority) | Containment design drawings; As-built inspection record; Fire-safety authority acceptance for contained aisles; Rear-door heat exchanger schedule and connection details (if used) | INSPECTION; DOCUMENT_REVIEW; RECONCILIATION | 1) Obtain containment design and fire acceptance. 2) Inspect sampled rows for completeness and condition. 3) Reconcile rear-door heat exchanger connections and leak detection where present. 4) Record deviations. | PREVENTIVE | IMPLEMENTATION | AL3 | DESIGN; BUILD; COMMISSION; CHANGE | NORMAL; MAINTENANCE | Applies where containment or rear-door heat exchangers are part of the air-side design. Not applicable to open-room designs that declare no containment, if MCF-THM-005 demonstrates inlet compliance. |  | CG-06; CG-04 | Open containment doors causing mixing; Containment obstructing suppression agent distribution; Rear-door heat exchanger fan or water failure unmonitored | AssetInstance; Safeguard; Hazard | Inspection only. Do not open containment roof panels or trigger drop-away mechanisms. | If fire-safety acceptance cannot be produced, record UNKNOWN and refer to the CG-04 evaluation; the control cannot be CONFORMING. | ASHRAE TC 9.9 Thermal Guidelines for Data Processing Environments; NFPA 75 (fire protection of information technology equipment); EN 50600-2-3 / ISO/IEC 22237-3 (data centre environmental control) | MCF-THM-005; MCF-THM-019; MCF-PHY-021; MCF-PHY-022 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-THM-007 | THM | Cooling, Thermal and Fluid Infrastructure | THM-02 | Air cooling systems | CRAH and In-Row Capacity | Ensure computer-room air handlers, fan walls and in-row coolers deliver the air-side capacity required by the heat-load model, with declared redundancy, at the actual chilled-water or facility-water supply temperature. | The facility operator shall maintain a unit schedule for air handlers and in-row coolers stating sensible capacity at the actual entering-water and return-air conditions, and shall demonstrate that each air-cooling zone meets residual air heat with the declared redundancy. The thermal engineering authority shall re-rate capacity when supply water temperature or return-air setpoints change. | 1) Unit schedule states sensible capacity at site entering-water and return-air conditions. 2) Each zone's capacity with the largest unit out of service meets zone air-side heat load. 3) Fan, valve and controller configuration matches commissioning records for sampled units. 4) Zone heat load used is the residual air heat from MCF-THM-001, including liquid-rack residual heat. 5) Units are maintained per schedule with no overdue critical maintenance in the sample. | Air-side redundancy per zone [configuration] default N+1 (illustrative) (Capability profile) Entering-water temperature for rating [°C] default site design value (Design basis) | Unit schedule with rated sensible capacity at site conditions; Zone capacity analysis; Unit configuration export or BMS point list; Air-handler and in-row cooler planned-maintenance completion records | DOCUMENT_REVIEW; RECONCILIATION; INSPECTION; ANALYSIS | 1) Obtain unit schedule and zone analysis. 2) Recalculate one zone's N−1 capacity at site conditions. 3) Reconcile configuration export with commissioning settings. 4) Check maintenance records for sampled units. | PREVENTIVE | IMPLEMENTATION | AL3 | DESIGN; COMMISSION; OPERATE; CHANGE | NORMAL; MAINTENANCE; DEGRADED | Applies where air handlers or in-row coolers remove in-scope heat. |  | CG-06 | Capacity overstated at elevated water temperature; Zone redundancy lost due to unit placement; Fan speed limits misconfigured | AssetInstance; CapacityAssertion; InfrastructureSystem | Records and configuration review. Any unit isolation to verify redundancy follows site permit-to-work. | If unit capacity at site water temperature is not documented, record UNKNOWN (U1) for the zone. | ASHRAE TC 9.9 Thermal Guidelines for Data Processing Environments; EN 50600-2-3 / ISO/IEC 22237-3 (data centre environmental control); ASHRAE Guideline 0 (the commissioning process) | MCF-THM-001; MCF-THM-002; MCF-THM-005 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-THM-008 | THM | Cooling, Thermal and Fluid Infrastructure | THM-02 | Air cooling systems | Air-Side Monitoring | Ensure air temperature, humidity and differential pressure are measured at points that represent IT inlet conditions, with alarm thresholds that give operators time to act before IT thermal limits or throttling are reached. | The facility operator shall deploy and maintain air-side sensors at IT inlet positions (not only at return air), with calibrated accuracy, defined alarm thresholds tiered below the IT envelope limits, and alarm routing to a staffed function. The facility operator shall review alarm performance, sensor coverage and nuisance alarms at least quarterly. | 1) Sensor coverage includes IT inlet positions in every row of high-density racks. 2) Sensors have calibration records within the calibration interval. 3) Warning and critical thresholds are defined below the declared envelope limits and documented. 4) Alarm routing reaches a staffed function and response times are recorded. 5) Data gaps and sensor failures are detected and tracked. | Inlet sensor density [sensors per row] default ≥ 3 (illustrative) (Capability profile) Sensor accuracy [K] default ±0.5 (illustrative) (Capability profile; instrument specification) Calibration interval [months] default 12 (illustrative) (Instrument manufacturer / site metrology policy) | Sensor layout drawing or point list; Calibration certificates for air-side temperature and humidity sensors; Alarm threshold schedule; Alarm log and response records; Telemetry data-completeness report | INSPECTION; SAMPLING; ANALYSIS; REPERFORMANCE | 1) Compare point list with rack layout. 2) Sample calibration records. 3) Review alarm thresholds against the envelope. 4) Analyse alarm log for response time and gaps. 5) Spot-check sensor reading against reference instrument. | DETECTIVE | OPERATION | AL4 | COMMISSION; OPERATE | NORMAL; DEGRADED; MAINTENANCE | Applies wherever air-side cooling serves in-scope IT. |  | CG-06 | Sensors at return air only, masking inlet hot spots; Uncalibrated sensors reading low; Alarms routed to unstaffed queue; Data gaps unnoticed | AssetInstance; Safeguard; EvidenceObject | Reference-instrument spot checks are non-intrusive; do not disconnect live sensors. | If sensor calibration or data completeness cannot be shown, treat telemetry as R2 and record UNKNOWN for operating claims relying on it. | ASHRAE TC 9.9 Thermal Guidelines for Data Processing Environments; EN 50600-2-3 / ISO/IEC 22237-3 (data centre environmental control) | MCF-THM-005; MCF-THM-022; MCF-OPS-013 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-THM-009 | THM | Cooling, Thermal and Fluid Infrastructure | THM-03 | Liquid cooling systems | Direct-to-Chip Architecture | Ensure the direct-to-chip liquid-cooling architecture (cold plates, manifolds, technology cooling system, CDUs and facility water interface) is designed to the accelerator OEM's coolant, temperature, flow, pressure and wetted-material requirements and to an explicit facility water class. | The thermal engineering authority shall document a direct-to-chip design basis stating: the TCS fluid, supply temperature range, minimum flow per rack and per cold plate, maximum pressure and differential pressure, filtration, wetted materials, and the ASHRAE liquid-cooling W-class of the facility water system at the CDU interface. The facility owner shall obtain written OEM confirmation that the design basis meets the platform requirements and shall maintain a TCS/FWS P&ID. | 1) The design basis states TCS fluid, supply temperature, flow, pressure, filtration and wetted materials, each with OEM source. 2) The FWS-to-TCS interface is classified by W-class with the facility water supply temperature range stated. 3) The approach temperature across the CDU heat exchanger is stated and the TCS supply temperature is achievable at worst-case FWS supply temperature. 4) A current P&ID shows TCS and FWS loops, CDUs, isolation valves, filters, expansion and fill points, and sensors. 5) OEM confirmation of compatibility with the design basis exists for each deployed platform. 6) The architecture identifies whether CDUs are liquid-to-liquid or liquid-to-air and the consequences for heat-rejection dependency. | Facility water class at CDU interface [ASHRAE W-class] default W32 (illustrative) (ASHRAE TC 9.9 liquid-cooling classes W17–W45 and W+) TCS supply temperature to cold plates [°C] default OEM-specified (illustrative 30–40) (Platform OEM specification) CDU heat-exchanger approach temperature [K] default 3 (illustrative) (CDU manufacturer data) TCS filtration rating [µm] default 50 (illustrative; OEM may require finer) (Platform OEM specification; OCP cold-plate guidance) | Direct-to-chip design basis document; TCS/FWS P&ID; OEM coolant and facility requirements documents; OEM compatibility confirmation; CDU selection data at design FWS temperature | DOCUMENT_REVIEW; ANALYSIS; INQUIRY | 1) Obtain design basis, P&ID and OEM requirements. 2) Compare each design parameter with the OEM requirement. 3) Check approach temperature: worst-case FWS supply + approach ≤ maximum TCS supply. 4) Confirm OEM compatibility statements. 5) Record mismatches as Findings. | DIRECTIVE | DESIGN | AL2 | PLAN; DESIGN; CHANGE | NORMAL; TRANSITION | Applies where any in-scope IT is cooled by direct-to-chip cold plates. Immersion systems are covered by MCF-THM-017 and MCF-THM-010 for their coolant and heat-exchange stages. |  | CG-06 | TCS supply temperature unattainable at peak FWS temperature; Wetted-material incompatibility causing corrosion; Flow per cold plate below OEM minimum; Undocumented loop topology | InfrastructureSystem; Interface; ArchitectureSnapshot; Resource | Desk-based review; no intrusive action. | If OEM requirements for a platform are unavailable, record U1 UNKNOWN and treat dependent CDU capacity claims as unverified. | ASHRAE TC 9.9 Liquid Cooling Guidelines for Datacom Equipment Centers; Open Compute Project Advanced Cooling Solutions guidance (cold plate, CDU, immersion); ASHRAE TC 9.9 Thermal Guidelines for Data Processing Environments; AIDCF-013 (AI Data Centre Assurance Reference Architecture) | MCF-THM-010; MCF-THM-011; MCF-THM-017; MCF-CMP-003 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-THM-010 | THM | Cooling, Thermal and Fluid Infrastructure | THM-03 | Liquid cooling systems | CDU Capacity | Demonstrate that coolant distribution units deliver the required heat transfer, flow and supply temperature to every served rack under design load, with declared redundancy of pumps, heat exchangers and power supplies. | The thermal engineering authority shall demonstrate, by commissioning or periodic test, that each CDU group delivers design heat transfer at design FWS temperature with the declared pump and heat-exchanger redundancy, and that pump failover maintains flow without TCS supply temperature leaving the OEM limit. The facility operator shall not connect racks to a CDU group beyond its demonstrated capacity. | 1) Each CDU group has a test record at design load (or load bank) showing heat transfer, TCS supply temperature and flow. 2) Pump redundancy (for example duty/standby or N+1) is tested by failing a duty pump; flow recovers within the declared time without exceeding TCS temperature limits. 3) CDU power supplies are dual-fed or the single-feed risk is treated under MCF-THM-003. 4) Racks connected per CDU group are within the demonstrated capacity. 5) For liquid-to-air CDUs, capacity is rated at the hall air temperature actually available. 6) Strainers and filters are monitored for differential pressure and the impact of fouling on flow is bounded. | CDU pump failover recovery time [s] default 10 (illustrative) (CDU manufacturer data; verify by test) Minimum TCS flow per rack [l/min] default OEM-specified (Platform OEM specification) CDU group redundancy [configuration] default N+1 (illustrative) (Capability profile) | CDU test records at design load; Pump failover test traces (flow, pressure, TCS supply temperature); CDU-to-rack connection register; CDU configuration export (pump control mode, setpoints); Filter differential-pressure trend | TEST; DOCUMENT_REVIEW; RECONCILIATION; ANALYSIS | 1) Select CDU groups serving the highest-load racks. 2) Review design-load and failover test records against criteria. 3) Reconcile rack connection register with demonstrated capacity. 4) Review CDU configuration and filter ΔP trends. 5) Record untested groups as UNKNOWN. | PREVENTIVE | EFFECTIVENESS | AL5 | COMMISSION; OPERATE; CHANGE | NORMAL; DEGRADED; MAINTENANCE; TRANSITION | Applies to all CDUs serving in-scope IT, including in-rack, in-row and facility-scale CDUs and immersion-tank heat exchangers. | CG-06 | CG-07 | Duty pump failure without successful standby start; CDU overloaded by rack additions; Strainer fouling reducing flow; Liquid-to-air CDU starved by high hall temperature | AssetInstance; CapacityAssertion; TestRecord; FaultDomain | Pump failover tests on live loops risk thermal trips of production IT. Requires a permit-to-work and method statement approved by the site authorising engineer, AI platform operator agreement and an abort criterion based on TCS supply temperature. | If no failover test exists for a CDU group, record U1 UNKNOWN; design data alone cannot support the EFFECTIVENESS claim. | ASHRAE TC 9.9 Liquid Cooling Guidelines for Datacom Equipment Centers; Open Compute Project Advanced Cooling Solutions guidance (cold plate, CDU, immersion); ASHRAE Guideline 0 (the commissioning process) | MCF-THM-009; MCF-THM-011; MCF-THM-021; MCF-THM-002 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-THM-011 | THM | Cooling, Thermal and Fluid Infrastructure | THM-03 | Liquid cooling systems | Secondary Loop Integrity | Ensure the technology cooling system (secondary loop) maintains pressure, flow, temperature and fluid inventory within limits, is pressure-tested, and has no unmanaged single points of failure between CDU and cold plate. | The facility operator shall monitor TCS supply and return temperature, differential pressure, flow, system pressure and make-up/fill volume continuously, shall pressure-test new and modified TCS pipework before fill, and shall investigate any unexplained make-up volume. The thermal engineering authority shall maintain a single-point-of-failure analysis of the TCS from CDU to manifold to cold plate. | 1) TCS pressure, differential pressure, flow and supply/return temperature are monitored continuously and trends are within limits for the period. 2) Pressure tests are recorded for all new or modified TCS pipework before fill, at the specified test pressure and hold time. 3) Make-up volume is metered and any unexplained loss is investigated. 4) A single-point-of-failure analysis of the TCS path (header, manifold, hoses, valves) exists and identified points are treated. 5) Rack ΔT and flow anomalies are alarmed before OEM throttle thresholds. | Pressure test level [× maximum operating pressure] default 1.5 (illustrative) (Piping code or manufacturer specification) Pressure test hold time [min] default 30 (illustrative) (Piping code or manufacturer specification) Unexplained make-up volume investigation threshold [l per week per loop] default 5 (illustrative) (Capability profile) | TCS telemetry trends (P, ΔP, flow, T); Pressure-test certificates; Make-up volume log; TCS single-point-of-failure analysis; Alarm schedule for TCS points | ANALYSIS; DOCUMENT_REVIEW; INSPECTION; SAMPLING | 1) Analyse TCS telemetry for excursions and trends. 2) Sample pressure-test certificates against modification records. 3) Reconcile make-up volume log with investigations. 4) Review the single-point-of-failure analysis. 5) Inspect a sample of manifolds and hose routes. | PREVENTIVE | OPERATION | AL4 | BUILD; COMMISSION; OPERATE; CHANGE | NORMAL; DEGRADED; MAINTENANCE; RECOVERY | Applies to all liquid TCS loops serving in-scope IT. | CG-06 | CG-09 | Slow leak depleting inventory; Air ingress causing pump cavitation; Manifold single point of failure; Over-pressure on valve closure | InfrastructureSystem; FaultDomain; Safeguard; AssetInstance | Pressure testing of filled loops is hazardous; it requires an approved method statement, pressure-equipment competence and isolation from IT equipment. Assessors do not operate valves. | If make-up volume or pressure-test records are missing for modified sections, record U1 UNKNOWN for those loops. | ASHRAE TC 9.9 Liquid Cooling Guidelines for Datacom Equipment Centers; Open Compute Project Advanced Cooling Solutions guidance (cold plate, CDU, immersion); ASME B31.9 (building services piping); Pressure Equipment Directive 2014/68/EU or equivalent national pressure-equipment regulation | MCF-THM-010; MCF-THM-012; MCF-THM-019 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-THM-012 | THM | Cooling, Thermal and Fluid Infrastructure | THM-03 | Liquid cooling systems | Quick-Disconnect Management | Ensure quick-disconnect couplings between manifolds and IT are specified, compatible, connected, inspected and replaced under control, because they are the most frequently operated wetted joints and a common leak and flow-restriction source. | The facility operator shall maintain a register of quick-disconnect coupling types and compatibility by platform, shall perform connect/disconnect only under a documented procedure by trained staff with drip containment, and shall inspect and replace couplings and seals on a defined interval or cycle count. The AI platform operator shall not install IT with couplings outside the register. | 1) A coupling register lists types, ratings, compatible counterparts and wetted materials per platform. 2) A connect/disconnect procedure exists with drip containment, purge and post-connection leak check. 3) Staff performing connections have recorded training. 4) Sample work orders show the procedure was followed, including post-connection leak checks. 5) Couplings are inspected or replaced per interval or cycle count, and failures are trended. | Coupling inspection interval [months] default 12 (illustrative) (Coupling manufacturer guidance) Rated connect/disconnect cycles [cycles] default manufacturer-rated (Coupling manufacturer data) | Coupling register; Connect/disconnect procedure; Training records; Sample work orders with leak-check sign-off; Coupling failure trend | DOCUMENT_REVIEW; SAMPLING; OBSERVATION; INQUIRY | 1) Review register against deployed platforms. 2) Sample work orders for procedure adherence. 3) Observe a connection or disconnection where possible. 4) Review failure trend and replacement records. | PREVENTIVE | OPERATION | AL4 | BUILD; OPERATE; CHANGE | NORMAL; MAINTENANCE; TRANSITION | Applies where IT is connected to TCS manifolds by quick-disconnect couplings. Not applicable to hard-piped cold-plate systems. |  | CG-06; CG-04; CG-14 | Incompatible couplings mated; Seal degradation causing drip leak; Partial engagement restricting flow; Coolant spill onto energised equipment | AssetInstance; Interface; Hazard; Safeguard | Observation only; connections are made by trained site staff under procedure. Spill onto energised equipment is an electrical hazard: the procedure must require drip containment. | If the coupling register does not cover a deployed platform, record U1 UNKNOWN for that platform. | Open Compute Project Advanced Cooling Solutions guidance (cold plate, CDU, immersion); ASHRAE TC 9.9 Liquid Cooling Guidelines for Datacom Equipment Centers | MCF-THM-011; MCF-THM-019; MCF-CMP-021 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-THM-013 | THM | Cooling, Thermal and Fluid Infrastructure | THM-04 | Heat rejection and water systems | Chiller Capacity | Demonstrate that chillers (where present) deliver required capacity at design condenser conditions with declared redundancy, restart quickly after power interruption, and that refrigerant hazards are controlled. | The facility operator shall demonstrate chiller capacity at design condenser conditions with the declared redundancy, shall evidence restart-to-capacity time after power interruption, and shall maintain refrigerant inventory, leak detection, machinery-room ventilation and safety classification records in accordance with the applicable refrigeration safety standard. | 1) Chiller capacity at design condenser conditions with N−1 meets design load. 2) Restart-to-capacity time after power interruption is evidenced by test and is within the ride-through window. 3) Refrigerant type, charge, safety class and machinery-room requirements are documented. 4) Refrigerant leak detection and ventilation are installed and functionally tested. 5) Refrigerant leak and charge records meet applicable regulatory requirements. 6) Chiller sequencing logic is documented and tested for failure of the lead chiller. | Chiller restart-to-capacity [s] default 300 (illustrative) (Manufacturer rapid-restart data) Chiller redundancy [configuration] default N+1 (illustrative) (Capability profile) | Chiller performance test or commissioning data at design conditions; Restart test record; Refrigerant register and safety classification; Refrigerant detector test records; Sequencing logic description and test | TEST; DOCUMENT_REVIEW; INSPECTION; ANALYSIS | 1) Review capacity and restart test records. 2) Compare restart time with ride-through analysis in MCF-THM-003. 3) Inspect refrigerant detection and machinery-room provisions. 4) Review sequencing tests and refrigerant records. | PREVENTIVE | EFFECTIVENESS | AL5 | COMMISSION; OPERATE; CHANGE | NORMAL; DEGRADED; EMERGENCY; RECOVERY | Applies where mechanical refrigeration is in the heat-removal path. Not applicable to chiller-less designs (for example W32+ with dry coolers only), provided MCF-THM-004 shows dry-cooler capacity at design ambient. | CG-06 | CG-04 | Chiller fails to restart after transfer; Lead chiller failure without sequencing to standby; Refrigerant leak in occupied space; Capacity loss at high condenser temperature | AssetInstance; CapacityAssertion; Hazard; TestRecord | Restart tests interrupt chilled water; Requires a permit-to-work and method statement approved by the site authorising engineer and thermal-storage or redundancy cover. Refrigerant work requires certified personnel. | If restart-to-capacity has not been tested, record U1 UNKNOWN; this carries into MCF-THM-003 ride-through. | ASHRAE Standard 15 / ISO 5149 / EN 378 (refrigeration system safety); EU F-gas Regulation or applicable refrigerant regulation; ASHRAE Guideline 0 (the commissioning process); Uptime Institute Tier Standard: Topology | MCF-THM-003; MCF-THM-004; MCF-THM-024 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-THM-014 | THM | Cooling, Thermal and Fluid Infrastructure | THM-04 | Heat rejection and water systems | Cooling Tower or Dry Cooler | Ensure final heat-rejection equipment (cooling towers, adiabatic or dry coolers) operates at the required capacity, is protected against fouling, freezing, recirculation and fan or spray failures, and is maintained to preserve capacity. | The facility operator shall operate and maintain heat-rejection units to preserve capacity at design ambient, shall monitor approach temperature and fan/pump status per unit, shall protect against freezing and hot-air recirculation, and shall record fouling and coil-cleaning interventions. Where evaporative or adiabatic systems are used, the facility operator shall implement MCF-THM-018 water treatment. | 1) Approach temperature per unit is trended and units with degraded approach are investigated. 2) Fan and pump status is monitored per unit with alarms. 3) Freeze protection (glycol concentration, heat tracing, drain-down) is in place where ambient can fall below freezing. 4) Layout or wind analysis addresses hot-air recirculation between units and from adjacent sources. 5) Coil cleaning or tower maintenance follows schedule. | Approach temperature degradation threshold [K above commissioned] default 2 (illustrative) (Capability profile) | Approach temperature trends; Unit status alarms; Freeze-protection records; Recirculation study or observation; Coil-cleaning and tower maintenance records | ANALYSIS; INSPECTION; DOCUMENT_REVIEW | 1) Analyse approach temperature by unit. 2) Inspect units for fouling, damage and recirculation paths. 3) Review freeze protection. 4) Review maintenance compliance. | PREVENTIVE | OPERATION | AL4 | COMMISSION; OPERATE; CHANGE | NORMAL; DEGRADED; MAINTENANCE | Applies to all final heat-rejection equipment in the boundary. |  | CG-06 | Hot-air recirculation raising entering temperature; Coil fouling; Freeze damage; Fan failure at peak ambient | AssetInstance; InfrastructureSystem; Hazard | Roof and plant-yard inspection requires working-at-height controls; evaporative towers require respiratory precautions under the legionella risk assessment. | If per-unit monitoring is absent, record U5 UNKNOWN for unit-level degradation. | ASHRAE Standard 169 / ASHRAE Handbook Fundamentals (climatic design conditions); ASHRAE Standard 188 (legionellosis risk management for building water systems); EN 50600-2-3 / ISO/IEC 22237-3 (data centre environmental control) | MCF-THM-004; MCF-THM-016; MCF-THM-018 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-THM-015 | THM | Cooling, Thermal and Fluid Infrastructure | THM-04 | Heat rejection and water systems | Water Continuity | Ensure evaporative and adiabatic heat rejection, and loop make-up, can continue through loss or restriction of mains water supply for the declared autonomy period. | The facility owner shall determine water consumption at design ambient and peak load, shall provide on-site storage or alternative supply for the declared water autonomy, and shall document the dependency on the water utility, including restriction scenarios and drought orders. The facility operator shall test the switchover to stored or alternative water and shall monitor stored volume. | 1) Peak water consumption at design ambient and load is calculated. 2) On-site storage or alternative supply provides the declared autonomy at peak consumption. 3) Switchover to stored water is tested and recorded. 4) Stored volume is monitored with low-level alarms. 5) The water utility dependency, including restriction scenarios, is documented and owned. 6) A fallback mode (for example dry operation with reduced capacity) is defined with its capacity impact on IT load. | Water autonomy at peak consumption [h] default 48 (illustrative) (Capability profile; utility risk assessment) Peak water consumption [m³/h] default site-calculated (Design calculation at design wet-bulb and load) | Water consumption calculation; Storage capacity data; Switchover test record; Level telemetry and alarms; Utility dependency record | ANALYSIS; TEST; DOCUMENT_REVIEW; INQUIRY | 1) Recalculate peak consumption. 2) Compare with storage autonomy. 3) Review switchover test. 4) Review dependency ownership and fallback mode. | PREVENTIVE | RESILIENCE | AL5 | DESIGN; OPERATE; CHANGE | NORMAL; DEGRADED; EMERGENCY | Applies where heat rejection or loop make-up depends on water supply. Not applicable to closed-loop dry heat rejection with no evaporative component, except for loop make-up which is covered by MCF-THM-011. | CG-06 | CG-03 | Mains supply loss exhausting storage; Drought restriction curtailing evaporative cooling; Switchover valve failure | Dependency; Resource; CapacityAssertion; FailureScenario | Switchover tests follow the site permit-to-work and must not drain storage below the minimum safe level. | If peak consumption is not calculated, record U1 UNKNOWN; autonomy cannot be asserted. | ASHRAE Standard 188 (legionellosis risk management for building water systems); EN 50600-2-3 / ISO/IEC 22237-3 (data centre environmental control); AIDCF-004 (Threat, Hazard and Failure Model) | MCF-THM-014; MCF-THM-016; MCF-DEP-009; MCF-ENV-011; MCF-ENV-022 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-THM-016 | THM | Cooling, Thermal and Fluid Infrastructure | THM-04 | Heat rejection and water systems | Heat-Rejection Dependency | Make explicit every dependency of the heat-removal path on external or shared resources (water, power, controls, district systems, shared plant with other tenants) and the common modes that could remove several redundant trains at once. | The thermal engineering authority shall maintain a heat-rejection dependency map from IT heat source to final heat sink, identifying shared headers, common controllers, common power boards, shared water supplies, third-party plant and heat-reuse interfaces, and shall record the treatment and owner of each common mode. The facility owner shall ensure heat-reuse or district-energy interfaces cannot reduce heat-rejection capacity below design load. | 1) A dependency map exists from rack to final heat sink for each redundant train. 2) Common-mode points (shared header, controller, board, water feed) are listed with treatment and owner. 3) Third-party or shared plant is identified with contractual service levels. 4) Heat-reuse or district interfaces have a defined fall-back that preserves heat rejection when the external heat sink is unavailable. 5) The map is reconciled to the current P&ID. |  | Heat-rejection dependency map; Common-mode register; Third-party service agreements; Heat-reuse interface design and fall-back | DOCUMENT_REVIEW; ANALYSIS; RECONCILIATION | 1) Obtain dependency map and P&ID. 2) Trace each train for shared elements. 3) Review treatment of each common mode. 4) Review heat-reuse fall-back. | DIRECTIVE | DESIGN | AL2 | PLAN; DESIGN; CHANGE | NORMAL; DEGRADED; EMERGENCY | Applies to all heat-rejection paths in scope. |  | CG-03; CG-09; CG-06 | Shared header defeating redundancy; District heat sink unavailable; Common controller failure; Tenant plant change | Dependency; FaultDomain; Interface; InfrastructureSystem | Desk-based review of dependency records and P&IDs; site walk-downs to confirm shared elements are visual only. | Any unmapped shared element discovered during inspection is recorded as a U10 dependency UNKNOWN and escalated to CG-03. | Uptime Institute Tier Standard: Topology; AIDCF-004 (Threat, Hazard and Failure Model); AIDCF-013 (AI Data Centre Assurance Reference Architecture) | MCF-THM-015; MCF-THM-003; MCF-DEP-005; MCF-DEP-006 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-THM-017 | THM | Cooling, Thermal and Fluid Infrastructure | THM-05 | Fluid quality and leak management | Coolant Compatibility | Ensure every coolant and immersion fluid is compatible with all wetted materials and IT components, is safe to handle, and that its hazards (toxicity, flammability, environmental, pressure) are identified and controlled. | The thermal engineering authority shall specify each coolant (for example propylene-glycol solution, treated water, dielectric immersion fluid) with its composition, inhibitor package, approved wetted materials and OEM approval, and shall obtain and act upon the safety data sheet. The facility owner shall ensure fluid handling, storage, spill response and disposal arrangements are in place and accepted by the site safety authority. | 1) Each coolant has a specification with composition, inhibitor package and OEM approval for every platform it contacts. 2) A wetted-materials list exists for each loop and is checked against the coolant's compatibility data. 3) Mixing of incompatible fluids is prevented by labelling, dedicated fill equipment and procedure. 4) Safety data sheets are held and hazards are reflected in handling, PPE, storage and spill procedures. 5) For immersion fluids, flammability, material compatibility with IT components and long-term fluid degradation are assessed. | Glycol concentration [% by volume] default OEM-specified (illustrative 25) (Platform OEM coolant specification; OCP propylene-glycol guidance) | Coolant specification per loop; Wetted-materials list; OEM approval letters; Safety data sheets; Handling and spill procedures | DOCUMENT_REVIEW; INQUIRY; INSPECTION | 1) Review coolant specifications against OEM requirements. 2) Cross-check wetted-materials list. 3) Inspect fluid storage and labelling. 4) Review handling procedures against the SDS. | PREVENTIVE | DESIGN | AL2 | DESIGN; BUILD; CHANGE | NORMAL; MAINTENANCE | Applies to all liquid and immersion cooling fluids in scope. |  | CG-04; CG-06 | Galvanic corrosion from mixed metals; Inhibitor package incompatible with wetted materials; Fluid mixing; Dielectric fluid incompatibility with cable jackets | Resource; Hazard; Safeguard; Interface | Fluid sampling follows the SDS and site PPE requirements. | If OEM approval for a coolant cannot be shown, record UNKNOWN and treat the loop's integrity claims as conditioned. | ASHRAE TC 9.9 Liquid Cooling Guidelines for Datacom Equipment Centers; Open Compute Project Advanced Cooling Solutions guidance (cold plate, CDU, immersion); Regulation (EC) No 1272/2008 (CLP) / GHS safety data sheets | MCF-THM-018; MCF-THM-009; MCF-THM-020; MCF-ENV-018 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-THM-018 | THM | Cooling, Thermal and Fluid Infrastructure | THM-05 | Fluid quality and leak management | Water Quality | Maintain the chemistry, cleanliness and microbiological quality of TCS, FWS and condenser water so that cold plates do not foul, corrosion is controlled, and evaporative systems do not present a legionella risk to people. | The facility operator shall implement a water-quality programme with sampling frequencies and limits for each loop (pH, conductivity, inhibitor level, glycol concentration, suspended solids, microbiological counts), shall maintain filtration to the OEM rating, and shall act on out-of-limit results within defined times. Where evaporative cooling towers or adiabatic systems exist, the facility owner shall maintain a legionella risk assessment and written control scheme under the applicable regulation, reviewed by a competent person. | 1) Sampling schedule and limits exist for each loop and are derived from OEM and fluid-supplier requirements. 2) Sample results for the period are within limits or exceedances were corrected within the defined time. 3) Filter differential pressure and replacement records show filtration maintained. 4) A current legionella risk assessment and written scheme exist for evaporative systems, with competent-person review. 5) Microbiological testing results for evaporative systems are recorded and actioned. 6) Laboratory analyses use an accredited or OEM-approved laboratory. | TCS sampling frequency [per month] default 1 (illustrative) (OEM/fluid supplier guidance) Out-of-limit corrective-action time [days] default 7 (illustrative) (Capability profile) Legionella risk assessment review interval [months] default 24 or on change (illustrative) (Applicable national regulation/ACOP) | Water-quality programme and limits; Sample results; Filter records; Legionella risk assessment and written scheme; Microbiological test results | DOCUMENT_REVIEW; ANALYSIS; SAMPLING; INSPECTION | 1) Obtain programme and limits. 2) Analyse 12 months of results for exceedances and corrective actions. 3) Review filter records. 4) Review legionella risk assessment, scheme and results. 5) Inspect a sample point and dosing equipment. | PREVENTIVE | OPERATION | AL4 | COMMISSION; OPERATE | NORMAL; MAINTENANCE | Applies to all water and water-glycol loops in scope. Legionella criteria apply only where evaporative or aerosol-generating systems exist. | CG-04 | CG-06 | Cold-plate microchannel fouling; Biofilm and microbiologically influenced corrosion; Legionella proliferation in cooling towers; Inhibitor depletion | Resource; Hazard; Safeguard; EvidenceObject | Sampling of evaporative systems requires respiratory protection per the legionella risk assessment. Chemical dosing equipment is operated only by the water-treatment contractor. | If no microbiological results exist for an evaporative system, record US4 UNKNOWN against CG-04; the control cannot be CONFORMING. | ASHRAE Standard 188 (legionellosis risk management for building water systems); HSE ACOP L8 (control of legionella bacteria in water systems, UK); ASHRAE TC 9.9 Liquid Cooling Guidelines for Datacom Equipment Centers; Open Compute Project Advanced Cooling Solutions guidance (cold plate, CDU, immersion) | MCF-THM-017; MCF-THM-014; MCF-ENV-009 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-THM-019 | THM | Cooling, Thermal and Fluid Infrastructure | THM-05 | Fluid quality and leak management | Leak Detection | Ensure liquid leaks from TCS, FWS, rear-door heat exchangers and immersion tanks are detected quickly and located precisely enough to isolate the right section before liquid reaches energised equipment or spreads beyond its fault domain. | The facility operator shall install leak detection (rope/cable sensors, spot sensors, CDU and rack-level detection, flow/pressure-based detection) covering every wetted zone above or adjacent to IT and electrical equipment, shall route alarms to a staffed function with locational information, and shall functionally test detection at defined intervals. The thermal engineering authority shall define detection coverage and response time requirements per zone. | 1) A coverage map shows detection for every zone where liquid is present above, within or adjacent to IT or electrical equipment. 2) Functional tests (wet test or manufacturer test method) are recorded for sampled sensors within the interval. 3) Alarms carry zone/location and reach a staffed function; response time is measured. 4) Detection is supplemented by flow/pressure or make-up anomaly detection for slow leaks. 5) False-alarm rates are tracked and do not lead to disabled sensors. | Leak detection functional test interval [months] default 12 (illustrative) (Manufacturer guidance; capability profile) Alarm-to-acknowledgement time [min] default 5 (illustrative) (Capability profile) | Leak detection coverage map; Functional test records; Alarm log with response times; Slow-leak analytics configuration; Disabled-sensor register | TEST; INSPECTION; ANALYSIS; DOCUMENT_REVIEW | 1) Review coverage map against the P&ID and room layout. 2) Witness or review functional tests on sampled sensors. 3) Analyse alarm log for response times. 4) Check disabled-sensor register. | DETECTIVE | EFFECTIVENESS | AL5 | BUILD; COMMISSION; OPERATE; CHANGE | NORMAL; MAINTENANCE; DEGRADED | Applies wherever liquid cooling or water piping is present in or above IT or electrical spaces. |  | CG-06; CG-09; CG-04 | Leak in an uncovered zone; Sensor disabled after false alarms; Alarm without location; Slow leak below sensor threshold | Safeguard; AssetInstance; FailureScenario | Wet tests use small water volumes away from energised equipment, under permit, with the IT operator informed. | Zones with no functional-test record within interval are recorded as U3 stale UNKNOWN. | ASHRAE TC 9.9 Liquid Cooling Guidelines for Datacom Equipment Centers; Open Compute Project Advanced Cooling Solutions guidance (cold plate, CDU, immersion); EN 50600-2-3 / ISO/IEC 22237-3 (data centre environmental control) | MCF-THM-020; MCF-THM-011; MCF-OPS-013; MCF-PHY-011 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-THM-020 | THM | Cooling, Thermal and Fluid Infrastructure | THM-05 | Fluid quality and leak management | Isolation and Drainage | Ensure a detected leak can be isolated to the smallest practicable section, the released liquid is contained and drained away from energised equipment, and the remaining cooling capacity is preserved, so that a leak remains within its fault domain. | The thermal engineering authority shall design isolation valves, drip trays, bunding and drainage so that a leak at any credible point can be isolated to a defined fault domain and drained without reaching electrical equipment outside that domain. The facility operator shall maintain isolation procedures, exercise valves, and demonstrate isolation of a representative section while adjacent sections continue cooling. | 1) Isolation points are defined so that each credible leak location can be isolated within a defined fault domain. 2) Automatic isolation (where used) is linked to leak detection and tested. 3) Drip trays, bunding or floor drainage direct liquid away from electrical equipment and are inspected. 4) Valve exercise records show isolation valves operate and seal. 5) A representative isolation test showed adjacent fault domains maintained cooling. 6) Spill volumes per fault domain are bounded by design. | Maximum release volume per isolated section [l] default design-specific (illustrative 50) (Design authority) Valve exercise interval [months] default 12 (illustrative) (Manufacturer guidance) | Isolation design and fault-domain definition; Automatic isolation test record; Drainage and containment inspection; Valve exercise records; Representative isolation test | TEST; INSPECTION; DOCUMENT_REVIEW; ANALYSIS | 1) Review isolation design against P&ID. 2) Inspect drip trays and drainage. 3) Review valve exercise and automatic isolation tests. 4) Review representative isolation test results. 5) Assess release volume bounds. | CORRECTIVE | EFFECTIVENESS | AL5 | DESIGN; BUILD; COMMISSION; OPERATE | NORMAL; DEGRADED; EMERGENCY; MAINTENANCE | Applies wherever liquid cooling is present in IT space. | CG-09 | CG-04; CG-06 | Isolation valve seized; Isolation of a leak removes cooling from a larger domain than intended; Liquid tracks to electrical busway; Automatic isolation fails to close | FaultDomain; Safeguard; AssetInstance; TestRecord | Isolation tests reduce cooling to the isolated section; Requires a permit-to-work and method statement approved by the site authorising engineer, with the affected IT drained or protected. | If no isolation test exists, record U1 UNKNOWN; design review alone supports DESIGN, not EFFECTIVENESS. | ASHRAE TC 9.9 Liquid Cooling Guidelines for Datacom Equipment Centers; Open Compute Project Advanced Cooling Solutions guidance (cold plate, CDU, immersion); ASME B31.9 (building services piping) | MCF-THM-019; MCF-THM-011; MCF-RES-006; MCF-RES-008; MCF-PHY-011 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-THM-021 | THM | Cooling, Thermal and Fluid Infrastructure | THM-06 | Thermal control, maintenance and recovery | Control Stability | Ensure cooling controls (CDU controllers, BMS sequences, chiller plant managers, pump and valve PID loops) remain stable under rapid AI load swings, fail to a safe cooling state on controller or network loss, and cannot be changed without control. | The controls engineering authority shall document control sequences and fail-safe states for each cooling controller, shall demonstrate stability of temperature and pressure loops under step load changes representative of synchronous training, and shall demonstrate that loss of controller, sensor or controls network leaves pumps running and valves in a safe position. The facility operator shall manage controller configuration under change control with version-controlled backups. | 1) Sequences of operation and fail-safe states are documented per controller. 2) Step-load test shows TCS supply temperature and pressure settle within the declared band and time without sustained oscillation. 3) Loss-of-controller and loss-of-network tests show pumps continue and valves fail to the safe state. 4) Controller configurations are backed up, version-controlled and reconciled to the approved baseline. 5) Remote write access to cooling controllers is restricted and logged. | Settling time after load step [s] default 120 (illustrative) (Controls design; capability profile) Temperature control band [K] default ±1 (illustrative) (Controls design) | Sequences of operation; Step-load test traces; Fail-safe test record; Configuration baseline and backup; Access log for controller changes | TEST; DOCUMENT_REVIEW; RECONCILIATION; ANALYSIS | 1) Review sequences and fail-safe definitions. 2) Review step-load and fail-safe test traces. 3) Reconcile running configuration with baseline. 4) Review access controls and logs. | PREVENTIVE | EFFECTIVENESS | AL5 | DESIGN; COMMISSION; OPERATE; CHANGE | NORMAL; DEGRADED; TRANSITION; FAILED | Applies to all automated controls in the heat-removal path, including vendor CDU controllers. | CG-07 | CG-06; CG-15 | PID oscillation under synchronous load; Controller failure stopping pumps; Valve fails closed on network loss; Unauthorised setpoint change | InfrastructureSystem; Safeguard; Interface; TestRecord | Fail-safe tests on live systems are hazardous; Requires a permit-to-work and method statement approved by the site authorising engineer, controls specialist on site and manual override available. | If fail-safe behaviour is undocumented or untested, record US4 UNKNOWN against CG-07. | IEC 62443 series (industrial automation and control system security); IEC 61131-3 (programmable controller languages); ASHRAE Guideline 0 (the commissioning process) | MCF-THM-010; MCF-THM-022; MCF-SEC-005; MCF-OPS-017 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-THM-022 | THM | Cooling, Thermal and Fluid Infrastructure | THM-06 | Thermal control, maintenance and recovery | Sensor Trust | Ensure the sensors that drive cooling control and alarming (temperature, pressure, flow, leak, level) are accurate, calibrated, redundant where control-critical, and that implausible or failed readings are detected before they mislead control or operators. | The facility operator shall identify control-critical sensors, shall calibrate them at defined intervals, shall provide redundancy or plausibility checks (cross-sensor comparison, rate-of-change, stuck-value detection) for control-critical points, and shall configure controllers to a safe default on sensor failure. | 1) Control-critical sensors are identified in a register. 2) Calibration records exist within interval for sampled sensors. 3) Control-critical points have redundant sensors or plausibility logic. 4) Controllers default to safe action on sensor failure, verified by documentation or test. 5) Sensor faults are alarmed and tracked. | Control-critical sensor calibration interval [months] default 12 (illustrative) (Instrument manufacturer / metrology policy) Redundant-sensor divergence alarm [K] default 1.5 (illustrative) (Capability profile) | Control-critical sensor register; Calibration certificates for control-critical temperature, pressure and flow sensors; Plausibility logic description; Sensor-fault alarm log | DOCUMENT_REVIEW; SAMPLING; ANALYSIS; REPERFORMANCE | 1) Review register. 2) Sample calibration certificates. 3) Review plausibility logic. 4) Analyse sensor-fault log. 5) Spot-check readings. | DETECTIVE | OPERATION | AL4 | COMMISSION; OPERATE; CHANGE | NORMAL; DEGRADED; MAINTENANCE | Applies to sensors used for cooling control or alarming of in-scope systems. |  | CG-07; CG-06 | Drifted sensor causing undercooling; Stuck flow meter masking flow loss; Single sensor failure driving valve closed | AssetInstance; Safeguard; EvidenceObject | Non-intrusive spot checks only. | If a control-critical sensor has no calibration record, treat its data as unverified (U6) and record UNKNOWN against controls relying on it. | IEC 62443 series (industrial automation and control system security); ASHRAE TC 9.9 Liquid Cooling Guidelines for Datacom Equipment Centers; ASHRAE TC 9.9 Thermal Guidelines for Data Processing Environments | MCF-THM-021; MCF-THM-008; MCF-OPS-011 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-THM-023 | THM | Cooling, Thermal and Fluid Infrastructure | THM-06 | Thermal control, maintenance and recovery | Maintenance States | Ensure planned maintenance on cooling plant (CDU servicing, filter changes, valve replacement, chiller overhaul, loop drain-down) is carried out without unplanned loss of cooling, with declared residual redundancy and safe isolation of pressurised fluid systems. | The facility operator shall plan cooling maintenance with a documented method statement stating residual capacity and redundancy during the work, required IT load limits, isolation and lock-out points, and back-out steps; shall coordinate with the AI platform operator where IT load must be reduced; and shall record post-maintenance return-to-service checks. | 1) Method statements for sampled cooling work state residual capacity and redundancy. 2) IT load limits during maintenance are agreed with the AI platform operator where required. 3) Isolation and lock-out of pressurised and energised systems are recorded. 4) Post-maintenance return-to-service checks (flow, pressure, temperature, leak check) are recorded. 5) Maintenance-induced incidents are analysed. | Minimum residual redundancy during maintenance [configuration] default N (illustrative) (Capability profile; risk acceptance) | Method statements; Load-limit agreements; Isolation records; Return-to-service checks; Incident analyses | DOCUMENT_REVIEW; SAMPLING; OBSERVATION; INQUIRY | 1) Sample method statements. 2) Check residual capacity statements against N−1 analysis. 3) Review isolation and return-to-service records. 4) Observe a maintenance activity where possible. | PREVENTIVE | OPERATION | AL4 | OPERATE; CHANGE | MAINTENANCE; TRANSITION; NORMAL | Applies to all planned work on in-scope cooling systems. |  | CG-06; CG-14; CG-04 | Maintenance removes the redundant unit while another is degraded; Air trapped after drain-down; Unsafe isolation of pressurised loop; Return to service without leak check | OperatingState; Safeguard; Action | Observation only; assessors do not take part in isolation. | If residual capacity is not stated on method statements, record a Finding; if records are missing, record U1 UNKNOWN. | ASHRAE Guideline 0 (the commissioning process); Uptime Institute Tier Standard: Topology; EN 50600-2-3 / ISO/IEC 22237-3 (data centre environmental control) | MCF-THM-003; MCF-OPS-006; MCF-OPS-007; MCF-OPS-008 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-THM-024 | THM | Cooling, Thermal and Fluid Infrastructure | THM-06 | Thermal control, maintenance and recovery | Thermal Recovery | Ensure that after loss of cooling or power, the heat-removal path is restored in the right order (power, controls, pumps, heat rejection, CDUs) and IT load is readmitted in steps that do not exceed recovering capacity or trigger repeated thermal trips. | The facility operator shall maintain a thermal recovery procedure defining restart sequence, prerequisites, hold points, verification criteria (flow, TCS supply temperature, leak checks) and staged IT readmission limits agreed with the AI platform operator, and shall exercise it at a defined interval. The facility owner shall define the thermal recovery time objective for each fault domain. | 1) A recovery procedure defines restart sequence, prerequisites and hold points. 2) Verification criteria for each step (flow, pressure, temperature, no leak) are defined. 3) Staged IT readmission limits are defined and agreed with the AI platform operator. 4) The procedure has been exercised (test or real event) within the interval, achieving the recovery time objective. 5) Lessons from exercises and incidents are incorporated. | Thermal recovery time objective [min] default 30 (illustrative) (Capability profile) IT readmission step [% of fault-domain design load] default 25 (illustrative) (Capability profile; recovering capacity) | Thermal recovery procedure; Recovery time objective definition; Exercise or incident record with timeline; Readmission agreement; Lessons-learned record | SCENARIO_EXERCISE; DOCUMENT_REVIEW; ANALYSIS; INQUIRY | 1) Review the recovery procedure and its alignment with power restoration. 2) Review the exercise timeline step by step against the recovery time objective. 3) Check readmission limits against recovering capacity. 4) Interview shift staff on hold points and verification criteria. 5) Record unachieved steps as Findings. | RECOVERY | RESILIENCE | AL5 | COMMISSION; OPERATE; CHANGE | RECOVERY; EMERGENCY; FAILED; TRANSITION | Applies to all heat-removal paths serving in-scope IT. | CG-10 | CG-06 | Pumps restarted before controls, causing pressure surge; IT readmitted too fast, causing repeat trip; Air lock after restart; No agreed readmission plan | FailureScenario; Safeguard; TestRecord; OperatingState | Recovery exercises should be tabletop or on isolated sections unless a live exercise is authorised; Requires a permit-to-work and method statement approved by the site authorising engineer and AI platform operator agreement. | If no exercise or real event is recorded, record US4 UNKNOWN against CG-10. | Uptime Institute Tier Standard: Topology; ASHRAE Guideline 0 (the commissioning process); ISO 22301 (business continuity management systems) | MCF-THM-003; MCF-CMP-023; MCF-RES-014; MCF-POW-024 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-ENV-001 | ENV | Environmental and Resource Performance | ENV-01 | Environmental operating conditions | Temperature Control | Demonstrate that air inlet temperatures at IT equipment and liquid coolant supply temperatures to cold plates or immersion tanks stay within the declared envelope and rate-of-change limits in all declared operating states, measured where the equipment experiences them. | The facility operator shall declare, for each hall and liquid loop, the environmental class (ASHRAE air-cooling class and liquid-cooling W class, or OEM envelope where more restrictive) and shall measure inlet air temperature at representative rack inlets and coolant supply temperature at the technology cooling system interface. The facility operator shall alarm excursions and rates of change outside the envelope, investigate them, and report excursion time per hall at the declared interval. | 1) Each hall and loop has a declared envelope traceable to ASHRAE classes or OEM specification. 2) Inlet sensors are at rack inlets (not return air) at the declared density, and coolant supply sensors are at the TCS interface. 3) Excursion time outside the recommended envelope per hall is reported and within the declared limit. 4) Rate-of-change alarms exist and events are investigated. 5) Sensor calibration is current for the sampled sensors. | Recommended IT inlet air temperature envelope [°C] default 18 to 27 (ASHRAE TC 9.9 thermal guidelines recommended envelope) Liquid-cooling facility/TCS supply class [ASHRAE W class] default W32 or W45 (illustrative) (ASHRAE TC 9.9 liquid cooling classes; OEM requirement) Rack inlet sensor density [sensors per rack] default 3 (top, middle, bottom; illustrative) (Capability profile; ASHRAE measurement practice) Permitted excursion time outside recommended envelope [hours per year] default per OEM allowable (illustrative: 50) (Capability profile) | Declared envelope per hall/loop; Sensor location map; Twelve months of inlet and supply temperature telemetry; Excursion reports and investigations; Calibration records | ANALYSIS; INSPECTION; RECONCILIATION | 1) Verify envelope declaration and source. 2) Inspect sensor positions in a sample of racks and loops. 3) Recompute excursion statistics from telemetry. 4) Review investigations and calibration. | DETECTIVE | OPERATION | AL4 | COMMISSION; OPERATE; CHANGE | NORMAL; DEGRADED; MAINTENANCE | Applies to all IT spaces and liquid loops in the boundary. |  | CG-06; CG-08 | Return-air sensing masks hot inlets; Coolant supply drift causes accelerator throttling; Rapid temperature change after cooling restart | OperatingState; Resource; EvidenceObject | Desk-based review of records and meter data; no intervention in plant or IT systems. | If inlet sensing is only at return air, record a U8 method UNKNOWN; the OPERATION claim is UNKNOWN for that hall. | ASHRAE TC 9.9 Thermal Guidelines for Data Processing Environments; EN 50600-2-3 (environmental control); ISO/IEC 22237 series | MCF-ENV-002; MCF-THM-008; MCF-THM-022; MCF-CAP-018 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-ENV-002 | ENV | Environmental and Resource Performance | ENV-01 | Environmental operating conditions | Humidity Control | Ensure moisture conditions avoid condensation on liquid-cooled components and pipework, electrostatic discharge risk at low humidity, and corrosion acceleration at high humidity. | The facility operator shall control and monitor dew point and relative humidity in IT spaces within the declared envelope and shall maintain coolant supply temperatures above room dew point by the declared margin wherever uninsulated liquid-cooling components are exposed to room air. The facility operator shall alarm when the margin is lost and shall define the response. | 1) Dew point and RH are monitored in each hall against the declared envelope. 2) Coolant supply temperature minus room dew point is monitored continuously for liquid-cooled halls and is at or above the declared margin for the period. 3) Margin-loss alarms exist with a defined response (raise supply temperature, dehumidify, isolate). 4) Humidification systems, if any, are maintained and water quality is controlled. | Recommended dew point envelope [°C dew point] default -9 to 15, and ≤ 60% RH (ASHRAE TC 9.9 thermal guidelines recommended envelope) Minimum margin of coolant supply temperature above room dew point [K] default 2 (illustrative) (Capability profile; CDU OEM guidance) | Humidity telemetry; Dew point margin trend for liquid-cooled halls; Alarm configuration; Response procedure; Humidifier maintenance records | ANALYSIS; DOCUMENT_REVIEW | 1) Analyse dew point and RH telemetry. 2) Compute coolant-to-dew-point margin. 3) Review alarm and response. | PREVENTIVE | OPERATION | AL4 | DESIGN; OPERATE | NORMAL; DEGRADED | Applies to all IT spaces; margin element applies to liquid-cooled halls. |  | CG-06 | Condensation on cold plates or manifolds; ESD damage at very low humidity; Humidifier contamination | OperatingState; Hazard | Desk-based review of records and meter data; no intervention in plant or IT systems. | If dew point margin is not monitored for a liquid-cooled hall, record a U1 UNKNOWN and refer to THM fluid controls. | ASHRAE TC 9.9 Thermal Guidelines; EN 50600-2-3 (environmental control) | MCF-ENV-001; MCF-THM-011 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-ENV-003 | ENV | Environmental and Resource Performance | ENV-01 | Environmental operating conditions | Particulate and Corrosion | Ensure airborne particulate and gaseous contaminants are controlled so that hardware reliability is not degraded, particularly where economisation or high airflow increases outdoor air exposure. | The facility operator shall measure gaseous corrosivity by copper and silver reactivity coupons or real-time monitors and particulate cleanliness at the declared interval, shall maintain filtration to the declared grade, and shall act when the severity level exceeds the declared class, including restricting economiser operation during external pollution events. | 1) Corrosivity measurements at the declared interval meet the declared severity level. 2) Particulate cleanliness meets the declared ISO 14644-1 class in sampled halls. 3) Filtration grade and replacement intervals are maintained. 4) Economiser operation has a contamination-triggered lockout or procedure. | Gaseous corrosion severity level [ANSI/ISA-71.04 class] default G1 (ASHRAE TC 9.9 gaseous and particulate contamination guidance) Particulate cleanliness [ISO 14644-1 class] default 8 (ASHRAE TC 9.9 contamination guidance) Corrosion coupon interval [months] default 3 (illustrative) (Capability profile) | Coupon or monitor reports; Particulate survey; Filter maintenance records; Economiser control logic or procedure | DOCUMENT_REVIEW; INSPECTION; ANALYSIS | 1) Review coupon and particulate results against classes. 2) Inspect filter condition. 3) Review economiser lockout. | PREVENTIVE | OPERATION | AL4 | OPERATE | NORMAL; DEGRADED | Applies to air-cooled spaces and to air-side portions of liquid-cooled halls; most material for economiser-equipped sites. |  | CG-08 | Sulphur corrosion of PCB traces; Zinc whiskers from raised floor; Wildfire smoke ingress | Hazard; Resource | Coupon placement and retrieval by the operator; assessors do not enter during filter changes. | If no corrosivity measurement exists for an economiser site, record a U1 UNKNOWN. | ANSI/ISA-71.04 (environmental conditions: airborne contaminants); ISO 14644-1 (cleanroom classification); ASHRAE TC 9.9 contamination guidance | MCF-ENV-001; MCF-PHY-002; MCF-CMP-019 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-ENV-004 | ENV | Environmental and Resource Performance | ENV-01 | Environmental operating conditions | Vibration and Acoustic Conditions | Ensure vibration and sound levels do not degrade storage and IT equipment (including acoustic damage to hard disk drives during gaseous suppression discharge), do not exceed occupational noise limits in dense halls, and comply with boundary noise limits in permits. | The facility owner shall specify suppression discharge nozzles and agent release rates that keep sound pressure at storage equipment below the storage OEM threshold, shall measure occupational noise exposure in halls and plant rooms against regulatory action values and provide hearing protection and signage where exceeded, and shall demonstrate that site boundary noise from generators, heat rejection and transformers complies with planning or permit limits. | 1) Suppression nozzle and discharge design addresses acoustic impact on storage, with OEM threshold. 2) Occupational noise surveys exist for dense halls and plant rooms, with controls where action values are exceeded. 3) Boundary noise assessment or monitoring shows compliance with permit limits, including during generator testing. 4) Vibration-sensitive equipment locations are separated or isolated from vibration sources. | Occupational noise lower / upper exposure action values [dB(A) daily exposure] default 80 / 85 (EU Directive 2003/10/EC (noise at work) or national equivalent) Sound pressure limit at storage arrays during discharge [dB] default per storage OEM threshold (Storage OEM guidance; suppression designer) Site boundary noise limit [dB(A)] default per planning or environmental permit (Permit conditions) | Suppression acoustic design note; Occupational noise survey; Boundary noise assessment or monitoring; Permit noise conditions | DOCUMENT_REVIEW; INSPECTION; ANALYSIS | 1) Review suppression acoustic design. 2) Review occupational noise surveys and controls. 3) Review boundary noise evidence against permit. | PREVENTIVE | IMPLEMENTATION | AL3 | DESIGN; BUILD; OPERATE | NORMAL; EMERGENCY; MAINTENANCE | Acoustic suppression elements apply where gaseous suppression protects HDD-based storage; occupational and boundary elements apply to all sites. |  | CG-08 | Inert-gas discharge causes HDD read/write failures; Hearing damage in dense halls; Permit breach from generator test noise | Hazard; Safeguard | Noise measurements in plant rooms require hearing protection; no suppression discharge is initiated for testing. | If the acoustic effect of discharge on storage is unassessed, record a U1 UNKNOWN and refer to STO integrity controls. | EU Directive 2003/10/EC (noise at work); ISO 9613-2 (outdoor sound propagation); ISO 7779 (IT equipment noise measurement) | MCF-PHY-022; MCF-PHY-007; MCF-STO-009 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-ENV-005 | ENV | Environmental and Resource Performance | ENV-02 | Energy performance | PUE Measurement | Ensure power usage effectiveness is measured according to ISO/IEC 30134-2 with a declared measurement category, boundary and period, so that reported values are comparable, traceable and not distorted by metering gaps or boundary choices. | The energy manager shall calculate PUE as annual total facility energy divided by annual IT equipment energy per ISO/IEC 30134-2, shall declare the measurement category and the metering points used for IT energy, shall include all energy sources (grid, on-site generation, fuel for generators), and shall report the value with category, period and data completeness. | 1) PUE uses annual energy (not instantaneous power) over a 12-month period. 2) The ISO/IEC 30134-2 measurement category is declared and IT energy meters match it. 3) All facility energy inputs, including generator fuel energy, are included. 4) Meter accuracy classes and calibration are documented for the meters used. 5) Data completeness is reported and gaps are filled by a documented method. | PUE measurement period [months] default 12 (ISO/IEC 30134-2) PUE measurement category [category] default Category 2 or higher (illustrative) (ISO/IEC 30134-2; capability profile) Revenue/sub-meter accuracy class [class] default 0.5S or better (illustrative) (IEC 62053 series) | PUE calculation workbook; Meter list with category mapping; Meter calibration records; Energy data with completeness report | REPERFORMANCE; RECONCILIATION; DOCUMENT_REVIEW | 1) Reconcile meters to category definition. 2) Reperform PUE from raw meter data. 3) Check inclusion of all energy inputs. 4) Review data gaps and fill method. | DETECTIVE | OPERATION | AL4 | OPERATE | NORMAL | Applies to sites reporting PUE internally or externally; colocation tenants report the provider's value with its basis. |  |  | PUE computed from instantaneous snapshot; Generator fuel energy omitted; IT energy measured at wrong point | EvidenceObject; Resource | Desk-based review of records and meter data; no intervention in plant or IT systems. | If metering does not support the declared category, record a U8 method UNKNOWN and report PUE only with a limitation. | ISO/IEC 30134-2 (power usage effectiveness); EN 50600-4-2 (PUE); IEC 62053 series (electricity metering) | MCF-ENV-006; MCF-ENV-016; MCF-POW-021 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-ENV-006 | ENV | Environmental and Resource Performance | ENV-02 | Energy performance | Energy Allocation | Ensure energy consumed by shared infrastructure is allocated to tenants, clusters or services by a documented and metered method, so that per-capability energy and emissions are defensible. | The energy manager shall define an allocation method for shared facility energy (cooling, losses, lighting, offices) to tenants or AI clusters, shall base allocation on sub-metered data wherever metering exists, and shall report unallocated energy below the declared threshold. | 1) An allocation method is documented and approved. 2) Allocation uses sub-meters for IT load and the best available meters for shared systems. 3) Unallocated energy is below the declared threshold. 4) Allocated totals reconcile to the site total. | Maximum unallocated energy [% of site total] default 2 (illustrative) (Capability profile) | Allocation method; Sub-meter data; Reconciliation to site total | RECONCILIATION; DOCUMENT_REVIEW | 1) Review method. 2) Reconcile allocations to site total. 3) Check unallocated energy. | DIRECTIVE | IMPLEMENTATION | AL3 | DESIGN; OPERATE | NORMAL | Applies to multi-tenant or multi-cluster sites where per-capability energy is reported. |  |  | Allocation does not reconcile; Shared cooling energy allocated by floor area only | Resource; EvidenceObject | Desk-based review of records and meter data; no intervention in plant or IT systems. | If allocation does not reconcile, record a U4 conflicting-evidence UNKNOWN on per-capability energy claims. | ISO/IEC 30134-2; ISO 50001 (energy management systems); GHG Protocol Scope 2 Guidance | MCF-ENV-005; MCF-ENV-013 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-ENV-007 | ENV | Environmental and Resource Performance | ENV-02 | Energy performance | Efficiency Under Load | Ensure facility efficiency is characterised across the load range actually experienced by AI deployments (partial occupancy during ramp-up, variable training load) and that heat reuse, where claimed, is measured. | The energy manager shall report PUE or partial PUE at the declared IT load points, shall document the efficiency curves of major equipment (UPS, chillers, CDUs) at those points, and, where heat is exported for reuse, shall measure exported heat energy and report the energy reuse factor per ISO/IEC 30134-6. | 1) Efficiency is reported at each declared IT load point. 2) Equipment efficiency curves at those points are documented. 3) Where heat reuse is claimed, exported heat is metered with heat meters and ERF calculated. 4) Improvement actions target the load points where the site operates most hours. | IT load points for efficiency characterisation [% of design IT load] default 25 / 50 / 75 / 100 (illustrative) (Capability profile) Energy reuse factor reporting [ratio] default measured annually (ISO/IEC 30134-6) | Load-point efficiency report; Equipment efficiency curves; Heat meter data and ERF calculation | ANALYSIS; DOCUMENT_REVIEW | 1) Review load-point reports. 2) Check heat metering and ERF. 3) Review improvement actions. | DETECTIVE | OPERATION | AL4 | OPERATE | NORMAL | Applies to sites reporting efficiency; ERF element applies only where heat reuse is claimed. |  |  | Efficiency reported only at design load; Heat reuse claimed without metering | Resource; EvidenceObject | Desk-based review of records and meter data; no intervention in plant or IT systems. | If heat reuse is claimed without heat metering, record a U1 UNKNOWN on the ERF claim. | ISO/IEC 30134-6 (energy reuse factor); ISO/IEC 30134-2 (PUE); EN 50600-4-6 | MCF-ENV-005; MCF-ENV-008 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-ENV-008 | ENV | Environmental and Resource Performance | ENV-02 | Energy performance | Resilience-Efficiency Trade-Off | Ensure that efficiency measures (UPS eco-mode, raised supply temperatures, reduced running redundant units, economiser hours, power capping) are evaluated for their effect on power and thermal resilience before adoption, so that efficiency gains do not silently consume resilience. | The facility owner shall require a resilience impact assessment for every efficiency measure affecting power or cooling, reviewed by the electrical and mechanical engineers responsible for CG-05 and CG-06 evidence, stating the effect on transfer behaviour, ride-through, thermal ride-through time and redundancy in each declared operating state. The facility owner shall approve the measure under change control only when the assessment shows declared tolerances are still met. | 1) A register of efficiency measures in use exists with linked resilience impact assessments. 2) Each assessment addresses transfer, ride-through, thermal margin and redundancy by operating state. 3) Assessments were reviewed by the responsible electrical and mechanical engineers. 4) Measures were approved under change control. |  | Efficiency measure register; Resilience impact assessments; Change approvals | DOCUMENT_REVIEW; ANALYSIS; INQUIRY | 1) Identify efficiency measures from configuration (UPS mode, setpoints, staging). 2) Check each has an assessment and approval. 3) Evaluate assessment quality against operating states. | DIRECTIVE | DESIGN | AL2 | DESIGN; CHANGE | NORMAL; DEGRADED; EMERGENCY | Applies to all sites operating any efficiency measure affecting power or cooling. |  | CG-05; CG-06; CG-14 | Eco-mode exposes load to transfer during grid event; Raised supply temperature reduces thermal ride-through below restart time; Redundant chiller switched off for efficiency | Safeguard; OperatingState; FailureScenario | Desk-based review of records and meter data; no intervention in plant or IT systems. | If an efficiency measure is found in configuration without an assessment, record a U1 UNKNOWN and carry it into CG-05/CG-06 gate-level evaluation. | ISO/IEC 30134 series (KPIs); EN 50600-2-2 and EN 50600-2-3; EU Code of Conduct on Data Centre Energy Efficiency (best practice guidelines) | MCF-POW-012; MCF-POW-019; MCF-OPS-018; MCF-THM-003 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-ENV-009 | ENV | Environmental and Resource Performance | ENV-03 | Water performance | Water Source and Quality | Ensure water supplies for heat rejection, adiabatic cooling and humidification are identified, of controlled quality, and treated to prevent scaling, corrosion, biofouling and Legionella risk. | The facility operator shall document each water source (mains, borehole, reclaimed), its contracted or permitted volume and quality, and shall operate a water treatment programme with the declared monitoring frequency for chemistry and microbiology, including a Legionella risk assessment and control scheme for evaporative systems, reviewed by a competent person. | 1) Each water source is documented with volume entitlement and quality. 2) Treatment programme monitoring results are within control limits for the period. 3) A current Legionella risk assessment exists for evaporative and adiabatic systems. 4) Out-of-limit results were acted on within the declared time. | Legionella risk assessment review interval [months] default 24 (illustrative) (National Legionella guidance (e.g. HSE L8, ASHRAE 188); capability profile) | Water source register; Treatment monitoring records; Legionella risk assessment; Corrective action records | DOCUMENT_REVIEW; ANALYSIS | 1) Review source register. 2) Analyse treatment records. 3) Review Legionella assessment and actions. | PREVENTIVE | OPERATION | AL4 | OPERATE | NORMAL; MAINTENANCE | Applies to sites using water for heat rejection or humidification. Closed-loop dry-cooled sites apply the source register element for make-up water only. |  | CG-06; CG-04 | Legionella outbreak from cooling tower; Scaling reduces heat-rejection capacity; Borehole quality change | Resource; Hazard; Dependency | Sampling from evaporative systems requires respiratory protection per the Legionella control scheme; assessors do not sample. | If no Legionella risk assessment exists for an evaporative system, record a U1 UNKNOWN and a Finding referred to CG-04 gate-level evaluation. | ASHRAE 188 (Legionellosis risk management); HSE L8 (Legionnaires' disease control, UK); ISO 14046 (water footprint) | MCF-ENV-010; MCF-THM-018; MCF-THM-015 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-ENV-010 | ENV | Environmental and Resource Performance | ENV-03 | Water performance | WUE Measurement | Ensure water usage effectiveness is measured per ISO/IEC 30134-9 with complete metering of site water inputs, so that water claims are comparable and traceable. | The energy and sustainability manager shall calculate WUE as annual site water use divided by annual IT equipment energy per ISO/IEC 30134-9, shall meter every water input, shall state which uses are included (heat rejection, humidification, domestic) and shall report data completeness. Where source-side water (water used in electricity generation) is reported, the basis shall be stated separately. | 1) All water inputs are metered and reconcile to utility bills. 2) WUE uses annual values and the ISO/IEC 30134-9 definition. 3) Inclusions and exclusions are stated. 4) Source-side water, if reported, is separate with stated basis. | WUE measurement period [months] default 12 (ISO/IEC 30134-9) | Water meter list; Meter data and bills; WUE calculation | REPERFORMANCE; RECONCILIATION | 1) Reconcile meters to bills. 2) Reperform WUE. 3) Check stated inclusions. | DETECTIVE | OPERATION | AL4 | OPERATE | NORMAL | Applies to sites reporting water performance. |  |  | Unmetered borehole abstraction; WUE uses design not measured data | Resource; EvidenceObject | Desk-based review of records and meter data; no intervention in plant or IT systems. | If an input is unmetered, record a U5 coverage UNKNOWN and report WUE with a limitation. | ISO/IEC 30134-9 (water usage effectiveness); EN 50600-4-9 | MCF-ENV-009; MCF-ENV-016 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-ENV-011 | ENV | Environmental and Resource Performance | ENV-03 | Water performance | Water Scarcity Response | Demonstrate that the site maintains heat-rejection capacity for the declared outcomes when water supply is restricted or interrupted, using storage, alternative sources or dry operation with a known capacity penalty. | The facility owner shall maintain a water scarcity response plan stating on-site storage autonomy at design-day consumption, alternative sources, the capacity of heat rejection in water-free or reduced-water mode at design ambient, and the load-reduction actions if that capacity is below the declared IT load. The facility operator shall exercise switchover to reduced-water mode at the declared interval. | 1) On-site water storage autonomy at design-day consumption is calculated and meets the declared value. 2) Heat-rejection capacity in reduced-water mode at design ambient is stated. 3) If that capacity is below IT load, load-reduction actions with MW values are defined. 4) Switchover to reduced-water mode was exercised within the interval. 5) Utility restriction notification arrangements are in place. | On-site water storage autonomy at design-day consumption [hours] default 48 (illustrative) (Capability profile) Heat-rejection capacity in reduced-water mode at design ambient [% of design IT load] default per thermal design (illustrative: 80) (Thermal design basis) | Water scarcity response plan; Storage autonomy calculation; Reduced-water capacity analysis; Exercise records | DOCUMENT_REVIEW; ANALYSIS; SCENARIO_EXERCISE | 1) Review plan. 2) Recompute storage autonomy. 3) Review capacity analysis. 4) Review exercise. | RECOVERY | RESILIENCE | AL5 | PLAN; OPERATE | DEGRADED; EMERGENCY | Applies to sites whose heat rejection depends on water. Not applicable to fully dry-cooled sites, recorded with evidence. |  | CG-06; CG-03 | Water restriction during heatwave (AIDCF-004 X10); Storage depleted before supply restored; Dry-mode capacity unknown | FailureScenario; Resource; Safeguard | Switchover exercises are performed by the operator under method statement with thermal contingency. | If reduced-water capacity is unknown, record a U1 UNKNOWN referred to CG-06. | ISO 22301 (business continuity); ISO 14046 (water footprint) | MCF-ENV-022; MCF-ENV-021; MCF-THM-015; MCF-THM-004 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-ENV-012 | ENV | Environmental and Resource Performance | ENV-03 | Water performance | Discharge Control | Ensure discharges of cooling-tower blowdown, treated water, glycol and stormwater comply with permits and that accidental releases of coolant, fuel or fire-water are contained. | The facility operator shall hold and comply with discharge consents for trade effluent and surface water, shall monitor discharge quality at the declared frequency, shall provide interceptors and containment for fuel, glycol and potentially contaminated fire-fighting water, and shall report permit breaches to the regulator as required. | 1) Current discharge consents exist for each discharge. 2) Monitoring results are within consent limits. 3) Interceptors and containment for fuel, glycol and fire-water are installed and maintained. 4) Permit breaches in the period were reported and corrected. | Discharge monitoring frequency [per consent] default per permit conditions (Discharge consent) | Discharge consents; Monitoring records; Interceptor maintenance records; Breach reports | DOCUMENT_REVIEW; INSPECTION | 1) Review consents. 2) Compare monitoring with limits. 3) Inspect interceptors and containment. | PREVENTIVE | OPERATION | AL4 | DESIGN; OPERATE | NORMAL; EMERGENCY | Applies to all sites with trade effluent or surface water discharge. |  |  | Glycol release to surface water; Fire-water run-off contamination; Biocide over-discharge | Hazard; Safeguard | Interceptor inspection follows confined-space rules where applicable; assessors inspect from surface. | If consents cannot be produced, record a U1 UNKNOWN and a regulatory-compliance Finding. | ISO 14001 (environmental management systems); National environmental permitting regime | MCF-ENV-019; MCF-ENV-009 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-ENV-013 | ENV | Environmental and Resource Performance | ENV-04 | Carbon and resource reporting | Carbon Accounting Boundary | Ensure the organisational and operational boundary for greenhouse gas accounting of AI capability is defined consistently with the GHG Protocol, including colocation, leased and on-site generation emissions, so that carbon usage effectiveness and footprint claims are well-founded. | The sustainability manager shall define the consolidation approach (operational or financial control, or equity share), the Scope 1 (generator fuel, refrigerant leakage), Scope 2 (location-based and market-based) and relevant Scope 3 categories (purchased hardware, construction, upstream fuel) for each site, shall state exclusions with justification, and shall calculate CUE per ISO/IEC 30134-8 on the declared basis. | 1) Consolidation approach and site boundaries are documented. 2) Scope 1 includes generator fuel and refrigerant leakage. 3) Scope 2 is reported on both location-based and market-based methods. 4) Relevant Scope 3 categories are identified with inclusion decisions. 5) CUE basis (emission factor method) is declared. | Materiality threshold for boundary exclusions [% of total emissions] default 5 (illustrative) (Capability profile; GHG Protocol guidance on exclusions) | GHG inventory methodology; Boundary statement; Emission factor sources; CUE calculation | DOCUMENT_REVIEW; ANALYSIS | 1) Review boundary and consolidation approach. 2) Check scope coverage. 3) Review CUE basis. | DIRECTIVE | DESIGN | AL2 | PLAN; OPERATE | NORMAL | Applies wherever carbon or CUE claims are made for the capability. |  |  | Refrigerant leakage excluded from Scope 1; Only market-based Scope 2 reported; Colocation emissions omitted | EvidenceObject; Resource | Desk-based review of records and meter data; no intervention in plant or IT systems. | If the boundary is undefined, record a U9 interpretation UNKNOWN on all carbon claims. | GHG Protocol Corporate Standard and Scope 2 Guidance; ISO 14064-1 (GHG inventories); ISO/IEC 30134-8 (carbon usage effectiveness) | MCF-ENV-014; MCF-ENV-016; MCF-ENV-018 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-ENV-014 | ENV | Environmental and Resource Performance | ENV-04 | Carbon and resource reporting | Energy Attribute Evidence | Ensure claims of renewable or carbon-free electricity are backed by retired energy attribute certificates or contractual instruments matched to consumption by the declared temporal and geographic rules, without double counting. | The sustainability manager shall hold evidence of cancellation or retirement of energy attribute certificates (for example guarantees of origin or RECs) or of contractual instruments (PPAs) for every claimed MWh, shall match them to consumption by the declared temporal granularity (annual or hourly) and market boundary, and shall ensure no instrument is claimed by another party. | 1) Retirement evidence exists for every claimed MWh in the period. 2) Matching follows the declared temporal and geographic rules. 3) PPA volumes are reconciled to delivered generation data. 4) Registry records show retirement on behalf of the claiming entity. | Temporal matching granularity [interval] default annual or hourly (declared) (GHG Protocol Scope 2 Guidance; hourly matching frameworks) | Registry retirement statements; PPA contracts and generation data; Matching analysis | RECONCILIATION; DOCUMENT_REVIEW | 1) Reconcile claimed MWh to retirements. 2) Check matching rules. 3) Reconcile PPA volumes. | DETECTIVE | IMPLEMENTATION | AL3 | OPERATE | NORMAL | Applies where renewable or carbon-free electricity claims are made. |  |  | Certificates not retired; Double-counted PPA output; Hourly claim based on annual matching | EvidenceObject | Desk-based review of records and meter data; no intervention in plant or IT systems. | If retirement cannot be verified in the registry, record a U6 source-unverified UNKNOWN on the claim. | GHG Protocol Scope 2 Guidance; EN 16325 (guarantees of origin); ISO/IEC 30134-3 (renewable energy factor) | MCF-ENV-013; MCF-ENV-016 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-ENV-015 | ENV | Environmental and Resource Performance | ENV-04 | Carbon and resource reporting | Embodied Resource Data | Ensure embodied carbon and material data for buildings, plant and AI hardware are collected on a consistent life-cycle basis so that lifecycle footprint and refresh decisions are informed. | The sustainability manager shall collect embodied-impact data for buildings and major plant from environmental product declarations or LCA studies, and for AI hardware from OEM product carbon footprints, using a documented life-cycle method, and shall report coverage by mass or spend. | 1) A documented LCA method is used (system boundary, life stages, data sources). 2) Coverage of building, plant and hardware by mass or spend meets the declared threshold. 3) Data sources (EPDs, OEM PCFs) are referenced and dated. | Embodied data coverage [% of hardware and plant by spend] default 80 (illustrative) (Capability profile) | LCA method; EPD and PCF register; Coverage calculation | DOCUMENT_REVIEW; ANALYSIS | 1) Review method. 2) Check data sources. 3) Compute coverage. | DIRECTIVE | DESIGN | AL2 | PLAN; DESIGN; DECOMMISSION | NORMAL | Applies where lifecycle or embodied claims are made. |  |  | Embodied claim based on generic factors only; Hardware omitted | EvidenceObject; AssetInstance | Desk-based review of records and meter data; no intervention in plant or IT systems. | If coverage is below threshold, report the claim with a limitation and record a U5 UNKNOWN. | ISO 14040 / ISO 14044 (life cycle assessment); EN 15978 (sustainability of construction works); ISO 14067 (carbon footprint of products) | MCF-ENV-013; MCF-ENV-020 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-ENV-016 | ENV | Environmental and Resource Performance | ENV-04 | Carbon and resource reporting | Reporting Traceability | Ensure every reported environmental metric (energy, PUE, WUE, CUE, REF, ERF, emissions) traces to source meter data and calculation, and that restatements are controlled and disclosed, including for regulatory data-centre reporting. | The sustainability manager shall maintain a reporting register that links each reported metric to its calculation, source data and approver, shall retain data for the declared period, shall restate when errors exceed the declared threshold, and shall meet the content and timing of applicable regulatory reporting (for example EU Energy Efficiency Directive data-centre reporting where in scope). | 1) Each reported metric traces to calculation and source data in the register. 2) A sample of metrics is reperformed from source data within tolerance. 3) Restatements above threshold were made and disclosed. 4) Applicable regulatory reports were submitted on time with required indicators. | Restatement threshold [% change in reported metric] default 5 (illustrative) (Capability profile) | Reporting register; Calculation files; Regulatory submissions; Restatement records | REPERFORMANCE; DOCUMENT_REVIEW; SAMPLING | 1) Sample metrics. 2) Trace to source and reperform. 3) Review restatements and submissions. | DETECTIVE | OPERATION | AL4 | OPERATE | NORMAL | Applies to all externally or regulatorily reported environmental metrics. |  |  | Reported PUE not reproducible; Late regulatory submission; Undisclosed restatement | EvidenceObject; AssuranceReport | Desk-based review of records and meter data; no intervention in plant or IT systems. | If a reported metric cannot be traced to source data, record a U6 UNKNOWN on that metric. | EU Energy Efficiency Directive (EU) 2023/1791 and Delegated Regulation (EU) 2024/1364 (data-centre reporting); ISO/IEC 30134 series; ISO 14064-3 (verification of GHG statements) | MCF-ENV-005; MCF-ENV-010; MCF-ENV-014; MCF-EVA-005 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-ENV-017 | ENV | Environmental and Resource Performance | ENV-05 | Hazardous materials and waste | Battery Materials | Ensure batteries in storage, transport, quarantine and end of life (UPS strings, BESS modules, rack battery backup units, spares) are inventoried, stored at safe state of charge, segregated when damaged and returned or recycled under applicable battery regulation. | The facility operator shall maintain an inventory of batteries held outside service, shall store lithium-ion spares at or below the declared state of charge in a designated, detected and separated location, shall quarantine damaged or swollen cells in a fire-rated container away from critical plant, and shall transfer end-of-life batteries only to authorised recyclers with documentation meeting applicable battery and waste regulation. | 1) An inventory of batteries outside service exists and reconciles to a physical count sample. 2) Lithium-ion spares are stored at or below the declared state of charge in a designated location. 3) A quarantine procedure and fire-rated container exist for damaged cells, with use recorded. 4) End-of-life transfers have waste transfer and recycler authorisation documents. 5) Spare battery storage is not within a compartment containing critical power or IT plant. | Maximum state of charge for stored lithium-ion spares [% SoC] default 30 (illustrative) (OEM guidance; aligns with air-transport limit for UN 3480 lithium-ion batteries) | Battery inventory; Storage location inspection; Quarantine procedure and records; Waste transfer and recycler documents | RECONCILIATION; INSPECTION; DOCUMENT_REVIEW | 1) Reconcile inventory to count sample. 2) Inspect storage and quarantine. 3) Review end-of-life records. | PREVENTIVE | OPERATION | AL4 | OPERATE; DECOMMISSION | NORMAL; MAINTENANCE | Applies to all sites holding batteries outside service. |  | CG-04 | Thermal runaway of fully charged spares in store; Damaged cell left in plant room; Unauthorised disposal | Hazard; AssetInstance; Safeguard | Inspection only; damaged cells are handled only by trained staff with battery-hazard PPE. | If spare battery state of charge is not controlled, record a Finding and a U1 UNKNOWN referred to CG-04 gate-level evaluation. | EU Battery Regulation (EU) 2023/1542; IEC 62619 (safety of industrial lithium batteries); UN Manual of Tests and Criteria (lithium battery transport); NFPA 855 | MCF-POW-010; MCF-PHY-021; MCF-ENV-020 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-ENV-018 | ENV | Environmental and Resource Performance | ENV-05 | Hazardous materials and waste | Refrigerants and Coolants | Ensure refrigerants, glycols and dielectric coolants are inventoried, contained, leak-checked and handled so that toxicity, flammability (including A2L refrigerants), asphyxiation and environmental hazards are controlled for people and plant. | The facility operator shall maintain an inventory of refrigerant charge per system (type, mass, CO2-equivalent, ISO 817/ASHRAE 34 safety class) and of coolants and dielectric fluids, shall leak-check refrigerant systems at the frequencies required by applicable regulation, shall provide refrigerant detection, alarms and ventilation in machinery rooms and occupied spaces where concentration could exceed the practical limit, shall use only certified technicians for refrigerant work, and shall hold safety data sheets and handling procedures for every coolant. | 1) Refrigerant inventory per system includes type, charge, CO2e and safety class. 2) Leak checks occurred at the required frequency, and leaks were repaired and rechecked. 3) Machinery rooms and spaces where the practical limit could be exceeded have detection, alarm and ventilation tested within the interval. 4) A2L or higher-flammability refrigerant installations have the ignition-source and ventilation measures required by the applicable safety standard. 5) Refrigerant work is performed by certified technicians, evidenced in the sample. 6) Coolant and dielectric fluid SDS and handling procedures are available, and spill kits are present. | Refrigerant leak-check frequency [per system] default tiered by CO2e charge per applicable regulation (EU F-gas Regulation (EU) 2024/573 or national equivalent) Refrigerant detector alarm setpoint [% of practical limit or ATEL/ODL] default per EN 378 / ISO 5149 (illustrative: 50% of practical limit) (EN 378 / ISO 5149 refrigerating systems safety) | Refrigerant and coolant inventory; Leak-check records; Detector and ventilation test records; Technician certification records; SDS and handling procedures | DOCUMENT_REVIEW; RECONCILIATION; INSPECTION; TEST | 1) Reconcile inventory to plant nameplates in a sample. 2) Review leak-check records against required frequency. 3) Review detector and ventilation tests; witness an alarm test where possible. 4) Check technician certification and SDS availability. | PREVENTIVE | OPERATION | AL4 | DESIGN; COMMISSION; OPERATE; CHANGE; DECOMMISSION | NORMAL; MAINTENANCE; EMERGENCY | Applies to all sites with refrigerating systems, glycol loops or dielectric immersion fluids. | CG-04 |  | Refrigerant release in machinery room causing asphyxiation; A2L ignition from unrated equipment; Undetected chronic leakage; Dielectric fluid spill and slip/fire hazard | Hazard; Safeguard; AssetInstance | Detector bump tests use certified calibration gas by the contractor; assessors do not enter machinery rooms during alarm without the operator's clearance. | If detection in a machinery room is untested or absent where required, record a US4 UNKNOWN against CG-04. | EN 378 / ISO 5149 (refrigerating systems: safety and environmental requirements); ISO 817 / ASHRAE 34 (refrigerant designation and safety classification); EU F-gas Regulation (EU) 2024/573; ASHRAE 15 (safety standard for refrigeration systems) | MCF-THM-017; MCF-THM-013; MCF-ENV-013; MCF-ENV-019 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-ENV-019 | ENV | Environmental and Resource Performance | ENV-05 | Hazardous materials and waste | Fuel and Suppressant Handling | Ensure generator fuel and fire suppressant agents are stored, contained, transferred and disposed of safely and in compliance with permits, and that suppressant inventory reflects its environmental profile. | The facility operator shall store fuel in tanks with secondary containment of the declared capacity, leak detection and overfill protection, shall control deliveries with a supervised procedure, shall inspect tanks and pipework at the declared interval, and shall maintain an inventory of suppressant agents with their pressure-vessel inspection status and environmental classification, recovering agents through certified contractors. | 1) Fuel tanks have secondary containment of at least the declared capacity, leak detection and overfill protection. 2) Deliveries follow a supervised procedure with spill kit and drain protection. 3) Tank and pipework inspections are current. 4) Suppressant inventory includes agent type, mass, cylinder inspection dates and environmental status. 5) Agent recovery and disposal records exist for removed systems. | Secondary containment capacity [% of largest tank volume] default 110 (illustrative) (Common oil-storage regulation and bunding practice; local permit) | Tank specifications and containment calculations; Delivery procedure and records; Inspection records; Suppressant inventory; Recovery records | DOCUMENT_REVIEW; INSPECTION | 1) Review containment. 2) Review delivery records and inspect fill point. 3) Review suppressant inventory. | PREVENTIVE | OPERATION | AL4 | DESIGN; OPERATE; DECOMMISSION | NORMAL; MAINTENANCE; EMERGENCY | Applies to sites storing fuel or suppressant agents. |  | CG-04 | Fuel spill to drain during delivery; Overfill; Overdue pressure-vessel inspection of agent cylinders | Hazard; Safeguard; Resource | Inspection of fuel areas follows ignition-source controls; assessors do not enter bunds. | If containment capacity cannot be verified, record a U1 UNKNOWN and an environmental Finding. | NFPA 30 (flammable and combustible liquids); National oil-storage and pressure-equipment regulation; ISO 14520 / NFPA 2001 (agent handling) | MCF-POW-007; MCF-ENV-012; MCF-PHY-022 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-ENV-020 | ENV | Environmental and Resource Performance | ENV-05 | Hazardous materials and waste | Hardware and Media Waste | Ensure retired AI hardware, network equipment and media are routed to reuse, refurbishment or authorised recycling with traceable records, after data sanitisation, and in line with waste electrical equipment regulation. | The facility operator shall route retired equipment through the decommissioning custody process (MCF-PHY-020), shall prefer reuse or refurbishment where data and security rules allow, shall transfer waste only to authorised operators with waste transfer documentation, and shall report mass by disposition route. | 1) Retired equipment disposition is recorded per serial and route (reuse, refurbish, recycle). 2) Waste transfers have authorised-operator and transfer documentation. 3) Mass by route is reported for the period. 4) Data sanitisation certificates precede reuse or recycling transfer. |  | Disposition records; Waste transfer notes; Mass report; Sanitisation certificates | SAMPLING; RECONCILIATION | 1) Sample retired serials. 2) Trace to route, transfer notes and certificates. 3) Review mass report. | DIRECTIVE | OPERATION | AL4 | DECOMMISSION | NORMAL | Applies to all equipment retired from the boundary. |  |  | Unauthorised e-waste export; Reuse before sanitisation | AssetInstance; EvidenceObject | Desk-based review of records and meter data; no intervention in plant or IT systems. | If disposition cannot be traced for sampled serials, record a U5 UNKNOWN and a Finding. | EU WEEE Directive 2012/19/EU; NIST SP 800-88 (media sanitisation) | MCF-PHY-020; MCF-ENV-015; MCF-CMP-024 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-ENV-021 | ENV | Environmental and Resource Performance | ENV-06 | Climate adaptation and resource continuity | Heatwave Readiness | Demonstrate that heat rejection, generators, transformers and battery rooms retain the capacity required by declared outcomes during extreme heat at or beyond the design ambient, and that operations has a tested response when forecasts approach design limits. | The facility owner shall state the design extreme ambient used for heat rejection, generator and transformer rating, shall evaluate capacity at that ambient and at the declared climate-adjusted ambient, and shall maintain a heatwave procedure triggered by forecast that includes pre-cooling, cleaning of coils, deferral of maintenance, readiness of mobile plant and workload reduction steps. The facility operator shall exercise the procedure before each hot season. | 1) Design extreme ambient is stated with source (e.g. ASHRAE climatic data n-year value). 2) Capacity of heat rejection, generators and transformers at design and climate-adjusted ambient is evaluated and covers declared load, or the shortfall has defined load reduction. 3) Recirculation of hot air at heat-rejection plant is assessed. 4) A forecast-triggered heatwave procedure exists and was exercised before the hot season. 5) Performance in the last heat event was reviewed with lessons applied. | Design extreme ambient dry-bulb [°C] default site n=20-year extreme (illustrative) (ASHRAE Handbook climatic design data) Climate-adjusted design ambient uplift [K] default 2 (illustrative) (Owner-adopted climate projection (e.g. IPCC AR6 scenario)) Forecast trigger margin below design ambient [K] default 3 (illustrative) (Capability profile) | Design ambient statement; Capacity-at-ambient analysis; Recirculation study; Heatwave procedure; Exercise and event review records | ANALYSIS; DOCUMENT_REVIEW; SCENARIO_EXERCISE | 1) Verify design ambient source. 2) Review capacity analysis. 3) Review procedure and exercise. 4) Review last heat event. | RECOVERY | RESILIENCE | AL5 | DESIGN; OPERATE | DEGRADED; EMERGENCY | Applies to all sites; material where design ambient margin is small or recirculation exists. |  | CG-06; CG-05 | Dry coolers lose capacity above design ambient; Generators derate in heatwave during grid stress; Transformer overheating | Hazard; CapacityAssertion; FailureScenario | Exercises are procedural; no plant is deliberately disabled. | If capacity at design ambient is unevaluated, record a U1 UNKNOWN referred to CG-06 and CG-05. | ASHRAE Handbook - Fundamentals (climatic design conditions); ISO 14090 / ISO 14091 (adaptation to climate change); IPCC AR6 (climate scenarios) | MCF-THM-004; MCF-POW-005; MCF-ENV-011 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-ENV-022 | ENV | Environmental and Resource Performance | ENV-06 | Climate adaptation and resource continuity | Drought Readiness | Ensure long-term water availability risk is assessed for the site's water-dependent cooling, so that water stress does not become a strategic constraint on AI capability. | The facility owner shall assess basin-level water stress over the declared planning horizon using recognised water-risk data and climate projections, shall evaluate the security of water entitlements, and shall define the strategy (alternative sources, technology change, reduced water design) if stress exceeds the declared threshold. | 1) A water-stress assessment covers the planning horizon with stated data sources. 2) Water entitlements and their renewal risks are documented. 3) A strategy exists where stress exceeds threshold. | Water-stress planning horizon [years] default 20 (illustrative) (Capability profile) | Water-stress assessment; Entitlement documents; Strategy | DOCUMENT_REVIEW; ANALYSIS | 1) Review assessment data sources. 2) Review entitlements. 3) Review strategy. | DIRECTIVE | DESIGN | AL2 | PLAN; DESIGN | NORMAL; DEGRADED | Applies to sites with water-dependent cooling. |  | CG-03 | Entitlement withdrawn; Basin stress forces cooling retrofit | Dependency; Resource; Hazard | Desk-based review of records and meter data; no intervention in plant or IT systems. | If no water-stress assessment exists, record a U1 UNKNOWN on long-term water dependency. | WRI Aqueduct water-risk atlas; ISO 14046 (water footprint); ISO 14091 (climate risk assessment) | MCF-ENV-011; MCF-ENV-024; MCF-DEP-009 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-ENV-023 | ENV | Environmental and Resource Performance | ENV-06 | Climate adaptation and resource continuity | Flood Adaptation | Ensure that flood protection for critical plant remains adequate under projected climate change and that temporary flood defences are deployable in time. | The facility owner shall evaluate flood levels under the declared climate scenario and horizon, shall confirm critical plant remains above the adjusted design level plus freeboard or is protected by permanent or demountable defences, and shall maintain a flood response plan with deployment time for demountable defences shorter than the warning lead time. | 1) Climate-adjusted flood levels are evaluated for the declared scenario and horizon. 2) Critical plant is above adjusted level plus freeboard, or defended. 3) Demountable defence deployment time is shorter than warning lead time, demonstrated by drill. 4) Drainage and pumping capacity is evaluated for adjusted rainfall intensity. | Climate scenario and horizon for flood adaptation [scenario / year] default SSP2-4.5 to 2060 (illustrative) (IPCC AR6 scenarios; owner-adopted projection) Demountable defence deployment time [hours] default less than flood warning lead time (illustrative: 4) (Flood response plan) | Climate-adjusted flood assessment; Plant level survey; Flood response plan; Drill records | DOCUMENT_REVIEW; ANALYSIS; INSPECTION | 1) Review adjusted flood assessment. 2) Compare plant levels. 3) Review drill records. | PREVENTIVE | DESIGN | AL2 | PLAN; DESIGN; OPERATE | NORMAL; EMERGENCY | Applies to all sites with any flood exposure identified in MCF-PHY-001. |  | CG-09 | Climate-driven flood exceeds original design level; Defences not deployed in time (AIDCF-004 X20) | Hazard; Safeguard; FailureScenario | Drills of demountable defences follow manual-handling procedures. | If climate-adjusted flood levels are not evaluated, record a U1 UNKNOWN and limit flood protection claims to current hazard levels. | ISO 14090 / ISO 14091; IPCC AR6; National flood-risk guidance | MCF-PHY-001; MCF-PHY-008; MCF-RES-003 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-ENV-024 | ENV | Environmental and Resource Performance | ENV-06 | Climate adaptation and resource continuity | Long-Term Resource Constraints | Ensure long-term constraints on grid capacity, water, permits and land that could limit growth or continuation of AI capability at the site are identified, owned and fed into capacity planning. | The facility owner shall maintain a resource constraints register covering grid capacity availability and reinforcement timelines, water entitlement, environmental permits and their renewal dates, planning constraints and emission limits, over the declared horizon, and shall review it with capability owners when demand forecasts change. | 1) The register covers grid, water, permit, planning and emission constraints with dates. 2) Each constraint has an owner and mitigation. 3) The register was reviewed with capability owners after the last demand forecast change. | Resource planning horizon [years] default 15 (illustrative) (Capability profile) | Resource constraints register; Permit list with renewal dates; Review minutes | DOCUMENT_REVIEW; INQUIRY | 1) Review register coverage. 2) Check owners and mitigations. 3) Confirm review with capability owners. | DIRECTIVE | DESIGN | AL2 | PLAN | NORMAL | Applies to all sites with planned growth or long-lived capability. |  | CG-01; CG-03 | Expansion blocked by grid reinforcement delay; Permit lapses; Emission cap limits generator testing | Dependency; Resource; CapacityAssertion | Desk-based review of records and meter data; no intervention in plant or IT systems. | If permit renewal dates are unknown, record a U1 UNKNOWN on resource continuity. | ISO 14001 (environmental management); ISO 50001 (energy management) | MCF-POW-001; MCF-ENV-022; MCF-CAP-015 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-CMP-001 | CMP | AI Compute Infrastructure | CMP-01 | Compute architecture and configuration | Accelerator Architecture | Establish a documented, approved accelerator architecture that links the Capability Instance's workload (training, fine-tuning, inference) to the accelerator type, memory capacity and bandwidth, scale-up domain size, scale-out fabric, power and cooling envelope, so that compute is sized and constrained by the Service Outcome rather than by procurement availability. | The compute engineering authority shall maintain an accelerator architecture record per cluster stating accelerator model and generation, accelerator memory capacity and bandwidth, scale-up domain size and interconnect, host CPU and memory ratio, scale-out network attachment per accelerator, per-node and per-rack power and heat, and the cooling method required. The AI platform owner shall approve the record and shall confirm its sufficiency against the performance and integrity outcomes defined for the Capability Instance. | 1) An approved architecture record exists per cluster with the attributes listed in the requirement. 2) Each attribute traces to a workload requirement (model size, parallelism strategy, sequence length, throughput or latency target). 3) Power and heat per rack in the record reconcile with the facility heat-load model (MCF-THM-001) and power budget. 4) Scale-up and scale-out attachment ratios are stated and match the fabric design (NET-01). 5) Mixed-generation or heterogeneous accelerators, where present, are identified with their scheduling constraints. 6) Known platform limitations and OEM errata relevant to the outcome are recorded. | Accelerators per scale-up domain [count] default platform-specific (illustrative: 8 node-scale; 72 rack-scale) (Platform OEM architecture) Scale-out bandwidth per accelerator [Gb/s] default 400 (illustrative) (Fabric design; platform OEM reference architecture) Rack power envelope [kW] default 120 (illustrative) (Platform OEM data; facility power budget) | Approved accelerator architecture record; Workload requirement statement linked to the Service Outcome; OEM reference architecture or design guide; Reconciliation with facility power and heat budgets | DOCUMENT_REVIEW; ANALYSIS; INQUIRY; RECONCILIATION | 1) Obtain the architecture record and workload statement. 2) Trace each attribute to a workload requirement. 3) Reconcile rack power and heat with facility budgets. 4) Check consistency with fabric design. 5) Record untraced attributes as Findings and missing workload inputs as UNKNOWN Records. | DIRECTIVE | DESIGN | AL2 | PLAN; DESIGN; CHANGE | NORMAL; TRANSITION | Applies to every in-scope accelerator cluster, owned or provider-operated. For cloud capacity consumed as a service, applies to the provider's documented architecture to the extent the service interface discloses it, with residual items recorded as UNKNOWN. |  | CG-08; CG-01 | Accelerator memory insufficient for model/parallelism plan; Scale-up domain smaller than tensor-parallel group; Rack power exceeding facility budget; Undeclared heterogeneous fleet | InfrastructureSystem; ArchitectureSnapshot; CapacityAssertion; RequiredFunction | Desk-based review; no system access needed. | If workload requirements are not defined, record a U1 UNKNOWN linked to CG-01; architecture sufficiency cannot be judged. | AIDCF-013 (AI Data Centre Assurance Reference Architecture); MLCommons MLPerf Training and Inference benchmark rules; Open Compute Project hardware management and fault-management specifications | MCF-CMP-003; MCF-CMP-005; MCF-THM-001; MCF-NET-001 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-CMP-002 | CMP | AI Compute Infrastructure | CMP-01 | Compute architecture and configuration | Node Configuration | Ensure each compute node's hardware and low-level configuration (BIOS/UEFI settings, BMC configuration, PCIe topology, NUMA and accelerator affinity, NIC attachment, power and thermal limits) matches the approved node specification, because silent configuration drift degrades performance and reliability of collective workloads. | The AI platform operator shall define a node configuration specification per node type and shall verify, at provisioning and at a defined interval, that every node conforms, using automated collection from the BMC (for example via Redfish) and host OS. The AI platform operator shall secure BMC interfaces with unique credentials, management-network isolation and logged access. | 1) A node configuration specification exists per node type covering BIOS/UEFI, BMC, PCIe/NUMA topology, accelerator power limits and NIC mapping. 2) Automated conformance collection covers ≥ the declared percentage of nodes and runs at the declared interval. 3) Nonconforming nodes are quarantined or remediated within the declared time. 4) BMCs use unique credentials, are reachable only from the management network, and access is logged. 5) Accelerator power and clock limits set in configuration match the facility power and thermal envelope. | Configuration conformance coverage [% of nodes] default 100 (illustrative) (Capability profile) Conformance scan interval [days] default 7 (illustrative) (Capability profile) Nonconforming node remediation time [days] default 3 (illustrative) (Capability profile) | Node configuration specification; Automated conformance report (per-node); Quarantine/remediation records; BMC credential and network-isolation configuration; BMC access logs | RECONCILIATION; SAMPLING; REPERFORMANCE; INSPECTION | 1) Obtain specification and latest conformance reports. 2) Reperform collection on a sample of nodes. 3) Check remediation of nonconforming nodes. 4) Review BMC isolation and access logs. | PREVENTIVE | IMPLEMENTATION | AL3 | BUILD; COMMISSION; OPERATE; CHANGE | NORMAL; MAINTENANCE | Applies to all in-scope compute nodes. For provider-managed nodes, applies to the evidence the provider supplies under its service obligations. |  | CG-08; CG-15 | NUMA/PCIe misaffinity degrading bandwidth; Accelerator power limit above rack budget; Default BMC credentials; Configuration drift after RMA | AssetInstance; ArchitectureSnapshot; Interface | Read-only collection; no configuration changes by the assessor. BMC access uses a read-only account authorised by the operator. | If conformance collection covers less than the target population, record U5 coverage-gap UNKNOWN for the uncovered nodes. | DMTF Redfish (platform management API); NIST SP 800-128 (security-focused configuration management); NIST SP 800-147B (BIOS protection guidelines for servers) | MCF-CMP-004; MCF-CMP-013; MCF-SEC-003; MCF-NET-013 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-CMP-003 | CMP | AI Compute Infrastructure | CMP-01 | Compute architecture and configuration | Rack-Scale Composition | Ensure rack-scale systems (integrated compute trays, scale-up switch trays, power shelves, busbars, liquid manifolds) are composed, connected and accepted as a unit, with their facility interfaces (power, liquid, network, weight) verified against the facility design. | The AI platform operator shall maintain a rack-scale composition record for each rack type (trays, switch trays, power shelves, manifold and QD layout, cable/backplane mapping) and shall verify each installed rack at acceptance. The facility operator and AI platform operator shall jointly sign the facility interface checklist covering power feeds, liquid connections and flow, floor loading and network uplinks before energisation. | 1) A composition record exists per rack type and matches OEM configuration. 2) Each installed rack has an acceptance record including tray inventory and scale-up interconnect validation. 3) A joint facility interface checklist (power, liquid, structural, network) is signed before energisation. 4) Rack power shelf redundancy and feed assignment match the electrical design. 5) Rack weight and point loads are within the floor or slab rating. | Rack weight [kg] default platform-specific (illustrative 1,500) (Platform OEM data; structural rating) | Rack composition record; Per-rack acceptance records; Joint facility interface checklists; Power feed assignment register; Structural load check | INSPECTION; DOCUMENT_REVIEW; RECONCILIATION; SAMPLING | 1) Sample racks and obtain acceptance records. 2) Inspect rack against composition record. 3) Review signed interface checklists. 4) Reconcile feed assignments with the electrical design. | PREVENTIVE | IMPLEMENTATION | AL3 | BUILD; COMMISSION; CHANGE | NORMAL; TRANSITION | Applies to integrated rack-scale systems and to conventional racks with liquid or high-power facility interfaces. |  | CG-08; CG-06; CG-05 | Both power shelves fed from same upstream source; Manifold connected without flow verification; Tray missing or mis-slotted; Floor overload | AssetInstance; Interface; InfrastructureSystem | Inspection of energised racks follows the site electrical safety rules; assessors do not open trays or power shelves. | If no joint interface checklist exists for a rack, record U1 UNKNOWN and reference the corresponding THM and POW controls. | AIDCF-013 (AI Data Centre Assurance Reference Architecture); Open Compute Project hardware management and fault-management specifications; IEC 62368-1 (audio/video, information and communication technology equipment safety) | MCF-CMP-001; MCF-THM-009; MCF-THM-012; MCF-PHY-006 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-CMP-004 | CMP | AI Compute Infrastructure | CMP-01 | Compute architecture and configuration | Approved Baseline | Maintain a single, approved, version-controlled compute baseline (hardware bill of materials, firmware set, driver and runtime stack, OS image, configuration) against which every node can be reconciled and every change can be measured. | The AI platform operator shall publish an approved compute baseline per node type that enumerates hardware components, firmware versions, driver and runtime versions, OS image hash and configuration profile, shall approve changes to it under change control, and shall reconcile the deployed fleet to it continuously, reporting the fraction of nodes on the current baseline. | 1) An approved baseline exists per node type with versioned components and image hashes. 2) Baseline changes have change records with approval. 3) Fleet reconciliation reports show the fraction of nodes on the current baseline and the age of exceptions. 4) Exceptions are approved with expiry dates. 5) The baseline is linked to the Capability Instance's architecture snapshot. | Fleet on current baseline [% of nodes] default 98 (illustrative) (Capability profile) Maximum exception age [days] default 30 (illustrative) (Capability profile) | Approved baseline manifest; Change records for baseline updates; Fleet reconciliation report; Exception register | RECONCILIATION; DOCUMENT_REVIEW; SAMPLING | 1) Obtain baseline manifest and change history. 2) Reconcile node sample to manifest. 3) Review exceptions and their expiry. 4) Link baseline to architecture snapshot. | PREVENTIVE | IMPLEMENTATION | AL3 | BUILD; OPERATE; CHANGE | NORMAL; MAINTENANCE; TRANSITION | Applies to all in-scope compute fleets. |  | CG-02; CG-08; CG-14 | Untracked component substitution; Mixed images across a training partition; Expired exceptions persisting | ArchitectureSnapshot; AssetInstance; InfrastructureSystem | Read-only reconciliation. | If no approved baseline exists, record U1 UNKNOWN against this control and against MCF-CMP-013/014. | NIST SP 800-128 (security-focused configuration management); ISO/IEC 19770 series (IT asset management); ISO/IEC 20000-1 (service management system requirements) | MCF-CMP-013; MCF-CMP-014; MCF-OPS-017; MCF-SUP-012 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-CMP-005 | CMP | AI Compute Infrastructure | CMP-02 | Cluster and scale-up domains | Cluster Topology | Document the cluster topology (nodes, scale-up domains, scale-out rails, storage attachment, management plane) so that job placement, failure analysis and capacity statements can be reasoned about against physical and logical locality. | The AI platform operator shall maintain a machine-readable cluster topology describing node-to-scale-up-domain membership, node-to-rail and leaf mapping, rack, power and cooling domain of every node, and storage and management attachment. The compute engineering authority shall reconcile the topology with the fabric (NET-01) and facility models at each change. | 1) A machine-readable topology exists and covers all in-scope nodes. 2) Each node's scale-up domain, fabric rail/leaf, rack, power feed group and cooling loop are recorded. 3) Topology reconciles with fabric and facility records for a sample. 4) The scheduler's topology view matches the documented topology. 5) Topology version is linked to the architecture snapshot. |  | Machine-readable topology export; Reconciliation report against fabric and facility models; Scheduler topology configuration | DOCUMENT_REVIEW; RECONCILIATION; ANALYSIS | 1) Obtain topology export. 2) Reconcile a sample against fabric discovery and facility registers. 3) Compare with scheduler topology. 4) Record mismatches. | DIRECTIVE | DESIGN | AL2 | DESIGN; BUILD; CHANGE | NORMAL; TRANSITION | Applies to all multi-node accelerator clusters. |  | CG-08; CG-02 | Scheduler unaware of rack/power domains; Topology stale after expansion; Rail mis-mapping | ArchitectureSnapshot; InfrastructureSystem; FaultDomain | Desk-based; read-only exports. | Nodes absent from the topology are recorded as U5 coverage-gap UNKNOWN. | AIDCF-013 (AI Data Centre Assurance Reference Architecture); Open Compute Project hardware management and fault-management specifications | MCF-CMP-008; MCF-CMP-010; MCF-NET-001; MCF-NET-004 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-CMP-006 | CMP | AI Compute Infrastructure | CMP-02 | Cluster and scale-up domains | Scale-Up Domain Integrity | Ensure each scale-up domain (the accelerator group joined by the high-bandwidth, low-latency interconnect, from a single node to a rack-scale domain) delivers its rated bandwidth with all links and switches healthy, and that a degraded domain is detected and withdrawn before it slows or corrupts a training job. | The AI platform operator shall validate every scale-up domain at acceptance and at a defined interval by running an all-to-all or all-reduce bandwidth test against the platform's rated performance, shall monitor interconnect link errors, retrains and lane degradation continuously, and shall automatically drain domains that fall below the declared bandwidth threshold or exceed the link-error threshold. | 1) Acceptance bandwidth tests for each scale-up domain meet the declared fraction of rated bandwidth. 2) Periodic re-validation runs at the declared interval with results recorded. 3) Link error, retrain and lane-width telemetry is collected for every domain. 4) Drain automation triggers on threshold breach and has been observed to work (test or real event). 5) Domains returned to service after repair pass the bandwidth test. | Minimum scale-up bandwidth [% of rated all-reduce bandwidth] default 90 (illustrative) (Platform OEM performance data; capability profile) Re-validation interval [days] default 30 (illustrative) (Capability profile) Link-error drain threshold [errors per hour per link] default platform-specific (Platform OEM RAS guidance) | Acceptance bandwidth test results per domain; Periodic re-validation results; Link-error telemetry; Drain automation configuration and event log; Return-to-service test results | TEST; REPERFORMANCE; ANALYSIS; SAMPLING | 1) Sample scale-up domains across racks. 2) Review acceptance and periodic test results. 3) Reperform the bandwidth test on idle sampled domains. 4) Analyse link-error telemetry and drain events. 5) Check return-to-service evidence. | DETECTIVE | EFFECTIVENESS | AL5 | COMMISSION; OPERATE; CHANGE | NORMAL; DEGRADED; RECOVERY | Applies to all accelerator platforms with a scale-up interconnect. For single-accelerator nodes with no scale-up domain, record NOT_APPLICABLE with rationale. | CG-08 | CG-09 | Degraded lane width halving bandwidth; Switch tray fault isolating part of domain; Intermittent link errors causing job hangs; Domain returned to service without retest | FaultDomain; InfrastructureSystem; TestRecord; FailureMode | Bandwidth tests run only on drained domains with operator authorisation. Draining nodes or partitions removes capacity from production jobs; the AI platform operator's change authority and job-owner notification are required. | If no re-validation within interval exists for a domain, record U3 stale UNKNOWN for that domain. | Open Compute Project hardware management and fault-management specifications; MLCommons MLPerf Training and Inference benchmark rules; PCI Express Base Specification (Advanced Error Reporting) | MCF-CMP-005; MCF-CMP-019; MCF-CMP-023; MCF-NET-008 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-CMP-007 | CMP | AI Compute Infrastructure | CMP-02 | Cluster and scale-up domains | Partitioning | Ensure logical partitions of the cluster (tenant, project, production versus test, accelerator partitioning such as multi-instance modes) are enforced so that one partition's jobs, faults or administrators cannot consume, disrupt or read another's resources. | The AI platform operator shall define partitions with membership, quotas, network and storage isolation, and administrator scope, shall enforce them in the scheduler, fabric and storage configuration, and shall verify enforcement after each change. Where accelerator-level partitioning is used, the AI platform operator shall document its isolation properties as stated by the OEM. | 1) Partition definitions exist with membership, quotas and admin scope. 2) Scheduler configuration enforces partition boundaries (verified by configuration review and a negative test). 3) Network and storage isolation for each partition is configured and reconciled. 4) Accelerator-level partition isolation properties are documented from OEM sources. 5) Partition changes have change records and post-change verification. |  | Partition definitions; Scheduler, fabric and storage configuration exports; Negative test record (job cannot use other partition's nodes); OEM isolation documentation | RECONCILIATION; TEST; DOCUMENT_REVIEW | 1) Obtain definitions and configurations. 2) Reconcile across scheduler, fabric and storage. 3) Run or review the negative test. 4) Review OEM isolation statements. | PREVENTIVE | IMPLEMENTATION | AL3 | DESIGN; BUILD; CHANGE | NORMAL; MAINTENANCE | Applies where more than one tenant, project or environment shares the cluster. |  | CG-09; CG-15 | Job escapes partition quota; Storage namespace shared unintentionally; Partition admin with cluster-wide rights | FaultDomain; Interface; Safeguard | Negative tests use a test account and minimal resources; no attempt to access other tenants' data. | If isolation in any layer cannot be evidenced, record UNKNOWN for that layer and do not assert partition isolation. | NIST SP 800-128 (security-focused configuration management); ISO/IEC 27001 (information security management systems) | MCF-CMP-010; MCF-NET-012; MCF-STO-012; MCF-SEC-006 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-CMP-008 | CMP | AI Compute Infrastructure | CMP-02 | Cluster and scale-up domains | Fault-Domain Design | Ensure the cluster is laid out so that loss of any single facility or infrastructure fault domain (rack, power feed group, CDU loop, leaf switch, scale-up domain) removes no more than the declared fraction of capacity and does not halt the Service Outcome beyond tolerance. | The compute engineering authority shall map each compute node to its facility and infrastructure fault domains, shall limit the fraction of a Capability Instance's capacity in any single fault domain to the declared maximum, and shall demonstrate, by controlled drain or real event, that loss of a representative fault domain is contained and that jobs resume on remaining capacity within the recovery tolerance. | 1) Every node is mapped to rack, power group, cooling loop, leaf and scale-up domain. 2) The largest fraction of capacity in any single fault domain is computed and is within the declared maximum. 3) Shared fault domains between nominally independent partitions are identified. 4) A controlled fault-domain drain or real event demonstrated containment and job resumption within tolerance. 5) The scheduler is configured to spread or co-locate according to the fault-domain policy. | Maximum capacity fraction in a single facility fault domain [% of Capability Instance accelerators] default 25 (illustrative) (Capability profile; outcome tolerance) Job resumption time after fault-domain loss [min] default 60 (illustrative) (Capability profile; checkpoint interval) | Node-to-fault-domain mapping; Fault-domain concentration analysis; Drain test or incident record with timeline; Scheduler placement policy | ANALYSIS; RECONCILIATION; SCENARIO_EXERCISE; TEST | 1) Obtain mapping and reconcile with facility and fabric data. 2) Recompute concentration per fault domain. 3) Review drain test or incident timeline. 4) Review scheduler placement policy. 5) Record exceedances. | PREVENTIVE | RESILIENCE | AL5 | DESIGN; COMMISSION; OPERATE; CHANGE | NORMAL; DEGRADED; FAILED; RECOVERY | Applies to all in-scope clusters. For a single-rack deployment, the control evaluates whether the outcome tolerates loss of the whole cluster. | CG-09 | CG-08; CG-03 | All scale-up domains of a job in one CDU loop; Capacity concentrated on a single power feed group; Hidden shared leaf between partitions | FaultDomain; Dependency; FailureScenario; CapacityAssertion | Controlled drains are capability-affecting. Draining nodes or partitions removes capacity from production jobs; the AI platform operator's change authority and job-owner notification are required. No facility fault (power or cooling) is induced for this control. | If node-to-facility-fault-domain mapping is incomplete, record U10 dependency UNKNOWN and US4 against CG-09. | AIDCF-004 (Threat, Hazard and Failure Model); AIDCF-013 (AI Data Centre Assurance Reference Architecture); Uptime Institute Tier Standard: Topology | MCF-CMP-005; MCF-NET-004; MCF-RES-005; MCF-RES-007 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-CMP-009 | CMP | AI Compute Infrastructure | CMP-03 | Capacity, scheduling and utilisation | Usable Accelerator Capacity | Measure the accelerator capacity actually usable by the Capability Instance (healthy, schedulable, at rated performance, not thermally or power-throttled) and compare it with the capacity the outcome requires, rather than reporting installed accelerator count. | The AI platform operator shall compute and report, at least daily, usable accelerator capacity as installed accelerators minus those drained, failed, quarantined, under repair, reserved, or throttled below the declared performance threshold, and shall compare it with the outcome's required capacity. The AI platform owner shall be notified when usable capacity falls below the required level. | 1) The usable-capacity definition excludes drained, failed, quarantined, repair, reserved and throttled accelerators. 2) Usable capacity is reported at least daily for the period. 3) Usable capacity is compared with required capacity and breaches are notified to the AI platform owner. 4) Thermal or power throttling is counted using accelerator telemetry, not inferred. 5) Reported usable capacity reconciles with scheduler state on a sampled day. | Required usable capacity [% of installed accelerators] default 92 (illustrative) (Capability profile; Service Outcome) Throttle performance threshold [% of rated clock or throughput] default 95 (illustrative) (Capability profile) | Usable-capacity definition and calculation; Daily usable-capacity reports; Notification records; Throttle telemetry; Scheduler state snapshot for reconciliation | ANALYSIS; RECONCILIATION; SAMPLING | 1) Review the calculation definition. 2) Analyse 90-day trend against required capacity. 3) Reconcile a sampled day to scheduler state and telemetry. 4) Review notifications for breaches. | DETECTIVE | OPERATION | AL4 | OPERATE | NORMAL; DEGRADED; MAINTENANCE | Applies to all in-scope accelerator capacity. | CG-08 | CG-01 | Installed count reported as usable; Throttled accelerators masked; Long-running quarantines eroding capacity | CapacityAssertion; Resource; EvidenceObject | Read-only data analysis. | If throttling cannot be measured, record U5 UNKNOWN; usable capacity cannot be asserted above the unthrottled-unknown fraction. | ISO/IEC 20000-1 (service management system requirements); MLCommons MLPerf Training and Inference benchmark rules | MCF-CMP-017; MCF-CMP-018; MCF-CAP-013; MCF-OPS-021 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-CMP-010 | CMP | AI Compute Infrastructure | CMP-03 | Capacity, scheduling and utilisation | Scheduler Controls | Ensure the workload scheduler (for example Slurm or Kubernetes-based schedulers) enforces placement, priority, quota, topology-awareness and health-gating so that jobs land only on healthy nodes in the right topology and privileged scheduler functions are restricted. | The AI platform operator shall configure the scheduler to admit jobs only to nodes passing health checks, to apply topology-aware placement for scale-up and rail locality, to enforce quotas and priorities per partition, and shall restrict scheduler administrative actions (drain, reservation, priority override) to authorised roles with logging. The scheduler control plane shall have documented high availability. | 1) Health-gating is configured so failed or quarantined nodes are not schedulable. 2) Topology-aware placement is configured consistent with MCF-CMP-005. 3) Quotas and priorities per partition are configured and match policy. 4) Administrative actions require authorised roles and are logged. 5) Scheduler controller high availability is configured and has been failed over (test or event). | Scheduler controller failover time [s] default 60 (illustrative) (Capability profile) | Scheduler configuration export; Health-gating rules; Role and permission configuration; Admin action logs; Controller failover record | RECONCILIATION; DOCUMENT_REVIEW; SAMPLING | 1) Obtain configuration export. 2) Verify health-gating and topology rules. 3) Sample admin logs for authorisation. 4) Review failover evidence. | PREVENTIVE | IMPLEMENTATION | AL3 | BUILD; OPERATE; CHANGE | NORMAL; DEGRADED; MAINTENANCE | Applies to all in-scope job schedulers and orchestrators. |  | CG-08; CG-15 | Jobs scheduled onto failing node; Topology-blind placement degrading collectives; Unauthorised priority override; Scheduler controller single point of failure | InfrastructureSystem; Safeguard; Interface | Read-only; no scheduler changes by the assessor. Failover tests only with operator authorisation. | If admin logs are unavailable, record U1 UNKNOWN for administrative-control assertions. | NIST SP 800-128 (security-focused configuration management); ISO/IEC 20000-1 (service management system requirements) | MCF-CMP-005; MCF-CMP-018; MCF-SEC-006; MCF-SEC-003 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-CMP-011 | CMP | AI Compute Infrastructure | CMP-03 | Capacity, scheduling and utilisation | Resource Reservation | Ensure capacity required for priority outcomes, hot spares and recovery (re-running from checkpoint after failure) is reserved and actually available when needed, rather than consumed by lower-priority work. | The AI platform operator shall reserve accelerator capacity for declared priority outcomes and for recovery (hot spare nodes or scale-up domains), shall verify daily that reservations are intact and healthy, and shall be able to reclaim reserved capacity from lower-priority jobs within the declared time. | 1) Reservations for priority outcomes and recovery are defined with sizes. 2) Daily verification shows reserved capacity is healthy and available. 3) Reclaim from lower-priority jobs works within the declared time (test or event). 4) Reservation size is justified against failure rates and recovery needs. | Recovery reserve [% of job size] default 5 (illustrative) (Capability profile; observed node failure rate) Reclaim time [min] default 15 (illustrative) (Capability profile) | Reservation definitions; Daily reservation health reports; Reclaim test or event record; Sizing rationale | ANALYSIS; SAMPLING; DOCUMENT_REVIEW | 1) Review definitions and sizing. 2) Analyse daily health reports. 3) Review reclaim evidence. | PREVENTIVE | OPERATION | AL4 | OPERATE; CHANGE | NORMAL; DEGRADED; RECOVERY | Applies where priority outcomes or recovery depend on reserved compute. |  | CG-10; CG-08 | Reserve nodes unhealthy when needed; Reserve consumed by preemptible jobs not reclaimed; Reserve undersized for failure rate | CapacityAssertion; Resource; Safeguard | Reclaim tests preempt jobs; job-owner notification required. | If reservation health is not verified, record U5 UNKNOWN for recovery-capacity assertions. | ISO/IEC 20000-1 (service management system requirements) | MCF-CMP-009; MCF-CMP-023; MCF-RES-010; MCF-STO-018 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-CMP-012 | CMP | AI Compute Infrastructure | CMP-03 | Capacity, scheduling and utilisation | Contention Management | Detect and manage contention for shared resources (accelerators, fabric, storage bandwidth, power caps) so that one workload's demand does not degrade another priority outcome beyond tolerance, including coordinated facility power capping. | The AI platform operator shall define contention policies (preemption, fair share, bandwidth QoS, power-cap allocation), shall monitor indicators of contention (queue wait, job slowdown, fabric and storage saturation), and shall act when priority outcomes degrade beyond tolerance. Where facility-driven power capping is used, the AI platform operator and facility operator shall agree the capping protocol and its effect on priority outcomes. | 1) Contention policies are documented and configured. 2) Contention indicators are monitored with thresholds. 3) Events where priority outcomes degraded show timely action. 4) Facility power-capping protocol is agreed and exercised where used. | Priority job slowdown tolerance [% versus baseline] default 10 (illustrative) (Capability profile) | Contention policy; Monitoring dashboards and thresholds; Contention event records; Power-capping protocol and exercise | ANALYSIS; DOCUMENT_REVIEW; INQUIRY | 1) Review contention policies and their configuration. 2) Analyse queue-wait, slowdown and saturation indicators for the period. 3) Review handling of events where priority outcomes degraded. 4) Review the facility power-capping protocol and its last exercise. | CORRECTIVE | OPERATION | AL4 | OPERATE; CHANGE | NORMAL; DEGRADED; EMERGENCY | Applies to shared clusters and to clusters subject to facility power capping. |  | CG-08 | Storage saturation by one job stalling others; Uncoordinated power capping slowing priority training; Starvation of priority queue | Resource; Safeguard; OperatingState | Analysis only. | If contention indicators are not collected, record U1 UNKNOWN for performance-outcome assertions. | ISO/IEC 20000-1 (service management system requirements) | MCF-CMP-009; MCF-STO-008; MCF-NET-007; MCF-POW-020 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-CMP-013 | CMP | AI Compute Infrastructure | CMP-04 | Firmware, driver and compatibility | Firmware Baseline | Ensure firmware on accelerators, NICs, BMCs, BIOS/UEFI, interconnect switches and power shelves is at approved, authenticated versions across the fleet, because firmware mismatch is a common-mode source of hangs, errors and security exposure. | The AI platform operator shall maintain an approved firmware matrix per node and rack type, shall verify signature or provenance of each firmware image before deployment, shall measure firmware versions across the fleet automatically, and shall remediate drift within the declared time. Where the platform supports it, the AI platform operator shall use device attestation (for example SPDM measurements or TPM-based measured boot) to confirm firmware identity. | 1) An approved firmware matrix exists covering every firmware-bearing component class. 2) Firmware image provenance or signature is verified before deployment. 3) Automated inventory covers the declared fraction of the fleet. 4) Drift beyond the declared time is absent or approved as exception. 5) Attestation evidence is collected where supported. | Firmware drift remediation time [days] default 7 (illustrative) (Capability profile) Firmware inventory coverage [% of devices] default 100 (illustrative) (Capability profile) | Approved firmware matrix; Signature/provenance verification records; Fleet firmware inventory; Drift and exception register; Attestation reports where supported | RECONCILIATION; SAMPLING; REPERFORMANCE; DOCUMENT_REVIEW | 1) Obtain matrix and inventory. 2) Reperform version query on a sample. 3) Review signature verification records. 4) Review drift and exceptions. 5) Review attestation where supported. | PREVENTIVE | IMPLEMENTATION | AL3 | BUILD; OPERATE; CHANGE | NORMAL; MAINTENANCE; TRANSITION | Applies to all firmware-bearing components in the compute boundary. | CG-08 | CG-14; CG-15 | Mixed accelerator firmware within a job; Unsigned BMC firmware; NIC firmware incompatible with fabric; Power-shelf firmware bug | AssetInstance; ArchitectureSnapshot; Safeguard | Read-only queries with operator-authorised accounts. | If any component class is not inventoried, record U5 UNKNOWN for that class; the control cannot be CONFORMING. | NIST SP 800-193 (platform firmware resiliency guidelines); NIST SP 800-147B (BIOS protection guidelines for servers); DMTF SPDM (Security Protocol and Data Model) for device authentication and attestation; TCG TPM 2.0 Library Specification; DMTF Redfish (platform management API) | MCF-CMP-004; MCF-CMP-015; MCF-SUP-014; MCF-SEC-013 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-CMP-014 | CMP | AI Compute Infrastructure | CMP-04 | Firmware, driver and compatibility | Driver Compatibility | Ensure accelerator drivers, communication libraries, runtimes, kernel and container base images form a tested compatible stack, and that workloads run only on stacks in the compatibility matrix. | The AI platform operator shall maintain a compatibility matrix linking firmware, kernel, accelerator driver, communication library, runtime and container base images, shall test each matrix entry before approval, and shall prevent workloads from running on unapproved combinations through image and node labelling. | 1) A compatibility matrix exists and is versioned. 2) Each approved combination has a test record. 3) Node labels or admission controls prevent unapproved combinations. 4) Container base images declare required driver ranges. 5) Deviations are tracked. |  | Compatibility matrix; Test records per combination; Admission control configuration; Image manifests | RECONCILIATION; DOCUMENT_REVIEW; SAMPLING | 1) Obtain matrix and tests. 2) Sample running nodes for stack versions. 3) Verify admission controls. | PREVENTIVE | IMPLEMENTATION | AL3 | BUILD; OPERATE; CHANGE | NORMAL; TRANSITION | Applies to all accelerator software stacks used by in-scope workloads. |  | CG-08 | Driver/firmware mismatch causing hangs; Library version causing silent numerical changes; Container with incompatible driver expectation | ArchitectureSnapshot; AssetInstance; Interface | Read-only sampling of running stacks via operator-provided inventory tooling. | If running stacks cannot be sampled, record U2 inaccessible UNKNOWN. | NIST SP 800-128 (security-focused configuration management); DMTF SPDM (Security Protocol and Data Model) for device authentication and attestation | MCF-CMP-013; MCF-CMP-015; MCF-SUP-015 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-CMP-015 | CMP | AI Compute Infrastructure | CMP-04 | Firmware, driver and compatibility | Upgrade Testing | Ensure firmware, driver and software upgrades are tested on representative workloads and rolled out in stages with soak periods and automatic halt criteria, so that a defective release cannot become a fleet-wide common-mode failure. | The AI platform operator shall test each upgrade on a staging environment with representative workloads (including multi-node collective tests and checkpoint/restore), shall roll out in stages starting with a canary cohort spread across fault domains, shall define soak periods and halt criteria based on error rates and performance, and shall record each stage's go/no-go decision. | 1) Each upgrade has a staging test record including multi-node collective and checkpoint/restore tests. 2) Rollout plans define canary, staged cohorts, soak periods and halt criteria. 3) Canary cohorts span multiple fault domains but are limited in size. 4) Go/no-go decisions per stage are recorded with metrics. 5) At least one halted rollout or a test of halt automation demonstrates halt criteria work. | Canary cohort size [% of fleet] default 2 (illustrative) (Capability profile) Soak period per stage [h] default 72 (illustrative) (Capability profile) Halt criterion: error-rate increase [× baseline] default 2 (illustrative) (Capability profile) | Staging test records; Rollout plans; Stage go/no-go records with metrics; Halt event or test record | DOCUMENT_REVIEW; SAMPLING; ANALYSIS; INQUIRY | 1) Sample recent upgrades. 2) Review staging tests. 3) Review rollout plans and stage decisions. 4) Check halt evidence. | PREVENTIVE | EFFECTIVENESS | AL5 | CHANGE; OPERATE | TRANSITION; NORMAL; DEGRADED | Applies to all firmware, driver and system software changes on in-scope compute. | CG-14 | CG-09; CG-08 | Fleet-wide firmware defect (common-mode); Upgrade breaks checkpoint compatibility; Canary in single fault domain hiding issues; Soak too short to show intermittent errors | Action; TestRecord; FailureScenario; Safeguard | Reviews of records; no upgrades performed by assessor. | If stage go/no-go evidence is missing for a sampled upgrade, record U1 UNKNOWN and Finding. | NIST SP 800-128 (security-focused configuration management); ISO/IEC 20000-1 (service management system requirements); AIDCF-004 (Threat, Hazard and Failure Model) | MCF-CMP-013; MCF-CMP-016; MCF-OPS-018; MCF-SUP-015 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-CMP-016 | CMP | AI Compute Infrastructure | CMP-04 | Firmware, driver and compatibility | Rollback Readiness | Ensure every firmware and software change can be rolled back to the previous known-good baseline within the declared time, including components where rollback is constrained (anti-rollback fuses, one-way firmware migrations). | The AI platform operator shall define a rollback procedure for each change class, shall identify components where rollback is constrained or impossible and treat them as higher-risk changes, shall retain previous known-good images, and shall test rollback in staging for each change before production rollout. | 1) Rollback procedures exist per change class. 2) Components with rollback constraints are identified and flagged in change records. 3) Previous known-good images are retained and integrity-verified. 4) Rollback has been tested in staging for sampled changes within the declared time. 5) A production rollback (test or event) achieved the declared time. | Rollback time objective [h] default 4 (illustrative) (Capability profile) | Rollback procedures; Rollback-constraint register; Image retention records with hashes; Staging rollback tests; Production rollback record | DOCUMENT_REVIEW; TEST; REPERFORMANCE | 1) Review procedures and constraints. 2) Verify retained image hashes. 3) Review staging and production rollback records. | RECOVERY | RESILIENCE | AL5 | CHANGE; OPERATE | TRANSITION; RECOVERY; DEGRADED | Applies to all changes in the compute baseline. |  | CG-10; CG-14 | Anti-rollback fuse prevents downgrade; Previous image deleted; Rollback untested | Action; Safeguard; TestRecord | Rollback tests in staging only unless authorised. | If rollback has not been tested, record U1 UNKNOWN; the RESILIENCE claim cannot be CONFORMING. | NIST SP 800-193 (platform firmware resiliency guidelines); NIST SP 800-128 (security-focused configuration management) | MCF-CMP-015; MCF-CMP-023; MCF-OPS-020; MCF-SEC-024 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-CMP-017 | CMP | AI Compute Infrastructure | CMP-05 | Compute health and observability | GPU Telemetry | Collect accelerator telemetry (temperature, power, clocks, throttle reasons, memory ECC counts, page/row retirement, interconnect errors, utilisation) at sufficient frequency and completeness to detect degradation and to correlate compute behaviour with facility events. | The AI platform operator shall collect accelerator telemetry from every in-scope accelerator at the declared interval using vendor management interfaces, shall monitor collection completeness, shall time-synchronise telemetry with facility (BMS/EPMS) data, and shall retain it for the declared period. | 1) Telemetry includes temperature, power, clocks, throttle reasons, ECC counts, retirement events and interconnect errors. 2) Collection covers the declared fraction of accelerators with completeness monitoring. 3) Timestamps are synchronised to a common time source shared with facility systems. 4) Retention meets the declared period. 5) Throttle-reason telemetry is used to report thermal and power throttling to facility operations. | Telemetry interval [s] default 10 (illustrative) (Capability profile) Collection completeness [% of expected samples] default 99 (illustrative) (Capability profile) Retention [days] default 90 (illustrative) (Capability profile) | Accelerator telemetry schema; Per-rack collection completeness reports; Time synchronisation configuration; Retention configuration; Throttle reports to facility | ANALYSIS; REPERFORMANCE; INSPECTION | 1) Review the telemetry schema against the required fields. 2) Analyse collection completeness by rack and accelerator. 3) Compare a live device query with stored values. 4) Check time synchronisation with BMS/EPMS and retention settings. | DETECTIVE | OPERATION | AL4 | COMMISSION; OPERATE | NORMAL; DEGRADED; MAINTENANCE; EMERGENCY | Applies to all in-scope accelerators. |  | CG-08; CG-06 | Telemetry blindness on a rack; Clock skew preventing correlation with cooling event; Throttling unreported | EvidenceObject; AssetInstance; Interface | Read-only device queries using an operator-authorised monitoring account. | If telemetry completeness is below target, record U5 UNKNOWN for affected accelerators. | DMTF Redfish (platform management API); Open Compute Project hardware management and fault-management specifications | MCF-CMP-018; MCF-CMP-019; MCF-NET-024; MCF-THM-008 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-CMP-018 | CMP | AI Compute Infrastructure | CMP-05 | Compute health and observability | Node Health | Ensure each node's health is checked before, during and after jobs by automated checks (accelerator diagnostics, memory, interconnect, NIC, storage mount, thermal state) and unhealthy nodes are drained before they cause job failure. | The AI platform operator shall run automated health checks at job prolog/epilog and at a periodic interval, shall define pass criteria per check, shall drain nodes failing a check automatically, and shall track drained nodes to repair or return-to-service. | 1) Health-check suite and pass criteria are documented. 2) Checks run at prolog/epilog and periodically, with logs. 3) Failing nodes are drained automatically. 4) Drained nodes are tracked to resolution with ageing. 5) Job failures attributable to node faults are trended. | Periodic health-check interval [h] default 24 (illustrative) (Capability profile) Maximum drained-node age before escalation [days] default 5 (illustrative) (Capability profile) | Health-check suite definition; Check execution logs; Drain events; Drained-node tracker; Job-failure attribution trend | ANALYSIS; SAMPLING; DOCUMENT_REVIEW | 1) Review suite. 2) Sample logs. 3) Trace job failures. 4) Review drained-node ageing. | DETECTIVE | OPERATION | AL4 | OPERATE | NORMAL; DEGRADED; MAINTENANCE | Applies to all in-scope nodes. |  | CG-08 | Unhealthy node admitted to job; Drained nodes forgotten; Health check too shallow | AssetInstance; Safeguard; EvidenceObject | Read-only review of health-check logs; no health checks triggered on production nodes. | If health-check logs are unavailable, record U1 UNKNOWN. | Open Compute Project hardware management and fault-management specifications; ISO/IEC 20000-1 (service management system requirements) | MCF-CMP-017; MCF-CMP-019; MCF-CMP-010 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-CMP-019 | CMP | AI Compute Infrastructure | CMP-05 | Compute health and observability | Error and Degradation Detection | Detect accelerator and node errors that threaten job integrity (uncorrectable ECC, rising correctable ECC, memory row remapping exhaustion, vendor fatal error events such as XID-type events, PCIe AER errors, interconnect CRC errors) and silent data corruption, and respond before corrupted results propagate into checkpoints or models. | The AI platform operator shall classify accelerator and node error events by severity with defined automatic actions (drain, reset, RMA), shall trend correctable error rates against thresholds, and shall run periodic silent-data-corruption screening (known-answer tests) across the fleet. The AI platform operator shall link detected corruption to affected jobs and checkpoints for integrity assessment. | 1) An error classification exists with severity and automatic action per event class. 2) Uncorrectable and fatal events trigger automatic drain within the declared time (verified on sample events). 3) Correctable error rates are trended and threshold breaches are actioned. 4) Silent-data-corruption screening runs fleet-wide at the declared interval and failures are actioned. 5) Jobs and checkpoints run on nodes later found faulty are identified for integrity review. 6) Detection has been validated by fault injection, known-bad hardware or real events. | Drain time after fatal error event [min] default 5 (illustrative) (Capability profile) SDC screening interval [days] default 30 (illustrative) (Capability profile; OCP SDC practice) Correctable ECC escalation threshold [events per day per accelerator] default platform-specific (Platform OEM RAS guidance) | Error classification and action table; Sample error events with timestamps of action; Correctable error trend; SDC screening results; Job/checkpoint impact analyses | ANALYSIS; SAMPLING; TEST; DOCUMENT_REVIEW | 1) Review classification. 2) Sample fatal events and reconstruct drain timelines. 3) Analyse correctable error trends. 4) Review SDC screening coverage and results. 5) Review job/checkpoint impact analyses. | DETECTIVE | EFFECTIVENESS | AL5 | COMMISSION; OPERATE | NORMAL; DEGRADED; FAILED | Applies to all in-scope accelerators and hosts. | CG-08 |  | Silent data corruption contaminating checkpoints; Fatal error not draining node causing job hangs; Rising correctable ECC preceding failure unnoticed; Row-remap exhaustion | FailureMode; Safeguard; EvidenceObject; FailureScenario | Fault injection only on drained test nodes with operator authorisation; never on production jobs. | If SDC screening is not performed, record US4 UNKNOWN against CG-08 for integrity outcomes. | Open Compute Project server component resilience and silent data corruption materials; JEDEC memory standards (DDR and HBM families) for ECC and RAS features; PCI Express Base Specification (Advanced Error Reporting); Open Compute Project hardware management and fault-management specifications | MCF-CMP-017; MCF-CMP-018; MCF-STO-009; MCF-STO-017 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-CMP-020 | CMP | AI Compute Infrastructure | CMP-05 | Compute health and observability | Performance Baselines | Maintain performance baselines (single-accelerator throughput, scale-up bandwidth, multi-node collective bandwidth, representative training step time) so that degradation from hardware, firmware, thermal or fabric causes is detected quantitatively. | The AI platform operator shall define baseline benchmarks per node type and cluster scale, shall run them at acceptance, after changes and at a periodic interval, and shall investigate deviations beyond the declared threshold. | 1) Baseline benchmarks and expected results are defined per node type and scale. 2) Benchmarks run at acceptance, after changes and periodically. 3) Deviations beyond the threshold are investigated with root cause. 4) Baselines are refreshed with approval when the baseline changes. | Performance regression threshold [% below baseline] default 5 (illustrative) (Capability profile) | Benchmark definitions and baselines; Benchmark run results; Deviation investigations | ANALYSIS; DOCUMENT_REVIEW; SAMPLING | 1) Review definitions. 2) Analyse run results. 3) Review investigations. | DETECTIVE | OPERATION | AL4 | COMMISSION; OPERATE; CHANGE | NORMAL; DEGRADED; TRANSITION | Applies to all in-scope clusters. |  | CG-08 | Gradual regression unnoticed; Thermal throttling reducing throughput; Post-upgrade slowdown | CapacityAssertion; TestRecord; EvidenceObject | Benchmarks run on drained nodes only. | If no baseline exists, record U1 UNKNOWN for performance-outcome claims. | MLCommons MLPerf Training and Inference benchmark rules | MCF-CMP-006; MCF-CMP-015; MCF-NET-008 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-CMP-021 | CMP | AI Compute Infrastructure | CMP-06 | Compute lifecycle and recovery | Provisioning | Ensure new and repaired hardware enters service only after verified identity, baseline conformance and burn-in acceptance, so that infant-mortality failures and counterfeit or mis-configured components are caught before production. | The AI platform operator shall provision nodes through an automated pipeline that verifies component identity against the purchase and provenance records, applies the approved baseline, runs a burn-in and acceptance suite (stress, memory, interconnect, thermal, storage) for the declared duration, and records acceptance before the node becomes schedulable. | 1) Component identity is verified against provenance records. 2) Baseline is applied automatically and verified. 3) Burn-in runs for the declared duration with defined pass criteria. 4) Nodes become schedulable only after recorded acceptance. 5) Burn-in failure rates are trended by supplier and lot. | Burn-in duration [h] default 48 (illustrative) (Capability profile; OEM guidance) | Provisioning pipeline definition; Identity verification records; Burn-in results; Acceptance records; Failure trend by lot | SAMPLING; DOCUMENT_REVIEW; RECONCILIATION | 1) Sample nodes. 2) Trace identity, baseline, burn-in and acceptance. 3) Review failure trends. | PREVENTIVE | IMPLEMENTATION | AL3 | BUILD; COMMISSION; CHANGE | TRANSITION; NORMAL | Applies to all nodes entering service, including after RMA. |  | CG-08; CG-14 | Infant-mortality failure in production; Counterfeit component; Node admitted without baseline | AssetInstance; TestRecord; Safeguard | Burn-in is performed by operator; assessors review records. | Nodes without acceptance records are U1 UNKNOWN. | Open Compute Project hardware management and fault-management specifications; ISO/IEC 20243 (Open Trusted Technology Provider Standard) | MCF-CMP-004; MCF-CMP-022; MCF-SUP-010; MCF-SUP-012 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-CMP-022 | CMP | AI Compute Infrastructure | CMP-06 | Compute lifecycle and recovery | Spares and RMA | Ensure spare accelerators, nodes, trays, switch trays, NICs and cables are held in quantities and locations sufficient to restore usable capacity within tolerance, and that RMA turnaround is tracked against supplier obligations. | The AI platform operator shall size spares from observed failure rates and lead times, shall hold spares on site or within the declared logistics time, shall track RMA turnaround against contractual obligations, and shall ensure returned parts are sanitised or tracked under custody. | 1) Spares sizing uses observed failure rates and lead times. 2) Spares inventory matches the sizing for sampled component classes. 3) RMA turnaround is tracked against supplier obligations. 4) Long-lead components are identified with mitigation. 5) Returned components with storage are sanitised or under custody. | On-site spares [% of installed by class] default 3 (illustrative) (Capability profile; failure-rate analysis) RMA turnaround obligation [days] default contractual (Supplier contract) | Spares sizing analysis; Inventory records; RMA tracker; Long-lead register; Custody/sanitisation records for returns | ANALYSIS; INSPECTION; DOCUMENT_REVIEW | 1) Review sizing. 2) Physically count sample. 3) Review RMA performance. 4) Review custody for returns. | CORRECTIVE | OPERATION | AL4 | OPERATE | NORMAL; DEGRADED; RECOVERY | Applies to all in-scope compute hardware. |  | CG-10; CG-03 | Stock-out of long-lead part; RMA delay eroding usable capacity; Returned drive leaking data | Resource; Dependency; AssetInstance | Inspection of stores under escort. | If inventory cannot be reconciled, record U4 conflicting UNKNOWN. | ISO/IEC 19770 series (IT asset management); NIST SP 800-88 (guidelines for media sanitisation) | MCF-CMP-021; MCF-SUP-017; MCF-SUP-018; MCF-DEP-011 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-CMP-023 | CMP | AI Compute Infrastructure | CMP-06 | Compute lifecycle and recovery | Node Rebuild | Ensure nodes and scale-up domains can be rebuilt from bare metal to an accepted, schedulable state within the declared time after failure, corruption or mass events (for example after a power or cooling outage), including re-qualification before rejoining production. | The AI platform operator shall maintain an automated rebuild path (image, baseline, configuration, credentials, health and bandwidth re-qualification) that does not depend on services lost in the same event, shall define the rebuild time objective per node and for a mass rebuild of a declared fraction of the cluster, and shall exercise mass rebuild at a defined interval. After facility power or cooling events, the AI platform operator shall re-qualify affected nodes before readmission. | 1) An automated rebuild path exists and its dependencies (image repository, provisioning network, identity) are documented. 2) Rebuild dependencies are not in the same fault domain as the event they recover from, or the gap is treated. 3) Single-node rebuild meets the time objective on sampled events. 4) A mass rebuild exercise of the declared fraction met the time objective. 5) Post-facility-event re-qualification is defined and was applied in the last event. | Single-node rebuild time objective [h] default 2 (illustrative) (Capability profile) Mass rebuild fraction [% of cluster] default 25 (illustrative) (Capability profile) Mass rebuild time objective [h] default 12 (illustrative) (Capability profile) | Rebuild automation definition; Rebuild dependency map; Single-node rebuild timings; Mass rebuild exercise record; Re-qualification records after facility events | SCENARIO_EXERCISE; ANALYSIS; DOCUMENT_REVIEW; SAMPLING | 1) Review rebuild path and dependencies. 2) Sample single-node rebuild timings. 3) Review mass rebuild exercise. 4) Review post-event re-qualification. | RECOVERY | RESILIENCE | AL5 | COMMISSION; OPERATE; CHANGE | RECOVERY; FAILED; TRANSITION | Applies to all in-scope compute. | CG-10 | CG-08 | Image repository in same failed domain; Mass rebuild overwhelms provisioning network; Nodes readmitted after thermal event without re-qualification | FailureScenario; Safeguard; TestRecord; Dependency | Mass rebuild exercises are capability-affecting. Draining nodes or partitions removes capacity from production jobs; the AI platform operator's change authority and job-owner notification are required. | If no mass rebuild exercise exists, record US4 UNKNOWN against CG-10. | AIDCF-004 (Threat, Hazard and Failure Model); ISO/IEC 20000-1 (service management system requirements); ISO 22301 (business continuity management systems) | MCF-CMP-016; MCF-THM-024; MCF-RES-015; MCF-STO-018 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-CMP-024 | CMP | AI Compute Infrastructure | CMP-06 | Compute lifecycle and recovery | Secure Retirement | Ensure retired or returned compute hardware (nodes, accelerators with memory, BMCs, boot drives, NICs with persistent configuration) is removed from inventory, sanitised, and disposed of with custody, so that data, credentials and model weights are not exposed and the asset register stays accurate. | The AI platform operator shall execute a retirement procedure that revokes credentials and attestation identities, sanitises persistent storage per a recognised sanitisation standard with verification, resets BMC and firmware secrets, updates the asset register and topology, and records custody to disposal or resale. | 1) The retirement procedure covers credentials, storage sanitisation, BMC reset, register update and custody. 2) Sanitisation method and verification are recorded per device. 3) Asset register and topology are updated for sampled retirements. 4) Custody chain to disposal or resale is complete. 5) Credentials and certificates of retired nodes are revoked. |  | Retirement procedure; Sanitisation certificates for boot drives and persistent devices; Asset register changes; Custody records from decommissioning to disposal; Credential revocation records | SAMPLING; DOCUMENT_REVIEW; RECONCILIATION | 1) Sample retirements from the last 12 months. 2) Verify credential and attestation-identity revocation for each sampled node. 3) Verify sanitisation certificates and method for each persistent device. 4) Reconcile asset register and topology removal. 5) Trace custody to disposal or resale. | PREVENTIVE | IMPLEMENTATION | AL3 | DECOMMISSION | SHUTDOWN; TRANSITION | Applies to all retired in-scope compute hardware. |  | CG-02 | Model weights recoverable from retired drive; Stale node in asset register; Unrevoked certificates | AssetInstance; Action; Safeguard | Record review; no handling of media. | Retirements without sanitisation evidence are recorded as U1 UNKNOWN and Findings. | NIST SP 800-88 (guidelines for media sanitisation); IEEE 2883 (standard for sanitizing storage); ISO/IEC 19770 series (IT asset management) | MCF-STO-024; MCF-PHY-020; MCF-ENV-020; MCF-CMP-022 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-STO-001 | STO | AI Storage and Data Infrastructure | STO-01 | Storage architecture and tiering | Training Data Tier | Ensure the storage tier holding training and fine-tuning datasets is designed for the read pattern of data loaders at cluster scale, preserves dataset versions and lineage, and keeps data within declared sovereignty and residency boundaries. | The storage engineering authority shall document the training data tier (system type, for example parallel file system or object store with cache; capacity; read throughput per accelerator; dataset versioning and lineage mechanism; locations and jurisdictions of every copy). The data owner shall approve the residency and sovereignty constraints and shall confirm that every copy, cache and replica lies within them. | 1) The tier design states system type, capacity, read throughput per accelerator and caching strategy. 2) Required read throughput is derived from workload data rate per accelerator × accelerator count with stated assumptions. 3) Dataset versioning and lineage (source, transformations, hash) are implemented and referenced by training jobs. 4) Every location holding the data (primary, cache, replica, backup) is listed with jurisdiction. 5) The data owner's residency and sovereignty approval exists and matches the location list. | Data-loader read throughput per accelerator [GB/s] default workload-specific (illustrative 1) (Workload characterisation) Permitted data jurisdictions [list] default capability-specific (Data owner; applicable law and contracts) | Training data tier design; Throughput derivation; Dataset version and lineage records; Data location register with jurisdictions; Data owner residency approval | DOCUMENT_REVIEW; ANALYSIS; RECONCILIATION | 1) Obtain tier design and derivation. 2) Recompute required throughput. 3) Sample datasets for lineage records. 4) Reconcile location register with configuration. | DIRECTIVE | DESIGN | AL2 | PLAN; DESIGN; CHANGE | NORMAL; TRANSITION | Applies where in-scope workloads read training or fine-tuning data from storage within or controlled by the boundary. |  | CG-08; CG-01 | Data-loader starvation leaving accelerators idle; Unversioned dataset preventing reproducibility; Cache replica outside permitted jurisdiction | InfrastructureSystem; Resource; ArchitectureSnapshot; Dependency | Desk-based and read-only. | If any data location is unknown, record U10 dependency UNKNOWN; sovereignty conformance cannot be asserted. | AIDCF-013 (AI Data Centre Assurance Reference Architecture); Regulation (EU) 2016/679 (GDPR) and applicable national data-residency law; ISO/IEC 27001 (information security management systems) | MCF-STO-005; MCF-STO-014; MCF-STO-022; MCF-DEP-012 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-STO-002 | STO | AI Storage and Data Infrastructure | STO-01 | Storage architecture and tiering | Checkpoint Tier | Ensure the checkpoint tier is sized so that model and optimiser state can be written within the declared checkpoint window at the declared interval, with the interval chosen against observed failure rates, and that checkpoints are placed in a fault domain independent of the compute they protect. | The storage engineering authority shall document checkpoint size per job class, required write bandwidth (checkpoint size ÷ checkpoint window), checkpoint interval and its derivation from job-level failure rate and checkpoint cost, retention count, and the fault-domain separation between the checkpoint tier and the protected compute. The AI platform operator shall confirm the parameters per production job class. | 1) Checkpoint size per job class is stated with its basis (parameter count, precision, optimiser state, sharding). 2) Required write bandwidth is derived from size and window and is within the tier's demonstrated capability (MCF-STO-005). 3) Checkpoint interval is justified against job-level mean time between interruptions and checkpoint cost. 4) Retention of N most recent good checkpoints is defined. 5) Checkpoint storage does not share a power, cooling or fabric fault domain with all of the compute it protects, or the residual risk is accepted. 6) Asynchronous or tiered (local NVMe then parallel file system) checkpointing, if used, documents when a checkpoint is considered durable. | Checkpoint size (large training job) [TB] default job-specific (illustrative 10) (Model architecture and optimiser state) Checkpoint write window [s] default 120 (illustrative) (Capability profile; acceptable step stall) Checkpoint interval [min] default derived (illustrative 30) (Young/Daly model using measured interruption rate) Retained good checkpoints [count] default 3 (illustrative) (Capability profile) | Checkpoint tier design; Size and bandwidth derivation; Interval derivation with interruption-rate data; Fault-domain separation analysis; Durability definition for asynchronous checkpointing | ANALYSIS; DOCUMENT_REVIEW; RECONCILIATION | 1) Recompute bandwidth from size and window. 2) Recompute interval from interruption data. 3) Review fault-domain separation. 4) Review durability definition. | DIRECTIVE | DESIGN | AL2 | DESIGN; CHANGE | NORMAL; DEGRADED; RECOVERY | Applies to all in-scope training and long-running fine-tuning workloads. Not applicable to stateless inference, where MCF-STO-003 covers model artefacts. |  | CG-08; CG-10 | Checkpoint exceeds write window, stalling training; Interval too long for failure rate, losing hours of work; Checkpoints co-located with compute lost in the same event; Asynchronous checkpoint believed durable before flush | CapacityAssertion; FaultDomain; Resource; RequiredFunction | Desk-based recalculation; no checkpoints triggered. | If job interruption rates are unknown, record U1 UNKNOWN for the interval justification. | Young/Daly optimum checkpoint interval model (published literature); AIDCF-013 (AI Data Centre Assurance Reference Architecture); IO500 benchmark methodology (HPC storage performance) | MCF-STO-005; MCF-STO-017; MCF-STO-018; MCF-CMP-008 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-STO-003 | STO | AI Storage and Data Infrastructure | STO-01 | Storage architecture and tiering | Model and Artifact Tier | Ensure trained models, adapters, tokenisers, configurations and release artefacts are stored in a versioned, access-controlled, integrity-protected registry from which deployments and recoveries draw known-good, hash-verified artefacts. | The AI platform operator shall store model and release artefacts in a registry that assigns immutable versions, records content hashes and provenance (training run, dataset version, checkpoint), restricts write and delete to authorised roles, and verifies hashes at deployment. The storage service owner shall protect the registry under MCF-STO-013 to MCF-STO-016. | 1) Artefacts have immutable versions with content hashes. 2) Provenance links artefact to training run, dataset version and source checkpoint. 3) Write and delete are restricted and logged. 4) Deployments verify hashes before use (sampled). 5) The registry is included in protection and recovery scope. |  | Registry configuration; Sample artefact records with hashes and provenance; Access policy and logs; Deployment hash-verification logs | RECONCILIATION; REPERFORMANCE; SAMPLING | 1) Sample artefacts. 2) Recompute hashes. 3) Review provenance and access logs. 4) Check deployment verification. | PREVENTIVE | IMPLEMENTATION | AL3 | BUILD; OPERATE; CHANGE | NORMAL; RECOVERY | Applies to all model and release artefacts produced or served within the boundary. |  | CG-08; CG-10 | Overwritten model version; Deployment of tampered artefact; Lost provenance | AssetInstance; EvidenceObject; Safeguard | Read-only hash verification. | Artefacts without hash or provenance are recorded as U6 source-unverified UNKNOWN. | ISO/IEC 27040 (storage security); NIST SP 800-209 (security guidelines for storage infrastructure); ISO/IEC 27001 (information security management systems) | MCF-STO-016; MCF-STO-009; MCF-SUP-013 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-STO-004 | STO | AI Storage and Data Infrastructure | STO-01 | Storage architecture and tiering | Archive Tier | Ensure long-term retention of datasets, model versions and checkpoints needed for reproducibility, audit or regulatory purposes is held on a durable archive tier with defined retention, retrievability, integrity checking and media-refresh plans. | The storage service owner shall define retention classes for archived AI data, shall store archives with fixity checks and at least the declared number of geographically or administratively separate copies, shall test retrieval at a defined interval, and shall plan media or format migration before end of support. | 1) Retention classes and durations are defined. 2) Archive copies meet the declared count and separation. 3) Fixity checks run periodically with results recorded. 4) Retrieval tests meet declared retrieval times. 5) Media/format migration plans exist. | Archive copies [count] default 2 (illustrative) (Capability profile) Retrieval time objective [h] default 48 (illustrative) (Capability profile) | Retention schedule; Archive configuration; Fixity check results; Retrieval test records; Migration plan | DOCUMENT_REVIEW; SAMPLING; TEST | 1) Review retention classes. 2) Review fixity results. 3) Select retrieval sample and review or run test. | PREVENTIVE | IMPLEMENTATION | AL3 | BUILD; OPERATE | NORMAL | Applies where AI data must be retained beyond active use. |  | CG-10 | Archive unreadable after media obsolescence; Bit rot undetected; Retrieval slower than obligation | Resource; AssetInstance; TestRecord | Retrieval to a test location only. | If fixity checks are absent, record U7 integrity-uncertain UNKNOWN. | ISO 14721 (OAIS reference model for archives); ISO/IEC 27040 (storage security) | MCF-STO-011; MCF-STO-016; MCF-STO-024 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-STO-005 | STO | AI Storage and Data Infrastructure | STO-02 | Performance and capacity | Throughput and IOPS | Demonstrate that the storage system delivers the aggregate read throughput for data loading and the aggregate write throughput for checkpointing that the outcome requires, at full cluster concurrency and in degraded states (failed server, rebuild in progress). | The storage engineering authority shall demonstrate, by benchmark at acceptance and after material change, that aggregate read and write throughput and IOPS meet the required values at the declared client concurrency, including with one storage server or enclosure failed and during erasure-coding or RAID rebuild. The AI platform operator shall measure production checkpoint write times and compare them with the window in MCF-STO-002. | 1) Benchmark results at declared concurrency meet required read and write throughput. 2) Degraded-state benchmarks (server failed, rebuild active) meet the declared degraded-state minimum. 3) Production checkpoint write times are within the window for the period. 4) Benchmark method (tool, file sizes, access pattern, client count) represents the AI workload. 5) Network path between clients and storage is included in the test, not only server-side capability. | Required aggregate checkpoint write throughput [GB/s] default derived: checkpoint size ÷ window (illustrative 100) (MCF-STO-002 derivation) Degraded-state minimum [% of required throughput] default 70 (illustrative) (Capability profile) Required aggregate read throughput [GB/s] default derived from MCF-STO-001 (Workload characterisation) | Acceptance and post-change benchmark reports; Degraded-state benchmark report; Production checkpoint timing data; Benchmark method statement | TEST; ANALYSIS; DOCUMENT_REVIEW | 1) Review benchmark method for representativeness. 2) Compare results with requirements. 3) Review degraded-state results. 4) Analyse production checkpoint timings. | PREVENTIVE | EFFECTIVENESS | AL5 | COMMISSION; OPERATE; CHANGE | NORMAL; DEGRADED; RECOVERY | Applies to storage serving in-scope training data loading or checkpointing. | CG-08 |  | Throughput collapse during rebuild; Benchmark unrepresentative (small client count); Network bottleneck hidden | CapacityAssertion; TestRecord; InfrastructureSystem | Benchmarks at full concurrency compete with production; schedule in maintenance windows with AI platform operator agreement. Degraded-state tests use controlled server removal approved by the storage engineering authority, never data deletion. | If no degraded-state benchmark exists, record U5 coverage-gap UNKNOWN; CONFORMING requires degraded-state evidence. | IO500 benchmark methodology (HPC storage performance); AIDCF-013 (AI Data Centre Assurance Reference Architecture) | MCF-STO-002; MCF-STO-006; MCF-STO-008; MCF-NET-009 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-STO-006 | STO | AI Storage and Data Infrastructure | STO-02 | Performance and capacity | Metadata Performance | Ensure metadata operations (open, create, stat, list) scale to the concurrency of AI jobs, because many-small-file datasets and synchronous checkpoint creation can saturate metadata services and stall entire clusters. | The storage service owner shall define required metadata operation rates and latency at peak concurrency, shall monitor metadata latency and queue depth continuously, and shall apply workload guidance (file packing, sharded checkpoints, directory fan-out limits) agreed with the AI platform operator. | 1) Required metadata rates and latency targets are defined. 2) Metadata latency and queue telemetry is collected and within targets for the period. 3) Workload guidance exists and is applied by sampled jobs. 4) Metadata saturation events are investigated. | Metadata operation p99 latency [ms] default 10 (illustrative) (Capability profile) Required metadata operations [ops/s] default workload-specific (Workload characterisation) | Metadata targets; Latency/queue telemetry; Workload guidance; Saturation event reviews | ANALYSIS; DOCUMENT_REVIEW; SAMPLING | 1) Review targets. 2) Analyse telemetry. 3) Sample jobs against guidance. 4) Review events. | DETECTIVE | OPERATION | AL4 | COMMISSION; OPERATE | NORMAL; DEGRADED | Applies to file-system based storage; for object stores, applies to listing and request-rate limits. |  | CG-08 | Metadata storm at synchronous checkpoint; Millions of small files exceeding inode or listing limits; Single metadata server bottleneck | InfrastructureSystem; CapacityAssertion; FailureMode | Read-only telemetry review; no metadata benchmarks on production namespaces. | If metadata telemetry is not collected, record U1 UNKNOWN. | IO500 benchmark methodology (HPC storage performance) | MCF-STO-005; MCF-STO-010; MCF-STO-021 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-STO-007 | STO | AI Storage and Data Infrastructure | STO-02 | Performance and capacity | Capacity Headroom | Maintain free capacity above the level at which the storage system's performance, rebuild ability or checkpoint retention degrade, so that capacity exhaustion never halts checkpointing. | The storage service owner shall define a capacity headroom threshold per tier that accounts for performance degradation at high fill, rebuild space and retention of N checkpoints, shall alert at warning and critical thresholds, and shall enforce quotas so that one job or tenant cannot exhaust a shared tier. | 1) Headroom thresholds are defined per tier with rationale. 2) Utilisation stayed below the critical threshold for the period, or breaches were handled. 3) Quotas are configured for shared tiers. 4) Checkpoint retention space is reserved or accounted for. | Critical utilisation threshold [% of usable capacity] default 80 (illustrative) (Storage vendor guidance; capability profile) Warning threshold [% of usable capacity] default 70 (illustrative) (Capability profile) | Threshold definitions; Utilisation trend; Quota configuration; Breach handling records | ANALYSIS; RECONCILIATION | 1) Review headroom thresholds and their rationale. 2) Analyse utilisation by tier over the period. 3) Review quotas and breach handling. | PREVENTIVE | OPERATION | AL4 | OPERATE | NORMAL; DEGRADED | Applies to all in-scope storage tiers. |  | CG-08 | Checkpoint write fails on full file system; Performance collapse near full; Rebuild impossible due to lack of spare capacity | CapacityAssertion; Resource | Read-only review of utilisation and quota configuration. | If utilisation data is unavailable for a tier, record U1 UNKNOWN. | ISO/IEC 27040 (storage security) | MCF-STO-022; MCF-STO-002; MCF-OPS-021 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-STO-008 | STO | AI Storage and Data Infrastructure | STO-02 | Performance and capacity | Burst Handling | Ensure the storage system absorbs synchronised write bursts (many ranks checkpointing simultaneously, several jobs checkpointing at once, restart storms after an outage) without timeouts, job failure or degradation of other tenants. | The storage engineering authority shall characterise peak burst demand (concurrent checkpoints, restart read storm), shall provide burst absorption (client-side or burst-buffer tier, QoS, admission control or staggered checkpoint scheduling), and shall demonstrate by test or production evidence that the declared burst completes within the window without client timeouts or impact beyond tolerance on other workloads. | 1) Peak burst demand is characterised including post-outage restart reads. 2) Burst absorption mechanisms are configured. 3) A test or production event shows the declared burst completed within the window. 4) No client timeouts or job failures attributable to storage occurred during the burst. 5) Impact on other tenants stayed within tolerance. | Concurrent checkpointing jobs [count] default 3 (illustrative) (Workload characterisation) Restart read-storm completion time [min] default 15 (illustrative) (Capability profile) | Burst characterisation; QoS/burst-buffer configuration; Burst test or event telemetry; Timeout and job failure logs | TEST; ANALYSIS | 1) Review characterisation. 2) Review configuration. 3) Analyse burst telemetry and logs. | PREVENTIVE | EFFECTIVENESS | AL5 | COMMISSION; OPERATE; CHANGE | NORMAL; DEGRADED; RECOVERY | Applies to shared storage serving synchronous training or multiple jobs. |  | CG-08; CG-09 | Restart storm after outage overwhelms storage; Concurrent checkpoints time out; Noisy neighbour degrades inference | FailureScenario; Safeguard; CapacityAssertion | Burst tests in maintenance windows only. | If restart read-storm behaviour is untested, record U5 UNKNOWN and link to MCF-STO-018. | IO500 benchmark methodology (HPC storage performance); AIDCF-004 (Threat, Hazard and Failure Model) | MCF-STO-005; MCF-STO-018; MCF-CMP-012; MCF-NET-007 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-STO-009 | STO | AI Storage and Data Infrastructure | STO-03 | Integrity and consistency | Data Integrity | Ensure data, checkpoints and model artefacts are protected end-to-end against undetected corruption from client to media and back, so that silent corruption cannot enter training or deployment. | The storage engineering authority shall implement end-to-end integrity protection (application or file-level checksums on checkpoints and artefacts, plus storage-level checksums or protection information) and shall verify checksums on read and on restore. The AI platform operator shall verify checkpoint checksums before resuming training from them and shall treat a verification failure as an integrity incident. | 1) Checksum or protection-information mechanisms cover the path from client to media. 2) Checkpoints and artefacts carry application-level checksums recorded at write. 3) Checksums are verified on restore and before resume (sampled). 4) Verification failures are treated as integrity incidents with impact analysis. 5) Detection effectiveness was demonstrated by injected corruption on a test copy. | Checksum coverage of checkpoints and artefacts [%] default 100 (illustrative) (Capability profile) | Integrity architecture description; Checkpoint/artefact checksum records; Resume-time verification logs; Integrity incident records; Corruption-injection test record | TEST; REPERFORMANCE; ANALYSIS; DOCUMENT_REVIEW | 1) Review integrity architecture. 2) Recompute checksums on sample. 3) Review resume-time verification. 4) Review injection test. | DETECTIVE | EFFECTIVENESS | AL5 | DESIGN; COMMISSION; OPERATE | NORMAL; DEGRADED; RECOVERY | Applies to all in-scope training data, checkpoints and model artefacts. | CG-08 |  | Silent corruption in checkpoint resumed into training; Bit flip in transit undetected; Corrupt model deployed | Safeguard; FailureMode; EvidenceObject | Corruption injection only on test copies in isolated namespaces. Tests run against test namespaces or copies; no destructive action against production data, snapshots or recovery copies is permitted without the data owner's written authorisation. | If no end-to-end checksum exists for a data class, record US4 UNKNOWN for that class. | T10 Protection Information (SCSI) and NVMe end-to-end data protection; ISO/IEC 27040 (storage security); NIST SP 800-209 (security guidelines for storage infrastructure) | MCF-STO-011; MCF-STO-017; MCF-CMP-019; MCF-STO-020 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-STO-010 | STO | AI Storage and Data Infrastructure | STO-03 | Integrity and consistency | Metadata Integrity | Ensure file-system or object-store metadata (namespace, layout, allocation, object maps) is protected, consistent and recoverable, because metadata loss can render intact data unreachable for the whole tier. | The storage engineering authority shall protect metadata with redundancy independent of the data path (replicated metadata servers or volumes), shall run consistency checks at a defined interval, shall back up metadata where the platform supports it, and shall demonstrate metadata service failover and recovery on a test system or in a controlled test. | 1) Metadata redundancy is configured and independent of single server or enclosure. 2) Consistency checks run at the interval and results are reviewed. 3) Metadata backups exist where supported and have been restored on test. 4) Metadata failover has been demonstrated within the declared time. 5) Metadata service failures in the period were contained. | Metadata failover time [s] default 60 (illustrative) (Capability profile; vendor data) Consistency check interval [days] default 30 (illustrative) (Vendor guidance) | Metadata redundancy configuration; Consistency check results; Metadata backup and test restore records; Failover test record | TEST; DOCUMENT_REVIEW; ANALYSIS | 1) Review redundancy. 2) Review checks and backups. 3) Review failover test. | PREVENTIVE | EFFECTIVENESS | AL5 | COMMISSION; OPERATE; CHANGE | NORMAL; DEGRADED; FAILED; RECOVERY | Applies to all in-scope storage systems with separate metadata services. | CG-08 | CG-10 | Metadata corruption making tier unreadable; Metadata failover hang during training; Shared metadata volume single point of failure | InfrastructureSystem; Safeguard; FaultDomain; TestRecord | Failover tests on production need storage engineering authority approval and a maintenance window. Tests run against test namespaces or copies; no destructive action against production data, snapshots or recovery copies is permitted without the data owner's written authorisation. | If metadata failover is untested, record US4 UNKNOWN against CG-08. | ISO/IEC 27040 (storage security); AIDCF-004 (Threat, Hazard and Failure Model) | MCF-STO-006; MCF-STO-019; MCF-STO-020 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-STO-011 | STO | AI Storage and Data Infrastructure | STO-03 | Integrity and consistency | Checksum and Scrubbing | Detect latent media and data errors before they are needed by scrubbing stored data and verifying checksums on a schedule that completes within the declared cycle. | The storage service owner shall schedule scrubbing so that all data on in-scope tiers is verified within the declared cycle, shall monitor scrub completion and error rates, and shall repair detected errors from redundancy promptly. | 1) Scrub schedule covers all in-scope tiers. 2) Scrub cycles completed within the declared period. 3) Detected errors were repaired and trended. 4) Scrub impact on production performance is bounded. | Scrub cycle [days] default 30 (illustrative) (Vendor guidance; capability profile) | Scrub schedule; Scrub completion records; Error and repair logs | ANALYSIS; DOCUMENT_REVIEW | 1) Review scrub schedule coverage of all tiers. 2) Analyse completion of the last three cycles. 3) Review detected errors and their repair from redundancy. | DETECTIVE | OPERATION | AL4 | OPERATE | NORMAL; DEGRADED | Applies to in-scope tiers with redundancy that supports repair. |  | CG-08 | Latent sector errors accumulating; Scrub never completing on large tiers | Safeguard; EvidenceObject | Read-only review of scrub logs; scrub schedules are not altered. | If scrub completion cannot be shown, record U1 UNKNOWN. | ISO/IEC 27040 (storage security) | MCF-STO-009; MCF-STO-023; MCF-STO-015 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-STO-012 | STO | AI Storage and Data Infrastructure | STO-03 | Integrity and consistency | Configuration Consistency | Ensure storage configuration (protection schemes, quotas, exports, client mount options, QoS, replication policies, retention locks) matches the approved baseline across all storage systems and clients. | The storage service owner shall maintain an approved storage configuration baseline, shall detect drift automatically, shall apply changes under change control with post-change verification, and shall verify client mount options and versions across the fleet. | 1) An approved baseline exists. 2) Drift detection runs and drift is remediated. 3) Changes have change records and post-change verification. 4) Client mount options and versions conform across sampled nodes. |  | Configuration baseline; Drift reports; Change records; Client mount survey | RECONCILIATION; SAMPLING; DOCUMENT_REVIEW | 1) Obtain baseline. 2) Review drift. 3) Sample client mounts. 4) Review changes. | PREVENTIVE | IMPLEMENTATION | AL3 | BUILD; OPERATE; CHANGE | NORMAL; MAINTENANCE; TRANSITION | Applies to all in-scope storage systems and clients. |  | CG-14; CG-08 | Replication policy silently disabled; Client mount options degrading performance; Retention lock removed | ArchitectureSnapshot; AssetInstance | Read-only configuration exports and client mount surveys. | Systems without drift detection are U5 coverage-gap UNKNOWN. | NIST SP 800-209 (security guidelines for storage infrastructure); ISO/IEC 27040 (storage security) | MCF-STO-014; MCF-STO-016; MCF-OPS-017; MCF-SEC-008 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-STO-013 | STO | AI Storage and Data Infrastructure | STO-04 | Protection and replication | Snapshot Protection | Ensure snapshots of datasets, artefact registries and checkpoint directories are taken at the declared frequency, retained, protected from deletion by ordinary users, and actually restorable, to recover from accidental deletion or logical corruption. | The storage service owner shall configure snapshot schedules and retention per protected namespace, shall restrict snapshot deletion to authorised roles, shall monitor snapshot success, and shall restore from snapshot on a sample basis at a defined interval. | 1) Snapshot schedules and retention are configured per protected namespace. 2) Snapshot success rate is monitored and failures remediated. 3) Snapshot deletion is restricted and logged. 4) Sample restores from snapshot succeeded within the period. | Snapshot recovery point objective [h] default 4 (illustrative) (Capability profile) Snapshot retention [days] default 14 (illustrative) (Capability profile) | Snapshot policy configuration; Success monitoring; Deletion permission configuration and logs; Sample restore records | ANALYSIS; SAMPLING; TEST | 1) Review snapshot policies per protected namespace. 2) Analyse snapshot success over the period. 3) Review snapshot deletion permissions and logs. 4) Review sample restore results. | PREVENTIVE | OPERATION | AL4 | OPERATE | NORMAL; RECOVERY | Applies to namespaces holding in-scope data. Snapshots do not satisfy MCF-STO-016 because they share the storage system's fault and administrative domain. |  | CG-10 | Snapshots silently failing; Snapshot deleted by compromised user; Snapshots on same system as corruption | Safeguard; TestRecord | Restores to test namespace only. Tests run against test namespaces or copies; no destructive action against production data, snapshots or recovery copies is permitted without the data owner's written authorisation. | If no sample restore exists, record U1 UNKNOWN for recoverability. | NIST SP 800-34 (contingency planning guide for information systems); ISO/IEC 27031 (ICT readiness for business continuity) | MCF-STO-016; MCF-STO-020 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-STO-014 | STO | AI Storage and Data Infrastructure | STO-04 | Protection and replication | Replication | Ensure data required for recovery is replicated to a target in an independent fault domain (another hall, site or region) within the declared recovery point objective, within permitted jurisdictions, and that replication lag and failures are detected. | The storage service owner shall define replication scope, target, mode (synchronous or asynchronous) and RPO per data class, shall place targets outside the source's power, cooling, network and administrative fault domains as declared, shall keep targets within permitted jurisdictions, shall monitor lag, and shall demonstrate failover or restore from the replica. | 1) Replication scope, target, mode and RPO are defined per data class. 2) Target fault-domain independence is documented. 3) Targets are within permitted jurisdictions. 4) Replication lag stayed within RPO for the period, with alerts on breach. 5) Restore or failover from replica has been demonstrated within the period. | Replication RPO (checkpoints) [min] default 60 (illustrative) (Capability profile) Replication RPO (datasets and artefacts) [h] default 24 (illustrative) (Capability profile) | Replication policy; Fault-domain independence analysis; Jurisdiction mapping; Lag telemetry and alerts; Replica restore/failover test | ANALYSIS; TEST; DOCUMENT_REVIEW; RECONCILIATION | 1) Review policy and independence. 2) Reconcile jurisdictions. 3) Analyse lag. 4) Review restore test. | RECOVERY | RESILIENCE | AL5 | DESIGN; OPERATE; CHANGE | NORMAL; DEGRADED; RECOVERY; EMERGENCY | Applies to data classes whose loss would exceed the recovery tolerance if the primary storage fault domain were lost. |  | CG-10; CG-09; CG-03 | Replica in same fault domain; Replication silently stalled; Corruption replicated to target; Replica in non-permitted jurisdiction | Dependency; FaultDomain; Safeguard; TestRecord | Failover tests require data owner approval and must not reverse replication over good data. Tests run against test namespaces or copies; no destructive action against production data, snapshots or recovery copies is permitted without the data owner's written authorisation. | If target fault-domain independence is not documented, record U10 dependency UNKNOWN. | ISO 22301 (business continuity management systems); ISO/IEC 27031 (ICT readiness for business continuity); NIST SP 800-34 (contingency planning guide for information systems); Regulation (EU) 2016/679 (GDPR) and applicable national data-residency law | MCF-STO-016; MCF-STO-001; MCF-RES-016; MCF-DEP-005 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-STO-015 | STO | AI Storage and Data Infrastructure | STO-04 | Protection and replication | Erasure Coding | Ensure erasure coding or RAID protection is configured so that stripes span independent failure domains (drive, server, enclosure, rack) and tolerate the declared number of concurrent failures, with rebuild completing before a further failure is likely. | The storage engineering authority shall document the protection scheme per tier (for example k+m), the failure domains across which stripes are placed, the number of concurrent domain failures tolerated, and expected rebuild time at current capacity; shall verify placement against physical topology; and shall demonstrate rebuild of a failed component within the declared time. | 1) Protection scheme and failure-domain placement are documented per tier. 2) Placement is verified against physical rack and power topology. 3) Concurrent failure tolerance meets the declared requirement. 4) Rebuild time at current fill is measured and within the declared time. 5) Rebuild performance impact is within the degraded-state minimum (MCF-STO-005). | Protection scheme [k+m] default 8+2 (illustrative) (Capability profile; vendor options) Concurrent failure-domain tolerance [count] default 2 (illustrative) (Capability profile) Rebuild time objective [h] default 24 (illustrative) (Capability profile; vendor data) | Protection configuration; Placement-to-topology reconciliation; Rebuild test or event record | RECONCILIATION; ANALYSIS; TEST | 1) Review protection scheme. 2) Reconcile placement with topology. 3) Review rebuild evidence. | PREVENTIVE | RESILIENCE | AL5 | DESIGN; COMMISSION; OPERATE; CHANGE | NORMAL; DEGRADED; RECOVERY | Applies to all in-scope storage using erasure coding or RAID. | CG-09 | CG-08 | Stripe members in same rack lost together; Rebuild too slow at high fill; Power-feed common mode across enclosures | FaultDomain; Safeguard; CapacityAssertion | Rebuild tests by controlled component removal approved by the storage engineering authority. Tests run against test namespaces or copies; no destructive action against production data, snapshots or recovery copies is permitted without the data owner's written authorisation. | If placement versus topology cannot be verified, record US4 UNKNOWN against CG-09. | ISO/IEC 27040 (storage security); AIDCF-004 (Threat, Hazard and Failure Model) | MCF-STO-005; MCF-STO-023; MCF-RES-005; MCF-CMP-008 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-STO-016 | STO | AI Storage and Data Infrastructure | STO-04 | Protection and replication | Immutable Recovery Copy | Ensure at least one copy of recovery-critical data (latest good checkpoints, model artefacts, key datasets, storage and platform configuration) is immutable for its retention period and held in a separate administrative and fault domain, so that ransomware, privileged-account compromise or operator error cannot destroy every copy. | The storage service owner shall maintain an immutable recovery copy of declared recovery-critical data with retention locks that cannot be shortened by administrators of the primary system, in a separate administrative domain with separate credentials, and shall demonstrate restore from it within the declared time. | 1) Recovery-critical data scope is declared. 2) Immutable copy exists with retention locks in compliance (non-shortenable) mode. 3) Administrative domain and credentials are separate from the primary. 4) Attempted deletion by a primary-domain administrator is refused (tested). 5) Restore from the immutable copy met the declared time within the period. | Immutable retention [days] default 30 (illustrative) (Capability profile) Restore time from immutable copy [h] default 24 (illustrative) (Capability profile) | Scope declaration; Retention-lock configuration; Administrative separation evidence; Deletion-refusal test; Restore test record | TEST; INSPECTION; DOCUMENT_REVIEW; RECONCILIATION | 1) Review scope. 2) Inspect lock configuration. 3) Verify administrative separation. 4) Review deletion-refusal and restore tests. | RECOVERY | RESILIENCE | AL5 | DESIGN; OPERATE; CHANGE | NORMAL; EMERGENCY; RECOVERY | Applies to all Capability Instances whose recovery depends on stored state. | CG-10 | CG-15 | Ransomware encrypts all copies; Privileged admin deletes backups; Retention lock in governance mode bypassed | Safeguard; FaultDomain; TestRecord | Deletion-refusal tests use a test object and test account. Tests run against test namespaces or copies; no destructive action against production data, snapshots or recovery copies is permitted without the data owner's written authorisation. | If the immutable copy shares administrative credentials with primary, record a Finding; if untested, US4 UNKNOWN. | NIST SP 800-209 (security guidelines for storage infrastructure); ISO/IEC 27040 (storage security); NIST SP 800-34 (contingency planning guide for information systems); ISO 22301 (business continuity management systems) | MCF-STO-013; MCF-STO-014; MCF-STO-020; MCF-SEC-003 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-STO-017 | STO | AI Storage and Data Infrastructure | STO-05 | Checkpoint and recovery services | Checkpoint Durability | Ensure each checkpoint is complete, consistent across all shards and ranks, durably committed and verifiable before it is marked good and before older checkpoints are deleted. | The AI platform operator shall mark a checkpoint good only after all shards are written, flushed to durable storage, checksummed and manifest-recorded; shall never delete the previous good checkpoint until the new one is verified; and shall retain the declared number of good checkpoints. The storage service owner shall ensure the checkpoint tier honours flush semantics. | 1) Checkpoint completion requires all shards, flush, checksum and manifest. 2) Previous good checkpoint is retained until the new one is verified. 3) Retained count meets the declared value for sampled jobs. 4) Partial or failed checkpoints are detected and not used. 5) A test interrupting a checkpoint mid-write showed the previous good checkpoint remained usable. | Retained good checkpoints [count] default 3 (illustrative) (Capability profile) | Checkpoint manifest examples; Framework configuration; Retention evidence; Interrupted-write test | TEST; REPERFORMANCE; SAMPLING | 1) Sample production jobs and their checkpoint manifests. 2) Verify shard checksums against the manifest. 3) Review retention of previous good checkpoints. 4) Review the interrupted-write test result. | PREVENTIVE | EFFECTIVENESS | AL5 | COMMISSION; OPERATE; CHANGE | NORMAL; DEGRADED; FAILED; RECOVERY | Applies to checkpointed in-scope workloads. | CG-08 | CG-10 | Partial checkpoint marked good; Previous checkpoint deleted before new verified; Asynchronous flush lost on power event | Safeguard; FailureMode; TestRecord | Interrupted-write test on non-production job. | If checkpoint completion semantics are undocumented, record US4 UNKNOWN. | Young/Daly optimum checkpoint interval model (published literature); T10 Protection Information (SCSI) and NVMe end-to-end data protection | MCF-STO-002; MCF-STO-009; MCF-STO-018 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-STO-018 | STO | AI Storage and Data Infrastructure | STO-05 | Checkpoint and recovery services | Restart Readiness | Ensure a training or fine-tuning job can be restarted from its latest good checkpoint on available capacity (including a different set of nodes or a reduced node count where the framework supports re-sharding) within the declared restart time objective. | The AI platform operator shall maintain restart procedures and automation for production job classes, shall verify that checkpoints can be loaded on a different node set, shall measure time from failure to resumed training, and shall exercise restart at a defined interval including after a storage or facility event. | 1) Restart procedures and automation exist per job class. 2) Restart onto a different node set has been demonstrated. 3) Time from failure to resumed training is measured and within objective. 4) Restart after a storage or facility event has been exercised. 5) Dependencies of restart (scheduler, storage, identity, data loaders) are documented. | Restart time objective [min] default 30 (illustrative) (Capability profile) Lost work tolerance [min of training] default 60 (illustrative) (Capability profile; checkpoint interval) | Restart procedures; Restart timing records; Different-node-set restart test; Post-event restart exercise; Dependency list | SCENARIO_EXERCISE; ANALYSIS; DOCUMENT_REVIEW | 1) Review procedures. 2) Analyse restart timings. 3) Review exercises. 4) Review dependencies. | RECOVERY | RESILIENCE | AL5 | COMMISSION; OPERATE | RECOVERY; FAILED; DEGRADED | Applies to checkpointed in-scope workloads whose recovery tolerance relies on resuming rather than restarting from scratch. | CG-10 |  | Checkpoint not loadable on new topology; Restart blocked by storage read storm; Hidden dependency on failed service | FailureScenario; Safeguard; TestRecord; Dependency | Exercises on non-production jobs or with job-owner approval. | If no post-event restart exercise exists, record US4 UNKNOWN against CG-10. | Young/Daly optimum checkpoint interval model (published literature); ISO 22301 (business continuity management systems) | MCF-STO-017; MCF-STO-019; MCF-CMP-023; MCF-RES-016 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-STO-019 | STO | AI Storage and Data Infrastructure | STO-05 | Checkpoint and recovery services | Storage Recovery Sequencing | Ensure that after a site, power or cooling event, storage services are brought back in a defined order (power and cooling verified, network and time, identity, metadata services, data servers, consistency checks, client mounts, then job readmission) so that recovery does not corrupt data or stall on hidden dependencies. | The storage service owner shall maintain a storage recovery sequence with prerequisites, hold points and verification checks for each step, aligned with facility (THM/POW) and compute (CMP) recovery, and shall exercise it at a defined interval. | 1) A recovery sequence exists with prerequisites, hold points and checks. 2) The sequence is aligned with facility and compute recovery sequences. 3) Dependencies (time, DNS, identity, key management) are available independently of storage. 4) The sequence has been exercised and timings recorded. 5) Consistency checks precede client readmission. | Storage recovery time objective [h] default 4 (illustrative) (Capability profile) | Recovery sequence document; Cross-domain alignment record; Dependency analysis; Exercise record | SCENARIO_EXERCISE; DOCUMENT_REVIEW; ANALYSIS | 1) Review sequence and alignment. 2) Review dependency analysis. 3) Review exercise timings. | RECOVERY | RESILIENCE | AL5 | DESIGN; OPERATE; CHANGE | RECOVERY; FAILED; SHUTDOWN | Applies to all in-scope storage systems. |  | CG-10; CG-09 | Clients mount before metadata consistency; Key management unavailable to unlock encrypted storage; Circular dependency on DNS hosted on storage | FailureScenario; Dependency; Safeguard | Tabletop or test-system exercise unless live exercise authorised. | If dependencies on key management or identity are not analysed, record U10 UNKNOWN. | ISO 22301 (business continuity management systems); ISO/IEC 27031 (ICT readiness for business continuity); NIST SP 800-34 (contingency planning guide for information systems) | MCF-STO-018; MCF-STO-020; MCF-RES-014; MCF-THM-024 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-STO-020 | STO | AI Storage and Data Infrastructure | STO-05 | Checkpoint and recovery services | Recovery Validation | Demonstrate by periodic restore tests that every protected data class can be restored from each protection mechanism (snapshot, replica, immutable copy) to a usable, integrity-verified state within the declared recovery time, and that restored checkpoints actually resume training. | The storage service owner shall run restore tests at a defined interval for each protected data class and protection mechanism, shall verify integrity of restored data by checksum, and, for checkpoints, the AI platform operator shall resume a training job from the restored checkpoint and confirm loss and step continuity. | 1) Restore test schedule covers each data class and each protection mechanism. 2) Restores in the period met the recovery time. 3) Restored data passed checksum verification. 4) A restored checkpoint resumed training with expected continuity. 5) Failures were remediated and retested. | Restore test interval [months] default 3 (illustrative) (Capability profile) | Restore test schedule; Restore test records with timings; Checksum verification results; Training resume evidence | TEST; REPERFORMANCE; SAMPLING; ANALYSIS | 1) Review restore schedule coverage by data class and mechanism. 2) Select a sample and review or reperform restores. 3) Verify checksums of restored data against source records. 4) Review training resume evidence for restored checkpoints. | CORRECTIVE | RESILIENCE | AL5 | COMMISSION; OPERATE | RECOVERY; NORMAL | Applies to all protected in-scope data classes. | CG-10 |  | Backups unrestorable; Restored checkpoint incompatible with current framework; Restore slower than objective | TestRecord; Safeguard; EvidenceObject | Restores to isolated test locations only. Tests run against test namespaces or copies; no destructive action against production data, snapshots or recovery copies is permitted without the data owner's written authorisation. | Data classes without a restore test in the interval are US4 UNKNOWN for CG-10. | NIST SP 800-34 (contingency planning guide for information systems); ISO 22301 (business continuity management systems); ISO/IEC 27031 (ICT readiness for business continuity) | MCF-STO-013; MCF-STO-014; MCF-STO-016; MCF-RES-016 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-STO-021 | STO | AI Storage and Data Infrastructure | STO-06 | Storage monitoring and lifecycle | Storage Telemetry | Collect storage telemetry (throughput, IOPS, latency percentiles, metadata latency, capacity, rebuild state, client errors, replication lag) with completeness monitoring and time synchronisation, to detect degradation and support incident analysis. | The storage service owner shall collect telemetry from all in-scope storage systems and a representative sample of clients at the declared interval, shall monitor collection completeness, shall time-synchronise with compute and facility telemetry, and shall alert on thresholds. | 1) Telemetry covers servers, metadata services and sampled clients. 2) Completeness is monitored and meets target. 3) Time is synchronised with compute and facility telemetry. 4) Alerts exist for latency, errors, capacity and lag. | Telemetry interval [s] default 30 (illustrative) (Capability profile) | Storage telemetry schema covering server, metadata and client metrics; Storage collection completeness reports; Time sync configuration; Alert definitions | ANALYSIS; INSPECTION | 1) Review telemetry coverage of servers, metadata services and clients. 2) Analyse completeness and time alignment with compute telemetry. 3) Review alert thresholds and a sample of alert handling. | DETECTIVE | OPERATION | AL4 | COMMISSION; OPERATE | NORMAL; DEGRADED; RECOVERY | Applies to all in-scope storage. |  | CG-08 | Client-side errors invisible to server telemetry; Clock skew preventing correlation | EvidenceObject; AssetInstance | Read-only comparison of stored telemetry with device counters. | If client-side telemetry is absent, record U5 UNKNOWN. | ISO/IEC 27040 (storage security) | MCF-STO-006; MCF-STO-022; MCF-CMP-017; MCF-NET-024 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-STO-022 | STO | AI Storage and Data Infrastructure | STO-06 | Storage monitoring and lifecycle | Capacity Forecasting | Forecast storage capacity and performance demand from planned training runs, dataset growth, checkpoint retention and model registry growth, against procurement lead times, so that expansion arrives before headroom thresholds are reached. | The storage service owner shall forecast capacity and throughput demand over a horizon at least as long as procurement and deployment lead time, using the AI platform's planned workloads, and shall trigger expansion when the forecast crosses headroom thresholds within the lead time. | 1) The forecast horizon is ≥ lead time. 2) Inputs include planned training runs, dataset growth and retention. 3) Forecast accuracy is reviewed against actuals. 4) Expansion triggers fired in time historically. | Forecast horizon [months] default 9 (illustrative) (Procurement lead time) | Forecast model; Input data; Forecast-versus-actual review; Expansion trigger records | ANALYSIS; DOCUMENT_REVIEW; INQUIRY | 1) Review model and inputs. 2) Compare with actuals. 3) Review triggers. | PREVENTIVE | OPERATION | AL4 | PLAN; OPERATE | NORMAL | Applies to all in-scope storage tiers whose growth is driven by planned AI workloads. |  | CG-08 | Expansion arrives after exhaustion; Forecast ignores checkpoint retention | CapacityAssertion; Resource | Desk-based review of forecast and procurement records. | If no forecast exists, record U1 UNKNOWN. | ISO/IEC 27040 (storage security) | MCF-STO-007; MCF-CAP-015; MCF-SUP-018 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-STO-023 | STO | AI Storage and Data Infrastructure | STO-06 | Storage monitoring and lifecycle | Media Health | Monitor drive and media health (SMART/NVMe health logs, wear level, media errors, annualised failure rate by model and lot) and replace degrading media proactively before redundancy is consumed. | The storage service owner shall collect media health indicators, shall define proactive replacement thresholds, shall track failure rates by model and lot, and shall replace media before failure where thresholds are crossed. | 1) Media health indicators are collected for all media. 2) Replacement thresholds are defined. 3) Failure rates by model/lot are tracked. 4) Proactive replacements occurred where thresholds crossed. | NVMe wear replacement threshold [% of rated endurance used] default 90 (illustrative) (Vendor endurance rating) AFR investigation threshold [%] default 2× fleet baseline (illustrative) (Capability profile) | Media health data; Thresholds; AFR trend; Replacement records | ANALYSIS; SAMPLING | 1) Review proactive replacement thresholds against vendor endurance data. 2) Analyse annualised failure rate by model and lot. 3) Sample proactive replacements against threshold crossings. | DETECTIVE | OPERATION | AL4 | OPERATE | NORMAL; DEGRADED | Applies to all in-scope storage media. |  | CG-08 | Batch failure of same lot; Wear-out of checkpoint tier flash | AssetInstance; FailureMode | Read-only access to media health logs. | Media without health data are U5 UNKNOWN. | NVMe Base Specification (SMART / health information log); ISO/IEC 27040 (storage security) | MCF-STO-015; MCF-STO-011; MCF-SUP-012 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-STO-024 | STO | AI Storage and Data Infrastructure | STO-06 | Storage monitoring and lifecycle | Secure Sanitisation | Ensure storage media and systems leaving service, RMA or tenant reassignment are sanitised to a recognised standard with verification, so that training data, model weights and credentials cannot be recovered. | The storage service owner shall sanitise media by clear, purge or destroy methods appropriate to media type and data classification under a recognised sanitisation standard, shall verify sanitisation, shall issue per-device certificates, and shall keep custody until sanitisation or destruction is complete, including for media sent for RMA. | 1) Method per media type and classification is defined. 2) Per-device sanitisation certificates exist for sampled devices. 3) Verification is performed and recorded. 4) Custody is maintained until completion including RMA. 5) Cryptographic erase key destruction is evidenced where used. |  | Sanitisation procedure; Per-device certificates; Verification records; Media custody records including RMA shipments | SAMPLING; DOCUMENT_REVIEW | 1) Sample devices retired or sent for RMA in the period. 2) Verify method against media type and data classification. 3) Verify certificates and verification records. 4) Trace custody until sanitisation or destruction. | PREVENTIVE | IMPLEMENTATION | AL3 | DECOMMISSION | SHUTDOWN; TRANSITION | Applies to all media that held in-scope data. |  |  | Data recoverable from RMA drive; Crypto-erase without key destruction evidence | AssetInstance; Action; Safeguard | Record review only. | Devices without certificates are U1 UNKNOWN and Findings. | NIST SP 800-88 (guidelines for media sanitisation); IEEE 2883 (standard for sanitizing storage); ISO/IEC 27040 (storage security) | MCF-CMP-024; MCF-PHY-019; MCF-ENV-020 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-NET-001 | NET | AI Network and Interconnect Architecture | NET-01 | Scale-up and scale-out fabrics | Fabric Topology | Ensure the scale-up and scale-out fabrics are built to an approved topology whose bisection bandwidth, tiering, rail assignment and endpoint attachment match what the declared training and inference Service Outcomes require. | The network architecture owner shall maintain an approved topology design for every back-end (scale-out) fabric and scale-up domain in scope, stating the topology class (for example rail-optimised multi-plane, two-tier leaf-spine or three-tier fat-tree/Clos, or rack-scale scale-up domain), switch radix, tier count, rail and plane assignment, endpoint-to-leaf mapping and the design bisection bandwidth per Capability Instance. The fabric operations lead shall reconcile the as-built fabric (LLDP or subnet-manager discovered topology, cabling records and port maps) to the approved design at commissioning and after every material change, and shall record every deviation as either an approved variance or a Finding. | 1) An approved topology design exists for each in-scope fabric and identifies topology class, tiers, radix, planes/rails, endpoint attachment and design bisection bandwidth. 2) Discovered topology (LLDP neighbour tables, InfiniBand subnet-manager topology dump or controller inventory) reconciles to the design with all mismatched, missing or miswired links listed and dispositioned. 3) Each accelerator NIC port is attached to the rail/plane and leaf required by the design; rail-mapping errors are zero or individually approved. 4) Design bisection bandwidth and per-endpoint injection bandwidth are traceable to the Service Outcome performance requirement for the Capability Instance. 5) Topology changes since the last reconciliation are linked to approved change records. | Rail-mapping conformance [% of accelerator ports on design rail/leaf] default 100 (illustrative) (Rail-optimised designs assume ordinal NIC n connects to rail n; any deviation alters collective paths. Site-specific.) Maximum topology reconciliation age [days] default 90 (illustrative) (Capability-profile parameter; shorten where change rate is high.) | Approved fabric topology design and high-level design document, with version and approver; Discovered topology export (LLDP tables, subnet-manager topology file or fabric-controller inventory) dated within the reconciliation window; Automated or manual reconciliation report of discovered versus designed links and port maps; Rail/plane mapping table per node type; Change records for topology modifications since the previous reconciliation | DOCUMENT_REVIEW; RECONCILIATION; ANALYSIS; SAMPLING; INSPECTION | 1) Obtain the approved topology design and confirm its version applies to the assessed Capability Instance. 2) Extract discovered topology from switches or the subnet manager using read-only collection. 3) Run or reperform the reconciliation of discovered links, port speeds and neighbours against design port maps. 4) Verify rail and plane assignment for a sample of nodes of each type, including recently replaced nodes. 5) Trace design bisection bandwidth to the Service Outcome performance requirement and to NET-003 oversubscription analysis. 6) Disposition every mismatch as approved variance or Finding and record residual UNKNOWNs. | PREVENTIVE | IMPLEMENTATION | AL3 | DESIGN; BUILD; COMMISSION; CHANGE | NORMAL; MAINTENANCE; TRANSITION | Applies to every back-end scale-out fabric (InfiniBand or Ethernet/RoCEv2) and every scale-up domain supporting an in-scope Capability Instance. Front-end and storage networks are covered by NET-009 and NET-010. Not applicable to single-node inference with no inter-node fabric, subject to approved rationale. | CG-08 | CG-02 | Miswired or missing links reducing effective bisection bandwidth; Rail-mapping error forcing cross-rail traffic through spine; Undocumented topology drift after expansion; Mixed link speeds negotiated below design rate | ArchitectureSnapshot; InfrastructureSystem; AssetInstance; Interface; CapacityAssertion | Topology collection shall use read-only interfaces and credentials. Re-cabling or port disablement to verify mapping shall not be performed on a production fabric without an approved change and workload owner consent. | If discovered topology cannot be obtained for a gate-critical fabric, or reconciliation coverage is below the full fabric without a justified sample, record a US4 UNKNOWN against CG-08 and do not infer conformance from design documents. | InfiniBand Trade Association, InfiniBand Architecture Specification (Volumes 1 and 2); InfiniBand Trade Association, RoCEv2 annex to the InfiniBand Architecture Specification; IETF RFC 7938 (Use of BGP for routing in large-scale data centres); AIDCF-013 (AI Data Centre Assurance Reference Architecture) | MCF-NET-002; MCF-NET-003; MCF-NET-020; MCF-CMP-005; MCF-CMP-006 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-NET-002 | NET | AI Network and Interconnect Architecture | NET-01 | Scale-up and scale-out fabrics | Path Diversity | Ensure that logical redundancy in fabrics, inter-hall links and WAN/DCI connections is matched by physically diverse paths, so a single cable route, conduit, carrier or building entry cannot defeat redundant connectivity. | The network architecture owner shall define, for each redundant path group (spine uplinks between halls, storage and front-end uplinks, WAN and data-centre interconnect circuits, OOB uplinks), the required diversity attributes: separate cable routes and containment, separate building entries, separate carriers or carrier-neutral dark-fibre routes, and separate optical line systems where DWDM is used. The connectivity manager shall obtain route evidence (carrier KMZ or route maps, cable-route surveys, containment records) for each path and shall record every shared segment, shared conduit, shared meet-me room or shared upstream carrier as a common-mode dependency. | 1) Each redundant path group has documented diversity requirements derived from the outcome criticality. 2) Route evidence for each external circuit identifies building entry, route and any shared segments to a defined granularity. 3) Intra-site redundant trunks are routed in separate containment or the shared section is analysed and accepted. 4) Carrier diversity accounts for wholesale or tail-circuit sharing (diverse brand on a shared underlying route is not treated as diverse). 5) Shared segments are registered as common-mode dependencies with owners and linked to DEP-007. 6) Diversity is re-verified after carrier grooming or re-routing notices. | Minimum physical separation between diverse routes [m] default Site-specific; set by risk analysis (illustrative: separate containment and entry points) (Capability-profile parameter; no universal distance applies.) Route evidence age [months] default 12 (illustrative) (Carriers re-groom circuits; evidence ages.) | Path-group register listing redundant groups and diversity requirements; Carrier route documentation (maps, KMZ or route letters) for WAN/DCI circuits; Internal cable-route and containment drawings for inter-hall trunks; Common-mode analysis of shared segments with dispositions; Carrier notifications of re-routing and the review of each | DOCUMENT_REVIEW; INSPECTION; ANALYSIS; RECONCILIATION; INQUIRY | 1) List all redundant path groups and their stated diversity requirements. 2) Collect route evidence for each member path and overlay routes to identify shared segments, entries and nodes. 3) Walk down building entries, risers and inter-hall containment for a sample of paths. 4) Check whether diverse carriers share wholesale tails, ducts or landing points. 5) Confirm each shared segment is in the dependency register with an owner and disposition. 6) Review carrier change notices for unreviewed re-routing. | PREVENTIVE | IMPLEMENTATION | AL3 | DESIGN; BUILD; OPERATE; CHANGE | NORMAL; MAINTENANCE; DEGRADED | Applies to every network path relied upon as redundant for an in-scope outcome, including WAN/DCI used for multi-site training, replication or alternate capacity. Not applicable to paths whose loss is explicitly tolerated by the Service Outcome. |  | CG-03; CG-08; CG-09 | Single excavation severing both 'diverse' DCI circuits; Both trunks in one cable tray exposed to one fire; Diverse carriers sharing one wholesale route; Silent carrier re-grooming removing diversity | Dependency; FaultDomain; Interface; Resource | Route verification is non-intrusive. Failover tests between diverse circuits shall be scheduled under change control with the service owner, and shall not be performed during declared DEGRADED states. | If a route for any member of a redundant path group cannot be evidenced, record UNKNOWN U2 or U10 and treat the group as non-diverse for CG-03 and blast-radius analysis until evidenced. | ANSI/TIA-942 (Telecommunications infrastructure standard for data centres); EN 50600 series / ISO/IEC 22237 series (Data centre facilities and infrastructures); AIDCF-004 (Threat, Hazard and Failure Model) | MCF-DEP-007; MCF-DEP-010; MCF-NET-020; MCF-RES-011; MCF-PHY-010 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-NET-003 | NET | AI Network and Interconnect Architecture | NET-01 | Scale-up and scale-out fabrics | Oversubscription | Ensure each fabric tier's oversubscription ratio is a deliberate design decision justified against the expected traffic matrix of the declared workloads, so collective and storage traffic are not throttled by uplink scarcity. | The network architecture owner shall state the design oversubscription ratio at every tier boundary (leaf-to-spine, spine-to-superspine, pod-to-core, storage and front-end uplinks) and shall justify each ratio against the traffic matrix of the declared workloads, including all-reduce, all-to-all (for example expert-parallel) and checkpoint bursts. The fabric operations lead shall re-derive effective oversubscription after link failures, partial builds and planned maintenance, and shall record the minimum tolerated effective ratio for each Service Outcome. | 1) Design oversubscription ratios are stated per tier and per fabric. 2) Each ratio is justified by a traffic-matrix or workload analysis covering the collective patterns and checkpoint traffic of declared workloads. 3) Effective oversubscription under N-1 uplink and N-1 spine conditions is calculated and compared to the tolerated ratio. 4) Partial-build or phased-expansion states that temporarily increase oversubscription are identified with accepted limitations. 5) Back-end fabrics designated non-blocking are verified to have uplink capacity equal to downlink capacity at each tier. | Back-end fabric design oversubscription [ratio (downlink:uplink)] default 1:1 (illustrative) (Common design choice for large training fabrics; site and workload specific.) Front-end/storage uplink oversubscription [ratio] default Workload-derived (illustrative 3:1) (Capability-profile parameter justified by traffic analysis.) Minimum tolerated effective ratio under N-1 [ratio] default Set per Service Outcome (illustrative 1.15:1 for back-end) (Derived from performance outcome tolerance.) | Fabric design ratio table per tier; Traffic-matrix or workload communication analysis for declared workloads; N-1 effective-capacity calculation; Phased-build limitation statements | DOCUMENT_REVIEW; ANALYSIS; INQUIRY | 1) Obtain the per-tier ratio table and the topology design from NET-001. 2) Recompute ratios from port counts and speeds. 3) Review the workload traffic analysis and confirm it covers declared collectives and checkpoint bursts. 4) Calculate effective ratios under N-1 uplink and N-1 spine and compare to tolerated values. 5) Record limitations for phased-build states. | PREVENTIVE | DESIGN | AL2 | PLAN; DESIGN; CHANGE | NORMAL; DEGRADED; MAINTENANCE; TRANSITION | Applies to every multi-tier fabric in scope. Single-tier fabrics need only the endpoint-to-switch capacity check. |  | CG-08 | Uplink scarcity throttling all-to-all traffic; Checkpoint burst saturating storage uplinks; Ratio degrading beyond tolerance after spine loss; Phased build left in temporary state | CapacityAssertion; InfrastructureSystem; OperatingState | Analytical; no production traffic injection is required. Synthetic load tests belong to NET-007/NET-008 and require scheduling with workload owners. | If no traffic analysis exists for a declared workload class, record UNKNOWN U1 against the performance outcome and do not accept a ratio solely on vendor reference designs. | IETF RFC 7938 (Use of BGP for routing in large-scale data centres); InfiniBand Trade Association, InfiniBand Architecture Specification (Volumes 1 and 2); AIDCF-013 (AI Data Centre Assurance Reference Architecture) | MCF-NET-001; MCF-NET-008; MCF-NET-009; MCF-CAP-006; MCF-STO-008 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-NET-004 | NET | AI Network and Interconnect Architecture | NET-01 | Scale-up and scale-out fabrics | Fabric Fault-Domain Design | Ensure fabric failure domains (switch, rail, plane, pod, spine group, subnet manager, controller, power feed and cooling zone) are designed so that any single credible failure stays within a blast radius the Service Outcome tolerates. | The network architecture owner shall define the fault domains of each fabric, including each switch, rail, plane, pod, spine group, subnet manager or fabric controller instance, and the power and cooling zones serving fabric equipment, and shall state for each the maximum affected endpoints and the resulting outcome impact. The fabric operations lead shall demonstrate, by controlled test or by analysed incident, that loss of a leaf, a spine, a rail or plane, a subnet-manager master and one power feed to a switch row each stay within the declared blast radius, and that fabric equipment does not share an undisclosed power or cooling fault domain with its own redundancy. | 1) Fault-domain register for each fabric lists domain, members, maximum affected endpoints and tolerated impact. 2) Redundant fabric elements (spines, planes, subnet managers, controllers) are not co-located in a single power distribution path, cooling zone or rack without accepted rationale. 3) Loss of a single leaf, spine, plane or subnet-manager master has been tested or observed, and the measured effect (endpoints lost, job failures, reroute time) is within declared tolerance. 4) Fabric behaviour that widens a failure (for example PFC pause propagation, routing reconvergence storms or subnet-manager sweep load) is analysed and bounded. 5) Fault domains reconcile to CMP-008 compute fault domains and RES-005 site fault domains. 6) Residual multi-element failure scenarios outside tolerance are recorded with accepted limitations. | Maximum endpoints affected by a single switch failure [accelerator ports] default Equal to leaf downlink count (illustrative) (Derived from topology; outcome-specific tolerance.) Maximum reroute/reconvergence time after single spine loss [s] default Set by job collective timeout margin (illustrative 30) (Must be below framework collective timeouts; site-specific.) Subnet-manager failover time [s] default Vendor- and scale-dependent (illustrative 60) (Capability-profile parameter verified by test.) | Fabric fault-domain register and blast-radius analysis; Power and cooling mapping of fabric switches, subnet managers and controllers; Test records or incident analyses for leaf, spine, plane and subnet-manager failure; PFC-propagation and reconvergence analysis; Reconciliation to compute and site fault-domain models | DOCUMENT_REVIEW; ANALYSIS; TEST; SCENARIO_EXERCISE; RECONCILIATION | 1) Review the fault-domain register and confirm completeness against NET-001 topology. 2) Map each fabric element to its power path and cooling zone and identify co-location of redundant elements. 3) Review test plans and results for single-element failures, checking measured blast radius and reroute time. 4) Analyse PFC pause propagation and routing reconvergence as failure-widening mechanisms. 5) Reconcile fabric fault domains with CMP-008 and RES-005. 6) Record residual scenarios outside tolerance and their acceptance status. | PREVENTIVE | RESILIENCE | AL5 | DESIGN; COMMISSION; OPERATE; CHANGE | NORMAL; DEGRADED; MAINTENANCE; FAILED; RECOVERY | Applies to all fabrics supporting in-scope Capability Instances. For fabrics where loss of any element is tolerated by job restart from checkpoint, the analysis still applies but tolerance may be expressed as lost work. | CG-09 | CG-08; CG-03 | Both subnet managers on one PDU; Spine group sharing one cooling zone; PFC storm spreading a single NIC fault fabric-wide; Reconvergence exceeding collective timeouts and killing all jobs | FaultDomain; FailureScenario; Dependency; TestRecord; InfrastructureSystem | Element-failure tests on a production fabric (switch power-off, link shutdown, subnet-manager failover) are disruptive and shall only be performed with written authorisation from the service owner and network change board, a rollback plan, workload drain or owner consent, and monitoring in place. Power-feed removal tests require electrical authorisation under OPS-007 permit-to-work. | Where blast radius has only been asserted by the vendor and not tested or observed locally, record UNKNOWN U8 (method uncertain) at US4 against CG-09. | InfiniBand Trade Association, InfiniBand Architecture Specification (Volumes 1 and 2); IEEE 802.1Qbb (Priority-based Flow Control); IETF RFC 7938 (Use of BGP for routing in large-scale data centres); AIDCF-004 (Threat, Hazard and Failure Model); AIDCF-013 (AI Data Centre Assurance Reference Architecture) | MCF-CMP-008; MCF-RES-005; MCF-RES-007; MCF-NET-021; MCF-POW-015 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-NET-005 | NET | AI Network and Interconnect Architecture | NET-02 | Performance and congestion control | Latency Baseline | Ensure the fabric has a measured latency baseline (idle and loaded, per path class) against which degradation can be detected and Service Outcome performance claims tested. | The fabric operations lead shall establish and maintain latency baselines for each path class (intra-leaf, intra-pod, cross-spine, cross-plane, storage path, front-end path) including idle round-trip time, loaded tail latency at defined percentiles and switch-hop count, measured with a repeatable method (for example perftest-class RDMA latency tools or active probing). The fabric operations lead shall alert on deviation from baseline beyond a defined threshold and shall re-baseline after any material NOS, firmware, topology or congestion-control change. | 1) Baselines exist per path class with method, tool, message size and date recorded. 2) Tail latency percentiles are captured under representative load, not only idle conditions. 3) Continuous or periodic probing compares current latency to baseline and alerts on deviation. 4) Re-baselining occurred after each material change in the period. 5) Deviations exceeding the threshold in the period were investigated and closed. | Latency deviation alert threshold [% above baseline at p99] default 25 (illustrative) (Capability-profile parameter tuned to measurement noise.) Baseline percentile set [percentiles] default p50, p99, p99.9 (illustrative) (Tail latency drives synchronous collective step time.) | Baseline report per path class with method details; Probe telemetry for the assessment period; Alert and investigation records for deviations; Change-linked re-baseline records | DOCUMENT_REVIEW; ANALYSIS; SAMPLING; OBSERVATION | 1) Review baseline reports for method repeatability and coverage of path classes. 2) Sample probe telemetry across the period and compare against baselines. 3) Trace deviations to alerts and investigation records. 4) Verify re-baselining after material changes recorded in NET-022. | DETECTIVE | OPERATION | AL4 | COMMISSION; OPERATE; CHANGE | NORMAL; DEGRADED; MAINTENANCE | Applies to latency-sensitive fabrics supporting training or low-latency inference outcomes. May be limited to idle baselines for batch-only storage networks with approved rationale. |  | CG-08 | Silent latency regression after firmware update; Degraded optic causing retransmission-driven tail latency; Unnoticed path asymmetry after reroute | CapacityAssertion; EvidenceObject; InfrastructureSystem | Active probes shall be rate-limited and run in a dedicated traffic class; loaded-latency measurements on production fabrics require scheduling with workload owners. | If baselines predate the current NOS/firmware baseline, treat them as stale (U3) and do not use them to support performance claims. | InfiniBand Trade Association, InfiniBand Architecture Specification (Volumes 1 and 2); InfiniBand Trade Association, RoCEv2 annex to the InfiniBand Architecture Specification; AIDCF-013 (AI Data Centre Assurance Reference Architecture) | MCF-NET-006; MCF-NET-008; MCF-NET-023; MCF-CMP-020 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-NET-006 | NET | AI Network and Interconnect Architecture | NET-02 | Performance and congestion control | Loss and Retransmission | Ensure packet loss, link errors and transport retransmissions are monitored against thresholds so that degrading links, optics and lossless-class failures are detected before they defeat job progress. | The fabric operations lead shall monitor, per port and per traffic class, pre-FEC and post-FEC bit error indicators, FEC corrected and uncorrectable codeword counts, CRC/symbol errors, link flaps, discards, and RDMA transport retransmission and out-of-sequence counters at NICs, against defined thresholds. The fabric operations lead shall automatically isolate or drain links that exceed uncorrectable-error or flap thresholds, shall track each to closure, and shall verify that the lossless traffic class shows no congestion drops under normal operation. | 1) Thresholds are defined for FEC uncorrectable codewords, symbol/CRC errors, link flaps and NIC retransmission rates. 2) Collection covers all switch ports and NICs in the fabric with gaps listed. 3) Links breaching thresholds were isolated or drained and tracked through remediation in the period. 4) The lossless (RDMA) traffic class shows zero congestion drops in normal operation, or each drop event is explained. 5) Trend analysis identifies slow-burn degradation (rising corrected-error rates) before uncorrectable thresholds are reached. | Link flap isolation threshold [flaps per hour] default 3 (illustrative) (Capability-profile parameter.) Post-FEC uncorrectable codeword threshold [count per interval] default Any non-zero sustained (illustrative) (Post-FEC errors become packet loss; vendor guidance applies.) Pre-FEC BER warning threshold [BER] default Vendor/PHY specific (illustrative: one order of magnitude below FEC limit) (Set from IEEE 802.3 FEC capability and vendor guidance.) | Threshold configuration in monitoring system; Error counter telemetry for all ports for the period; Auto-isolation or drain events and tickets; Lossless-class drop counters; Trend reports | ANALYSIS; SAMPLING; DOCUMENT_REVIEW; OBSERVATION | 1) Review threshold definitions against PHY and vendor guidance. 2) Confirm telemetry coverage across switch ports and NICs and list gaps. 3) Sample breaching links and trace isolation, ticket and remediation. 4) Inspect lossless-class drop counters and explain each event. 5) Review trend analysis for slow-burn degradation detection. | DETECTIVE | OPERATION | AL4 | COMMISSION; OPERATE | NORMAL; DEGRADED; MAINTENANCE | Applies to all back-end, storage and front-end fabrics. Lossless-class criteria apply only to fabrics carrying RDMA over Ethernet or InfiniBand. |  | CG-08 | Marginal optic causing intermittent uncorrectable errors and job stalls; Link flapping triggering repeated reroute; Lossless-class drops due to misconfigured PFC headroom; Slow optical degradation unnoticed | FailureMode; AssetInstance; EvidenceObject; Event | Monitoring review only. Deliberate error injection or link disablement requires change approval and workload owner consent. | If NIC-side retransmission counters are not collected, record U5 coverage gap; switch-side counters alone shall not support a claim of transport health. | IEEE 802.3 (Ethernet, including optical PHY and FEC clauses); InfiniBand Trade Association, InfiniBand Architecture Specification (Volumes 1 and 2); InfiniBand Trade Association, RoCEv2 annex to the InfiniBand Architecture Specification; IEEE 802.1Qbb (Priority-based Flow Control) | MCF-NET-005; MCF-NET-007; MCF-NET-018; MCF-NET-023; MCF-CMP-019 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-NET-007 | NET | AI Network and Interconnect Architecture | NET-02 | Performance and congestion control | Congestion Control | Ensure congestion control and lossless configuration (ECN marking, PFC, DCQCN-style or vendor rate control, adaptive routing, InfiniBand credit-based flow control) keep fabrics stable under incast and many-to-one load, and that lossless-mode hazards such as PFC storms and deadlocks are prevented or contained. | The network architecture owner shall define a congestion-control design per fabric stating traffic-class mapping, ECN marking thresholds, PFC enablement and headroom per priority, PFC watchdog behaviour, end-host rate-control algorithm and parameters, and adaptive routing settings, and shall analyse the design for cyclic buffer dependency (PFC deadlock) and pause-storm propagation. The fabric operations lead shall verify by controlled test that incast and congestion scenarios representative of declared workloads do not cause lossless-class drops, sustained pause propagation beyond the congested port, or deadlock, and that the PFC watchdog detects and breaks a stuck-pause condition within the configured time. | 1) A congestion-control design states class mapping, ECN thresholds, PFC priorities and headroom, watchdog settings, NIC rate-control parameters and routing behaviour. 2) Device configurations across the fabric match the design for all congestion-related parameters (sampled or fully reconciled). 3) Deadlock analysis demonstrates absence of cyclic buffer dependency under normal and failure routing, or mitigations (for example limiting lossless classes, routing restrictions) are in place. 4) Incast/congestion tests representative of declared workloads show no lossless-class drops and bounded pause propagation. 5) A simulated stuck-pause (pause-storm) condition is detected and isolated by the PFC watchdog or equivalent within the configured time. 6) ECN marking and congestion notification counters are monitored and show expected behaviour in operation. | PFC watchdog detection time [ms] default Vendor default unless tuned (illustrative 200) (Configured per NOS; verified by test.) Maximum tolerated pause propagation [hops from congestion point] default 1 (illustrative) (Design objective to keep pause local.) Lossless traffic classes [count] default 1 or 2 (illustrative) (Fewer lossless classes reduce deadlock and headroom exposure.) | Congestion-control design document; Configuration reconciliation of ECN, PFC, headroom, watchdog and NIC rate-control settings; Deadlock/cyclic-dependency analysis; Incast and pause-storm test plans and results; Operational ECN/PFC/CNP counter telemetry | DOCUMENT_REVIEW; RECONCILIATION; ANALYSIS; TEST; REPERFORMANCE | 1) Review the congestion-control design and its rationale. 2) Reconcile congestion parameters across all fabric devices and NICs, recording drift. 3) Review deadlock analysis including failure-routing cases. 4) Review or witness incast tests and evaluate drops, pause propagation and job-level effect. 5) Review or witness a controlled pause-storm test and confirm watchdog action. 6) Sample operational counters for unexplained pause or drop events. | PREVENTIVE | EFFECTIVENESS | AL5 | DESIGN; COMMISSION; OPERATE; CHANGE | NORMAL; DEGRADED; MAINTENANCE | Applies to every fabric carrying RDMA (RoCEv2, InfiniBand) or other congestion-sensitive collective traffic. For InfiniBand, PFC criteria are replaced by credit-based flow control and adaptive-routing configuration review. | CG-08 | CG-09 | PFC storm from a malfunctioning NIC halting a pod; PFC deadlock from cyclic buffer dependency after a routing change; Insufficient headroom causing lossless drops; ECN thresholds too high leading to buffer exhaustion; Parameter drift between switches | Safeguard; InfrastructureSystem; FailureMode; TestRecord | Incast and pause-storm tests can stall production fabrics and shall only be run with explicit written authorisation from the service owner and network change board, in a scheduled window, with the workload drained or isolated, the watchdog verified enabled beforehand and an abort criterion defined. | If NIC-side rate-control parameters cannot be extracted, record U2 and treat the end-to-end congestion design as unverified. | IEEE 802.1Qbb (Priority-based Flow Control); IEEE 802.1Qaz (Enhanced Transmission Selection and DCBX); IETF RFC 3168 (Explicit Congestion Notification); InfiniBand Trade Association, RoCEv2 annex to the InfiniBand Architecture Specification; InfiniBand Trade Association, InfiniBand Architecture Specification (Volumes 1 and 2); Ultra Ethernet Consortium specification (UEC 1.0) | MCF-NET-006; MCF-NET-008; MCF-NET-004; MCF-NET-022; MCF-CMP-012 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-NET-008 | NET | AI Network and Interconnect Architecture | NET-02 | Performance and congestion control | Collective Communication Performance | Ensure collective operations (all-reduce, all-gather, reduce-scatter, all-to-all) achieve the bus bandwidth and step-time required by declared training and inference outcomes at full and degraded scale. | The fabric operations lead shall run a defined collective benchmark suite (for example NCCL- or RCCL-class tests and a representative workload proxy) at commissioning, after every material fabric, NIC or library change and at a defined periodic interval, covering message sizes and scales used by declared workloads, and shall compare achieved bus bandwidth and latency to acceptance targets. The capability owner shall set the acceptance targets from the performance Service Outcome and shall accept or reject results for degraded scale (for example one plane or one spine unavailable). | 1) A collective benchmark suite is defined with operations, message sizes, scales, library versions and environment variables recorded. 2) Acceptance targets per operation and scale are approved by the capability owner and traceable to the performance Service Outcome. 3) Current results at full scale meet targets, or shortfalls are recorded as Findings. 4) Results at defined degraded scale meet the degraded targets. 5) Benchmarks were rerun after every material change and at the periodic interval. 6) Per-node or per-rail outliers are identified and remediated. | Collective acceptance target [% of design bus bandwidth] default 90 (illustrative) (Capability-profile parameter derived from performance outcome.) Benchmark periodic interval [days] default 30 (illustrative) (Detects slow drift.) | Benchmark suite definition; Approved acceptance targets; Benchmark results with raw outputs and environment captures; Degraded-scale results; Outlier remediation records | TEST; REPERFORMANCE; ANALYSIS; DOCUMENT_REVIEW | 1) Review the benchmark suite definition against declared workload communication patterns. 2) Confirm targets are approved and traceable to Service Outcomes. 3) Parse raw outputs and verify reported bus bandwidth and latency. 4) Witness or reperform a benchmark run at representative scale. 5) Review degraded-scale results and acceptance. 6) Trace outliers to remediation. | DETECTIVE | EFFECTIVENESS | AL5 | COMMISSION; OPERATE; CHANGE | NORMAL; DEGRADED; TRANSITION | Applies to multi-node training and distributed inference Capability Instances. Not applicable where outcomes do not depend on inter-node collectives. | CG-08 |  | Collective bandwidth regression after library upgrade; Single bad node or rail throttling a whole job; Degraded-scale performance below outcome tolerance; Environment misconfiguration bypassing RDMA | TestRecord; CapacityAssertion; ServiceOutcome; InfrastructureSystem | Full-scale benchmarks consume the cluster and shall be scheduled with the capability owner; degraded-scale tests that disable a plane or spine are disruptive and require change-board authorisation. | Benchmarks run with library versions or environment settings different from production are not representative (U5) and shall not support a CONFORMING result. | InfiniBand Trade Association, InfiniBand Architecture Specification (Volumes 1 and 2); InfiniBand Trade Association, RoCEv2 annex to the InfiniBand Architecture Specification; Ultra Ethernet Consortium specification (UEC 1.0); AIDCF-013 (AI Data Centre Assurance Reference Architecture) | MCF-NET-003; MCF-NET-005; MCF-NET-007; MCF-CMP-020; MCF-CAP-006 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-NET-009 | NET | AI Network and Interconnect Architecture | NET-03 | Storage and service networks | Storage Fabric | Ensure the storage network (dedicated or converged) delivers the throughput, latency and isolation needed for dataset reads and checkpoint write bursts without interfering with collective traffic. | The network architecture owner shall define the storage network design: whether storage traffic uses a dedicated fabric, a dedicated plane or a separate traffic class on the compute fabric; the path from compute nodes to storage servers and metadata services; capacity per storage server; and the traffic-class and congestion policy that prevents checkpoint bursts from degrading collective traffic. The storage platform owner and fabric operations lead shall jointly test a synchronised checkpoint write and a dataset-read burst at declared scale and confirm achieved throughput and the effect on concurrent collective performance meet targets. | 1) Storage network design states topology, traffic-class policy, capacity per storage target and metadata service paths. 2) Configured traffic-class and QoS settings match the design. 3) A synchronised checkpoint-write test at declared scale achieves the throughput needed to meet the checkpoint-time target. 4) Concurrent collective performance during the checkpoint burst stays within the tolerated degradation. 5) Storage metadata services are reachable over redundant paths with no single switch dependency. | Checkpoint write window [s] default Derived from checkpoint size and goodput target (illustrative 120) (Capability-profile parameter; see RES-016.) Tolerated collective degradation during checkpoint [% bus bandwidth reduction] default 10 (illustrative) (Capability-profile parameter.) | Storage network design and traffic-class policy; QoS/traffic-class configuration extracts; Checkpoint-burst and dataset-read test results; Concurrent collective measurement during burst; Metadata path redundancy analysis | DOCUMENT_REVIEW; RECONCILIATION; TEST; ANALYSIS | 1) Review storage network design and confirm path to metadata and data services. 2) Reconcile traffic-class configuration on switches and NICs. 3) Review or witness checkpoint-burst and dataset-read tests. 4) Measure or review collective performance during the burst. 5) Confirm metadata path redundancy. | PREVENTIVE | EFFECTIVENESS | AL5 | DESIGN; COMMISSION; OPERATE; CHANGE | NORMAL; DEGRADED | Applies to any Capability Instance that reads training data or writes checkpoints over a network. Local-NVMe-only checkpointing still requires assessment of the path used to drain checkpoints to durable storage. | CG-08 | CG-10 | Checkpoint burst saturating shared uplinks (X06); Storage and collective traffic sharing a lossless class causing head-of-line blocking; Metadata service reachable via a single switch; Dataset-read starvation reducing accelerator utilisation | InfrastructureSystem; Interface; CapacityAssertion; TestRecord | Checkpoint-burst tests load shared storage and may affect other tenants; schedule with the storage platform owner and notify affected service owners. Do not run destructive storage tests under this control. | If checkpoint throughput is only known from storage vendor specifications, record U8 and limit the claim to DESIGN. | InfiniBand Trade Association, RoCEv2 annex to the InfiniBand Architecture Specification; IEEE 802.1Qaz (Enhanced Transmission Selection and DCBX); AIDCF-013 (AI Data Centre Assurance Reference Architecture) | MCF-STO-005; MCF-STO-008; MCF-STO-017; MCF-NET-003; MCF-RES-016 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-NET-010 | NET | AI Network and Interconnect Architecture | NET-03 | Storage and service networks | Frontend Network | Ensure the front-end network that carries user, API, inference request, orchestration and data-ingest traffic is built to an approved, redundant design and reconciles to it. | The network architecture owner shall maintain an approved front-end network design covering node attachment (dual-homed or single-homed), routing protocol and ECMP design, uplinks to core and edge, load-balancer and gateway placement, and capacity for inference request and data-ingest peaks. The network operations manager shall reconcile as-built configuration and attachment to the design at commissioning and after material changes, and shall confirm that loss of a single front-end switch or uplink does not disconnect inference endpoints or orchestration control traffic beyond tolerance. | 1) Approved front-end design exists with attachment, routing, capacity and redundancy stated. 2) As-built attachment and routing configuration reconcile to design. 3) Inference and orchestration endpoints have redundant attachment or an accepted single-homed rationale. 4) Capacity for declared inference request and ingest peaks is demonstrated by telemetry or test. 5) Single-switch or uplink failure has been tested or observed with effect within tolerance. | Front-end peak utilisation ceiling [% of uplink capacity] default 70 (illustrative) (Capability-profile parameter for headroom.) | Front-end network design; Configuration and attachment reconciliation; Utilisation telemetry at peak; Failover test or incident record | DOCUMENT_REVIEW; RECONCILIATION; ANALYSIS; SAMPLING | 1) Review design and capacity basis. 2) Reconcile attachment and routing configuration. 3) Check redundancy of inference and orchestration endpoints. 4) Review peak utilisation telemetry. 5) Review failover evidence. | PREVENTIVE | IMPLEMENTATION | AL3 | DESIGN; BUILD; COMMISSION; CHANGE | NORMAL; DEGRADED; MAINTENANCE | Applies to front-end networks serving in-scope inference, orchestration and data-ingest. Where the front end is provided by a cloud or colocation provider, the provider boundary (DEP-018) governs evidence rights. |  | CG-08 | Single-homed inference gateways; ECMP imbalance saturating one uplink; Orchestration traffic lost on front-end switch failure | InfrastructureSystem; Interface; ArchitectureSnapshot | Front-end failover tests affect customer-facing inference and require service owner authorisation and customer-impact assessment. | Where provider-operated front-end segments cannot be inspected, record U2 and bound claims to the owned segment. | IETF RFC 7938 (Use of BGP for routing in large-scale data centres); IEEE 802.1Q (Bridges and bridged networks); ANSI/TIA-942 (Telecommunications infrastructure standard for data centres) | MCF-NET-011; MCF-NET-012; MCF-DEP-018; MCF-CAP-005 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-NET-011 | NET | AI Network and Interconnect Architecture | NET-03 | Storage and service networks | Service Gateways | Ensure gateways, load balancers, NAT, firewalls and edge routers on the service path operate within capacity, with health monitoring and redundancy that sustain inference and data-ingest outcomes. | The network operations manager shall operate each service gateway cluster (load balancers, inference API gateways, NAT, edge routers and in-path firewalls) as a redundant pair or cluster with health checks, session-state handling and capacity monitoring, and shall define capacity thresholds for connections, throughput and TLS handshakes. The network operations manager shall review gateway capacity and failover events monthly and shall demonstrate that gateway failover occurred, or was tested, within tolerance in the assessment period. | 1) Every in-path gateway is redundant or the single instance is an accepted limitation. 2) Capacity thresholds for connections, throughput and handshake rate are defined and monitored. 3) Health checks and failover triggers are configured and their behaviour is understood (state synchronisation, session loss). 4) Monthly capacity and event reviews occurred in the period with actions tracked. 5) Failover occurred or was tested in the period with measured disruption within tolerance. | Gateway capacity alert threshold [% of rated connections/throughput] default 70 (illustrative) (Capability-profile parameter.) Tolerated failover disruption [s] default Set by inference availability outcome (illustrative 5) (Derived from Service Outcome.) | Gateway inventory with redundancy mode; Capacity telemetry and thresholds; Monthly review records; Failover event or test records | ANALYSIS; SAMPLING; DOCUMENT_REVIEW; INQUIRY | 1) Inventory in-path gateways and redundancy modes. 2) Review thresholds and sample telemetry for breaches. 3) Review monthly reviews and actions. 4) Examine failover events or tests and measured disruption. | DETECTIVE | OPERATION | AL4 | OPERATE; CHANGE | NORMAL; DEGRADED; MAINTENANCE | Applies to gateways on the path of in-scope inference, API and data-ingest outcomes. Security policy content of firewalls is assessed under SEC-011. |  | CG-08 | Gateway connection-table exhaustion; Failover dropping all sessions; TLS handshake capacity exhausted at peak; Asymmetric routing through stateful gateways | AssetInstance; CapacityAssertion; Event | Gateway failover tests disrupt sessions and require service owner authorisation and a customer communication plan where external customers are affected. | If session-state behaviour during failover is undocumented and untested, record U8 and limit availability claims. | IETF RFC 7938 (Use of BGP for routing in large-scale data centres); AIDCF-013 (AI Data Centre Assurance Reference Architecture) | MCF-NET-010; MCF-SEC-011; MCF-OPS-022 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-NET-012 | NET | AI Network and Interconnect Architecture | NET-03 | Storage and service networks | Traffic Isolation | Ensure tenant, workload and traffic-class isolation on shared fabrics prevents one tenant or job from degrading, observing or reaching another beyond tolerance. | The network architecture owner shall define the isolation model for shared fabrics: InfiniBand partition keys, VRFs, VXLAN/EVPN segments, VLANs, RDMA queue-pair and memory-region protections, traffic-class guarantees and rate limits. The fabric operations lead shall verify by test that endpoints in one isolation domain cannot reach endpoints in another, and that a saturating or misbehaving tenant cannot reduce another tenant's guaranteed bandwidth or trigger fabric-wide pause beyond the defined tolerance. | 1) The isolation model states mechanisms, domains, and which traffic classes are shared. 2) Configuration of partitions, VRFs or segments reconciles to tenant assignments. 3) Reachability tests confirm no unintended cross-domain connectivity at layer 2, layer 3 and RDMA. 4) Performance-isolation tests show a saturating tenant does not reduce another tenant's guaranteed share beyond tolerance. 5) Tenant onboarding and offboarding updates isolation configuration and is verified. | Guaranteed bandwidth share per tenant class [% of link] default Contract-specific (illustrative 25) (Set by tenant commitments (GOV-021).) Tolerated cross-tenant degradation [% throughput reduction] default 5 (illustrative) (Capability-profile parameter.) | Isolation model; Partition/VRF/segment configuration extracts with tenant mapping; Reachability test results; Performance-isolation test results; Onboarding/offboarding change records | DOCUMENT_REVIEW; RECONCILIATION; TEST; SAMPLING | 1) Review the isolation model and tenant assignments. 2) Reconcile partition/VRF/segment configuration with tenant records. 3) Review or witness reachability tests across domains. 4) Review or witness performance-isolation tests. 5) Sample onboarding/offboarding changes for verification. | PREVENTIVE | EFFECTIVENESS | AL5 | DESIGN; COMMISSION; OPERATE; CHANGE | NORMAL; DEGRADED | Applies to fabrics shared by more than one tenant, customer or trust domain. For single-tenant fabrics, only traffic-class isolation between storage, collective and management traffic applies. |  | CG-09; CG-08; CG-15 | Partition key misassignment exposing tenant RDMA memory; Noisy-neighbour congestion degrading other tenants; Stale segment after offboarding; Shared lossless class propagating pause across tenants | FaultDomain; Safeguard; Interface; TestRecord | Cross-tenant reachability tests shall use designated test endpoints and shall not access tenant data. Saturation tests require tenant notification and change approval. | If RDMA-layer isolation has not been tested separately from IP-layer isolation, record U5 and do not infer RDMA isolation from IP results. | InfiniBand Trade Association, InfiniBand Architecture Specification (Volumes 1 and 2); IEEE 802.1Q (Bridges and bridged networks); IEEE 802.1Qaz (Enhanced Transmission Selection and DCBX); AIDCF-013 (AI Data Centre Assurance Reference Architecture) | MCF-DEP-019; MCF-SEC-009; MCF-CMP-007; MCF-NET-007; MCF-RES-006 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-NET-013 | NET | AI Network and Interconnect Architecture | NET-04 | Management and out-of-band networks | Management Separation | Ensure management traffic for switches, servers, BMCs, PDUs, storage and facility gateways traverses a management network separated from data and tenant networks, so data-plane failure or compromise does not remove management reach. | The network architecture owner shall define the management network architecture, separating in-band management, BMC/out-of-band management and facility OT management, and shall prohibit management interfaces from being reachable from tenant or data networks except through defined conduits. The network operations manager shall reconcile the management network attachment of every switch management port, BMC, PDU, console server and storage controller to the design, and shall record any device whose management is only reachable in-band as a Finding. | 1) Management network architecture defines in-band, out-of-band and OT management segments and permitted conduits. 2) Every in-scope managed device has its management interface attached to the designated segment. 3) No management interface is reachable from tenant or data networks except via defined conduits (verified by scan or ACL review). 4) Devices relying solely on in-band management are listed and dispositioned. 5) Management network capacity and addressing are independent of the data fabric. |  | Management network architecture; Device-to-management-segment inventory; Reachability scan or ACL analysis from tenant/data networks; List of in-band-only devices | DOCUMENT_REVIEW; RECONCILIATION; TEST; SAMPLING | 1) Review the management architecture and conduits. 2) Reconcile device management attachment against inventory. 3) Review reachability scans or ACL analysis from tenant/data segments. 4) Disposition in-band-only devices. | PREVENTIVE | IMPLEMENTATION | AL3 | DESIGN; BUILD; COMMISSION; CHANGE | NORMAL; MAINTENANCE; DEGRADED | Applies to all managed network, compute, storage, power-distribution and facility gateway devices supporting in-scope outcomes. Security policy of the conduits is assessed under SEC-010. |  | CG-15; CG-08 | BMCs on tenant VLAN; Switch management only in-band, lost when the fabric fails; Facility gateways bridged to IT management | InfrastructureSystem; Interface; FaultDomain | Reachability scans shall be non-intrusive, rate-limited and authorised by the security owner; scanning OT segments requires OT owner approval (see SEC-009). | Devices whose management attachment cannot be determined are treated as reachable from data networks (U1) until evidenced. | ISA/IEC 62443-3-3 (System security requirements and security levels); NIST SP 800-82 Rev. 3 (Guide to operational technology security); ANSI/TIA-942 (Telecommunications infrastructure standard for data centres) | MCF-SEC-010; MCF-NET-014; MCF-NET-015; MCF-SEC-009 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-NET-014 | NET | AI Network and Interconnect Architecture | NET-04 | Management and out-of-band networks | Console Access | Ensure serial console and remote KVM access to network, compute and storage devices exists, is authenticated and is reachable independently of the data plane. | The network operations manager shall provide serial console access to every switch, router, firewall and storage controller, and BMC/KVM access to every server, through console servers or OOB infrastructure that is independent of the data fabric, and shall require individual authentication, session logging and role-based authorisation for console sessions. The network operations manager shall verify console reachability for every device at a defined interval and after rack moves. | 1) Every in-scope device has a mapped console or BMC path recorded in inventory. 2) Console servers authenticate individual users against a central identity source with local fallback governed by NET-016. 3) Console sessions are logged with user, device, time and, where supported, keystroke capture. 4) Periodic console reachability checks cover all devices and failures are remediated. 5) Console port mappings are verified after rack moves or re-cabling. | Console reachability check interval [days] default 30 (illustrative) (Capability-profile parameter.) | Console mapping inventory; Console server authentication configuration; Session log samples; Reachability check reports | DOCUMENT_REVIEW; INSPECTION; SAMPLING; TEST | 1) Review console mapping completeness against device inventory. 2) Review console authentication and logging configuration. 3) Sample devices and confirm live console reach using read-only access. 4) Review reachability check history and remediation. | CORRECTIVE | IMPLEMENTATION | AL3 | BUILD; COMMISSION; OPERATE; CHANGE | NORMAL; MAINTENANCE; FAILED; RECOVERY | Applies to all network, storage and compute devices that would need recovery action during fabric or control-plane failure. |  | CG-10; CG-15 | Unmapped console after rack move; Shared console credentials; Console servers dependent on the failed fabric | Interface; AssetInstance; Safeguard | Live console checks shall use read-only roles and shall not send break signals or keystrokes that could interrupt device boot or operation. | If console mapping completeness cannot be verified, treat unmapped devices as lacking recovery access (U1) in recovery-sequence analysis. | ANSI/TIA-942 (Telecommunications infrastructure standard for data centres); ISA/IEC 62443-3-3 (System security requirements and security levels) | MCF-NET-013; MCF-NET-015; MCF-NET-016; MCF-SEC-003 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-NET-015 | NET | AI Network and Interconnect Architecture | NET-04 | Management and out-of-band networks | OOB Resilience | Ensure the out-of-band management network remains available when the data fabric, site core, primary identity services or primary WAN fail, so restoration can proceed. | The network architecture owner shall design the OOB network with its own switching, power supply from a protected source with defined autonomy, independent upstream connectivity (for example a separate carrier or cellular path), and locally available authentication and name resolution, and shall document every dependency the OOB network has on the systems it is used to recover. The network operations manager shall test at a defined interval that OOB access to critical devices is achievable with the production fabric, primary WAN and primary identity provider unavailable. | 1) OOB design states switching, power source and autonomy, upstream paths and authentication fallback. 2) Dependency analysis shows the OOB network does not depend on the production fabric, production DNS/identity or the primary WAN, or each dependency is mitigated. 3) OOB equipment power is from a protected supply with autonomy meeting the recovery-sequence requirement. 4) A test in the period demonstrated OOB reach to critical devices with production fabric, primary WAN and primary identity unavailable (or simulated unavailable). 5) OOB health is monitored and failures alarm to an independent channel. | OOB power autonomy [h] default Equal to or greater than black-start sequence duration (illustrative 4) (Derived from RES-014 restoration sequence.) OOB test interval [months] default 6 (illustrative) (Capability-profile parameter.) | OOB design and dependency analysis; Power path and autonomy evidence for OOB equipment; OOB isolation test record; OOB health monitoring configuration and alarms | DOCUMENT_REVIEW; ANALYSIS; TEST; SCENARIO_EXERCISE; INSPECTION | 1) Review the OOB design and list its dependencies. 2) Trace OOB power to its source and verify autonomy. 3) Confirm local authentication and name resolution fallback exist and are tested. 4) Review or witness the isolation test. 5) Review OOB health monitoring and alarm routing. | RECOVERY | RESILIENCE | AL5 | DESIGN; COMMISSION; OPERATE; CHANGE | NORMAL; FAILED; EMERGENCY; RECOVERY | Applies to every site supporting in-scope outcomes. Where OOB is provided by a colocation operator, responsibilities shall be explicit under DEP-018. | CG-10 | CG-15; CG-03 | OOB authentication dependent on the identity provider hosted on the failed cluster; OOB switches powered from non-protected supply; OOB uplink sharing the primary carrier route; Circular dependency on production DNS | InfrastructureSystem; Dependency; Safeguard; TestRecord | Isolation tests shall not disconnect production identity or WAN; they shall simulate isolation by forcing OOB clients to fallback paths, under an approved change with a rollback plan. | Any OOB dependency on a production service that has not been analysed is recorded as U10 at US4 against CG-10. | ANSI/TIA-942 (Telecommunications infrastructure standard for data centres); EN 50600 series / ISO/IEC 22237 series (Data centre facilities and infrastructures); NIST SP 800-82 Rev. 3 (Guide to operational technology security) | MCF-NET-013; MCF-NET-016; MCF-RES-013; MCF-RES-014; MCF-SEC-004 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-NET-016 | NET | AI Network and Interconnect Architecture | NET-04 | Management and out-of-band networks | Break-Glass Access | Ensure emergency access to network devices and controllers works when central authentication is unavailable, and that its use is controlled, logged and reviewed. | The network operations manager shall provision break-glass local credentials or offline authentication for network devices, fabric controllers, subnet managers and console servers, stored in a sealed or vaulted mechanism with dual control, and shall test break-glass login on a sample of device classes at a defined interval. The infrastructure security owner shall review every break-glass use within a defined time, rotate the credentials afterwards, and confirm that break-glass accounts are disabled for routine use. | 1) Break-glass credentials exist for every device class needed in recovery and are stored under dual control. 2) Break-glass login works on a sampled device of each class when central authentication is unreachable. 3) Every break-glass use in the period was logged, reviewed within the defined time and followed by credential rotation. 4) Break-glass accounts are not used for routine operations (log analysis). 5) Retrieval of break-glass credentials is possible during loss of the primary vault (offline copy governed by SEC-004). | Break-glass post-use review time [h] default 24 (illustrative) (Capability-profile parameter.) Break-glass test interval [months] default 6 (illustrative) (Capability-profile parameter.) | Break-glass account inventory per device class; Vault and dual-control configuration; Break-glass test records; Use logs, reviews and rotation records | DOCUMENT_REVIEW; TEST; SAMPLING; ANALYSIS | 1) Review break-glass inventory against recovery device classes. 2) Inspect dual-control and offline retrieval arrangements. 3) Review or witness a break-glass login test with central authentication made unreachable for the test device. 4) Sample use events and confirm review and rotation. 5) Analyse logs for routine use of break-glass accounts. | RECOVERY | EFFECTIVENESS | AL5 | COMMISSION; OPERATE | EMERGENCY; FAILED; RECOVERY | Applies to network devices, fabric controllers, subnet managers and console servers supporting in-scope outcomes. Governance of break-glass across all infrastructure is SEC-004. |  | CG-15; CG-10 | Break-glass password unknown or expired at time of need; Vault unreachable during outage; Break-glass account used routinely; No rotation after use | Safeguard; TestRecord; Event | Break-glass tests shall be performed on a non-critical device or in a maintenance window, without disabling central authentication for other devices; rotation shall follow every test. | If no break-glass test has been performed for a device class, record U1 and treat emergency access for that class as unavailable in recovery analysis. | ISA/IEC 62443-3-3 (System security requirements and security levels); NIST SP 800-82 Rev. 3 (Guide to operational technology security) | MCF-SEC-004; MCF-NET-014; MCF-NET-015; MCF-SEC-003 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-NET-017 | NET | AI Network and Interconnect Architecture | NET-05 | Physical connectivity and optics | Cabling Standards | Ensure structured cabling and high-density fibre plant are designed to recognised standards for pathways, bend radius, polarity, labelling, density and serviceability so that the physical layer does not become a latent fabric failure source. | The cabling plant owner shall maintain a cabling design standard for the site covering pathway and containment fill limits, segregation from power, minimum bend radius by cable type, MPO/MTP polarity method, connector cleanliness acceptance, labelling scheme and test acceptance (insertion loss and, where applicable, reflectance), aligned with recognised data-centre cabling standards. The cabling plant owner shall approve deviations, and installers shall be bound to the standard contractually. | 1) A site cabling standard exists covering pathways, fill, segregation, bend radius, polarity, cleanliness, labelling and test acceptance. 2) The standard references recognised cabling standards families and is approved by the cabling plant owner. 3) High-density back-end trunk designs (fibre counts, breakout scheme, patch-panel density) are specified. 4) Installer contracts reference the standard and its acceptance tests. 5) Deviations are approved and recorded. | Maximum containment fill [% cross-section] default Per adopted standard (illustrative 50) (From adopted cabling standard; site-specific.) Fibre link loss acceptance margin [dB below transceiver budget] default Set from optics budget (illustrative 1.0) (Ensures operating margin; see NET-018.) | Site cabling standard; Trunk and breakout design for back-end fabrics; Installer contract clauses; Deviation register | DOCUMENT_REVIEW; INSPECTION; INQUIRY | 1) Review the cabling standard against adopted standards families. 2) Check coverage of high-density back-end trunk design. 3) Inspect a sample of installed pathways for conformance. 4) Review installer contracts and deviations. | DIRECTIVE | DESIGN | AL2 | PLAN; DESIGN; BUILD | NORMAL; MAINTENANCE | Applies to all owned or operated cabling plant supporting in-scope fabrics. Provider-owned cabling is governed by provider contracts. |  | CG-08 | Bend-radius violations causing marginal loss; Polarity errors on MPO trunks; Overfilled trays preventing safe moves; Dirty connectors | Control; AssetInstance; Interface | Physical inspection shall not disturb live cabling; opening trays or handling live fibre requires an approved method statement. | If no site standard exists, physical-layer claims rely only on test results (NET-018/NET-020) and confidence is capped at CONF-2. | ANSI/TIA-942 (Telecommunications infrastructure standard for data centres); ISO/IEC 11801 series (Generic cabling for customer premises, including data centres); ISO/IEC 14763 series (Implementation and operation of customer premises cabling, including optical fibre testing); ANSI/TIA-606 (Administration standard for telecommunications infrastructure); EN 50600 series / ISO/IEC 22237 series (Data centre facilities and infrastructures); IEC 61300-3-35 (Fibre optic connector endface visual and automated inspection) | MCF-NET-018; MCF-NET-019; MCF-NET-020; MCF-PHY-005 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-NET-018 | NET | AI Network and Interconnect Architecture | NET-05 | Physical connectivity and optics | Optics Compatibility | Ensure transceivers, active and passive cables and NIC/switch firmware are qualified combinations with adequate link budget, so optics do not become a common-mode source of link errors and flaps. | The network architecture owner shall maintain a qualified-optics matrix listing approved transceiver and cable part numbers, firmware versions, host switch/NIC models and NOS/firmware versions, reach and link-budget class. The fabric operations lead shall reconcile installed optics (from digital diagnostic and CMIS inventory) to the matrix, shall monitor optical diagnostics (Rx/Tx power, temperature, bias, pre-FEC error indicators), and shall quarantine unqualified or degrading optics. | 1) A qualified-optics matrix exists with part numbers, firmware, host combinations and link-budget class. 2) Installed optics inventory reconciles to the matrix; unqualified parts are listed and dispositioned. 3) Optical diagnostics are collected for all optics with thresholds for low Rx power and high temperature. 4) Measured link loss for a sample of links is within the transceiver budget with the defined margin. 5) Optics firmware is at qualified versions; mixed versions within a fabric are justified. 6) Failure and RMA data are analysed for batch or lot-level common modes. | Rx power warning margin [dB above receiver sensitivity] default 2 (illustrative) (Capability-profile parameter derived from vendor budget.) Optics failure-rate review trigger [failures per 1000 per month] default Site baseline-derived (illustrative) (Triggers lot-level analysis.) | Qualified-optics matrix; Installed optics inventory with serial, part and firmware; Optical diagnostics telemetry; Link loss test records; RMA and failure analysis | RECONCILIATION; ANALYSIS; SAMPLING; DOCUMENT_REVIEW | 1) Review the qualified-optics matrix for completeness. 2) Extract installed optics inventory and reconcile. 3) Review diagnostics thresholds and sample telemetry. 4) Sample link loss test records against budget. 5) Review RMA data for lot or firmware common modes. | PREVENTIVE | IMPLEMENTATION | AL3 | DESIGN; BUILD; COMMISSION; OPERATE; CHANGE | NORMAL; MAINTENANCE | Applies to all pluggable optics, AOCs and DACs in in-scope fabrics; for co-packaged or linear-drive optics, the matrix records host and module firmware combinations. |  | CG-08; CG-03 | Unqualified optic causing intermittent errors; Optic lot defect affecting thousands of links; Firmware mismatch between module and host; Insufficient link margin | AssetInstance; FailureMode; Resource | Reading diagnostics is non-intrusive; removing optics for inspection requires change approval and link drain. | Optics whose diagnostics cannot be read are treated as unqualified (U1) pending inspection. | OSFP MSA and QSFP-DD MSA module specifications; CMIS (Common Management Interface Specification); IEEE 802.3 (Ethernet, including optical PHY and FEC clauses); IEC 61300-3-35 (Fibre optic connector endface visual and automated inspection); ISO/IEC 14763 series (Implementation and operation of customer premises cabling, including optical fibre testing) | MCF-NET-006; MCF-NET-017; MCF-SUP-010; MCF-SUP-015 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-NET-019 | NET | AI Network and Interconnect Architecture | NET-05 | Physical connectivity and optics | Cross-Connect Control | Ensure physical moves, adds and changes to patching and cross-connects (including in meet-me rooms and carrier demarcations) are authorised, recorded and verified, so that maintenance does not sever redundant paths. | The network operations manager shall require an approved work order for every physical patch or cross-connect change, specifying both ends, labels, affected path groups and redundancy impact, and shall verify after each change that the link came up on the expected ports and that the cabling records were updated. The network operations manager shall prohibit simultaneous work on members of the same redundant path group unless explicitly approved. | 1) Every physical change in the sampled period has an approved work order identifying both ends and path-group impact. 2) Post-change verification (link state, neighbour, label) is recorded for each change. 3) Cabling records are updated within the defined time after change. 4) No simultaneous work on members of one redundant path group occurred without approval. 5) Carrier and colocation cross-connect changes are reconciled to provider orders. | Record update time after change [h] default 24 (illustrative) (Capability-profile parameter.) | Work-order records for physical changes; Post-change verification records; Cabling record audit trail; Provider cross-connect orders | SAMPLING; RECONCILIATION; DOCUMENT_REVIEW | 1) Extract link up/down events for the period from devices. 2) Match events to work orders and identify unmatched changes. 3) Check sampled work orders for path-group impact and post-change verification. 4) Check for concurrent work on redundant pairs. 5) Reconcile provider cross-connect orders. | PREVENTIVE | OPERATION | AL4 | OPERATE; CHANGE | NORMAL; MAINTENANCE | Applies to all owned patching and to provider cross-connects for in-scope paths. |  | CG-14; CG-08 | Wrong cable pulled during maintenance severing the surviving path; Unrecorded patch causing rail mis-mapping; Simultaneous work on both diverse trunks | Event; Action; Interface | Reconciliation is records-based and non-intrusive. | Unmatched link events are recorded as Findings unless explained; if link-event logs are unavailable, record U2 and limit the claim. | ANSI/TIA-606 (Administration standard for telecommunications infrastructure); ANSI/TIA-942 (Telecommunications infrastructure standard for data centres) | MCF-NET-020; MCF-OPS-018; MCF-OPS-006; MCF-NET-002 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-NET-020 | NET | AI Network and Interconnect Architecture | NET-05 | Physical connectivity and optics | Path Documentation | Ensure end-to-end physical and logical path records (port to patch panel to trunk to panel to port, and circuit to route) are complete and accurate enough to support fault isolation, diversity analysis and recovery. | The network operations manager shall maintain a path-documentation system (DCIM or cable-management database) recording every in-scope link from endpoint port through patch panels, trunks and cross-connects to the far-end port, with labels matching the physical plant and links to circuit IDs for external paths. The network operations manager shall audit a sample of paths physically and electronically at a defined interval and shall correct discrepancies, with an accuracy target set as a capability-profile parameter. | 1) Path records exist for all in-scope links including intermediate panels and trunks. 2) Labels in the field match records for the audited sample. 3) Electronic reconciliation (LLDP or subnet-manager neighbours) matches end-to-end records. 4) Audit accuracy meets the target, and discrepancies are corrected. 5) External circuit records link to provider circuit IDs and routes (NET-002). | Path record accuracy target [% of audited links correct end-to-end] default 99 (illustrative) (Capability-profile parameter.) Audit sample size [links per audit] default Statistically justified (illustrative 200) (Sampling per AIDCF-009.) | Path-documentation system extract; Physical audit records; Electronic reconciliation report; Discrepancy correction log | INSPECTION; RECONCILIATION; SAMPLING | 1) Extract path records for in-scope fabrics. 2) Select a sample and physically verify labels and routes. 3) Reconcile electronically against neighbour data. 4) Compute accuracy and review corrections. | DETECTIVE | IMPLEMENTATION | AL3 | BUILD; COMMISSION; OPERATE; CHANGE | NORMAL; MAINTENANCE; RECOVERY | Applies to all in-scope links and external circuits. |  | CG-02; CG-03; CG-10 | Records misidentifying the surviving path during an incident; Untraceable trunks after expansion; Circuit ID not linked to route | ArchitectureSnapshot; Interface; EvidenceObject | Physical audits shall not disturb live cables beyond visual label inspection. | Where records cannot be reconciled for a fabric segment, the segment's paths are treated as undocumented (U1) in diversity and blast-radius analysis. | ANSI/TIA-606 (Administration standard for telecommunications infrastructure); ANSI/TIA-942 (Telecommunications infrastructure standard for data centres); ISO/IEC 14763 series (Implementation and operation of customer premises cabling, including optical fibre testing) | MCF-NET-001; MCF-NET-002; MCF-NET-019; MCF-DEP-007 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-NET-021 | NET | AI Network and Interconnect Architecture | NET-06 | Network control and observability | Controller Resilience | Ensure fabric control functions (InfiniBand subnet managers, SDN or EVPN controllers, fabric management platforms, route reflectors) survive single failures and that their loss does not disrupt forwarding beyond tolerance. | The network architecture owner shall deploy fabric control functions with redundancy (master/standby subnet managers, clustered controllers, redundant route reflectors) placed in separate power and rack fault domains, and shall document the data-plane behaviour when the control function is lost (forwarding continues with stale state, or fails). The fabric operations lead shall test controller and subnet-manager failover at a defined interval and after upgrades and shall confirm forwarding continuity and failover time within tolerance. | 1) Each fabric control function has redundancy and placement in separate power/rack domains. 2) Data-plane behaviour on control-plane loss is documented. 3) Failover tests in the period show forwarding continuity and failover time within tolerance. 4) Controller state backups exist and restore has been tested. 5) Controller health is monitored and alarms on loss of redundancy. | Controller failover time tolerance [s] default Below job collective timeout margin (illustrative 60) (Capability-profile parameter.) Controller failover test interval [months] default 12 (illustrative) (Capability-profile parameter.) | Controller architecture and placement; Behaviour-on-loss documentation; Failover test records; Backup and restore test records; Health monitoring configuration | DOCUMENT_REVIEW; TEST; ANALYSIS; INSPECTION | 1) Review controller architecture and placement against power and rack domains. 2) Review documented behaviour on control-plane loss. 3) Review or witness failover test. 4) Review backup/restore test. 5) Verify health monitoring. | PREVENTIVE | EFFECTIVENESS | AL5 | DESIGN; COMMISSION; OPERATE; CHANGE | NORMAL; DEGRADED; FAILED; RECOVERY | Applies to fabrics whose forwarding or configuration depends on a control function. Security of controllers is SEC-007. |  | CG-08; CG-09; CG-10 | Subnet-manager split-brain; Standby controller unable to take over at scale; Controllers co-located on one PDU; Controller loss causing data-plane flush | InfrastructureSystem; FaultDomain; TestRecord; Safeguard | Controller failover tests risk fabric-wide disruption and require change-board authorisation, a rollback plan and workload owner consent. | If data-plane behaviour on controller loss is undocumented and untested, record U8 at US4 against CG-08. | InfiniBand Trade Association, InfiniBand Architecture Specification (Volumes 1 and 2); IETF RFC 7938 (Use of BGP for routing in large-scale data centres); OpenConfig gNMI specification and OpenConfig data models | MCF-NET-004; MCF-SEC-007; MCF-RES-015; MCF-NET-022 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-NET-022 | NET | AI Network and Interconnect Architecture | NET-06 | Network control and observability | Configuration Management | Ensure network operating system, firmware and configuration across switches, NICs, optics and controllers are held to an approved baseline, changed only through staged and verified rollout, and restorable. | The fabric operations lead shall maintain a version-controlled source of truth for intended network configuration and an approved baseline of NOS, switch firmware, NIC firmware and driver, optics firmware and controller versions; shall detect configuration and version drift at a defined interval; and shall roll out changes in stages (canary, partial, full) with automated pre- and post-change checks and defined rollback. The network operations manager shall ensure that no single change can be applied simultaneously to both members of a redundant pair or to all planes of a fabric. | 1) A version-controlled intended configuration and an approved version baseline exist for each device class. 2) Drift detection runs at the defined interval and drift is remediated or approved. 3) Changes in the period followed staged rollout with pre- and post-checks and recorded rollback plans. 4) No change was applied simultaneously to both members of a redundant pair or all planes without approval. 5) Configuration backups exist for all devices and a restore from backup has been tested. 6) Emergency changes were retrospectively reviewed. | Drift detection interval [h] default 24 (illustrative) (Capability-profile parameter.) Canary stage size [% of devices] default ≤5 (illustrative) (Limits firmware common-mode exposure (X08).) | Source of truth repository and version baseline; Drift reports for the period; Change records with stage plans, checks and rollback; Configuration backup inventory and restore test | REPERFORMANCE; SAMPLING; DOCUMENT_REVIEW; RECONCILIATION | 1) Review the source of truth and version baseline. 2) Reperform drift detection on a sample of devices. 3) Sample changes and verify staged rollout, checks and rollback plans. 4) Check for simultaneous change to redundant pairs or all planes. 5) Review backup coverage and the restore test. 6) Review emergency change retrospectives. | PREVENTIVE | OPERATION | AL4 | OPERATE; CHANGE; COMMISSION | NORMAL; MAINTENANCE; TRANSITION; RECOVERY | Applies to all network devices, NICs, optics and fabric controllers in scope. Site-wide change governance is OPS-018. | CG-14 | CG-08; CG-10 | Firmware rollout common-mode failure across all planes (X08); Configuration drift breaking congestion control; No backup for recovery; Recovery restoring corrupt configuration (X15) | ArchitectureSnapshot; Action; ReassessmentTrigger; AssetInstance | Drift comparison is read-only. Restore tests shall be on a spare or isolated device unless a maintenance window is authorised. | If NIC or optics firmware versions are not in the baseline, record U5 and treat firmware common-mode exposure as unassessed. | OpenConfig gNMI specification and OpenConfig data models; IETF RFC 7938 (Use of BGP for routing in large-scale data centres); AIDCF-004 (Threat, Hazard and Failure Model) | MCF-OPS-017; MCF-OPS-018; MCF-CMP-013; MCF-RES-015; MCF-SEC-013 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-NET-023 | NET | AI Network and Interconnect Architecture | NET-06 | Network control and observability | Flow Telemetry | Ensure network telemetry (counters, streaming telemetry, flow sampling, congestion and buffer metrics) is collected with sufficient coverage, resolution and retention to detect degradation, attribute job slowdowns and support evidence for assurance. | The fabric operations lead shall collect streaming or polled telemetry from all in-scope switches and NICs covering interface counters, error counters, PFC pause and ECN mark counts, buffer occupancy, and flow sampling, at a resolution sufficient to observe collective-scale events, and shall retain it for the evidence retention period. The fabric operations lead shall monitor telemetry pipeline health and alert on collection gaps. | 1) Telemetry coverage includes all in-scope switches and NICs with gaps listed. 2) Counters include errors, PFC pause, ECN marks, buffer occupancy and drops per traffic class. 3) Collection resolution meets the defined parameter for congestion visibility. 4) Retention meets the evidence retention requirement. 5) Pipeline gaps are alerted and recorded, and gap rates are within tolerance. | Telemetry collection interval for congestion counters [s] default 10 (illustrative) (Capability-profile parameter; finer for diagnosis.) Telemetry retention [days] default Per evidence retention class (illustrative 395) (AIDCF-008 retention classes.) | Telemetry coverage report; Collector configuration; Pipeline health and gap reports; Retention configuration | ANALYSIS; SAMPLING; INSPECTION | 1) Compare telemetry source list to device inventory. 2) Query a sample of counters and check resolution. 3) Review gap reports and pipeline health. 4) Verify retention. | DETECTIVE | OPERATION | AL4 | COMMISSION; OPERATE | NORMAL; DEGRADED; MAINTENANCE; RECOVERY | Applies to all in-scope fabrics and networks. |  | CG-08 | Telemetry gaps hiding congestion events; Coarse sampling missing microbursts; Telemetry pipeline sharing failure domain with fabric | EvidenceObject; InfrastructureSystem; Safeguard | Non-intrusive; increasing collection frequency on production switches shall be assessed for control-plane CPU impact first. | Telemetry with unresolved gaps covering the assessed period is marked INCOMPLETE and cannot alone support OPERATION claims. | OpenConfig gNMI specification and OpenConfig data models; sFlow version 5 specification (sFlow.org); IETF RFC 7011 (IPFIX protocol specification) | MCF-NET-005; MCF-NET-006; MCF-SEC-017; MCF-CMP-017 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-NET-024 | NET | AI Network and Interconnect Architecture | NET-06 | Network control and observability | Time and Core Services | Ensure time (NTP/PTP), DNS, DHCP, IPAM and network AAA services that fabrics and clusters depend on are redundant, independent of the services they support, and resilient to failure and divergence. | The network architecture owner shall deploy time sources (with at least two independent references such as GNSS and a holdover oscillator or a remote time service), DNS, DHCP, IPAM and network AAA as redundant services placed in separate fault domains, and shall document every circular dependency between these services and the systems they support. The network operations manager shall monitor time offset, stratum and source agreement, and service availability, and shall test failure of a time source and of a DNS/AAA instance at a defined interval. | 1) Each core service has redundancy across separate power and rack fault domains. 2) Time architecture has independent references with holdover and monitors offset and source divergence (X13). 3) Circular dependencies (for example DNS needed to reach the time server, or AAA hosted on the cluster it authenticates) are documented and broken or mitigated. 4) Tests of time-source loss and DNS/AAA instance loss in the period showed service continuity. 5) Clients are configured with multiple servers and sensible failover. 6) Time offset across a sample of devices stays within tolerance. | Time offset tolerance [ms] default Workload- and log-correlation-dependent (illustrative 1 for NTP; sub-microsecond for PTP where required) (Capability-profile parameter.) Holdover duration [h] default Covers time-source repair time (illustrative 24) (Capability-profile parameter.) | Core service architecture and placement; Circular-dependency analysis; Time offset and source telemetry; Failure test records; Client configuration samples | DOCUMENT_REVIEW; ANALYSIS; TEST; SAMPLING | 1) Review architecture and placement for each core service. 2) Review circular-dependency analysis against RES-013. 3) Sample time offsets and source agreement. 4) Review failure tests. 5) Sample client configurations. | PREVENTIVE | EFFECTIVENESS | AL5 | DESIGN; COMMISSION; OPERATE | NORMAL; DEGRADED; FAILED; RECOVERY | Applies to time, DNS, DHCP, IPAM and network AAA services relied upon by in-scope infrastructure. |  | CG-08; CG-03; CG-10 | Time-source divergence corrupting log correlation and certificate validity (X13); AAA hosted on the failed cluster; DNS loss blocking cluster bring-up; GNSS spoofing or loss without holdover | InfrastructureSystem; Dependency; FaultDomain; TestRecord | Time-source failure tests shall be performed by withdrawing one source while monitoring offset; never step production clocks. DNS/AAA instance tests require change approval. | If time source independence cannot be established, record U10 and treat time as a single common-mode dependency. | IEEE 1588 (Precision Time Protocol); IETF RFC 5905 (Network Time Protocol version 4); IETF RFC 8915 (Network Time Security for NTP); AIDCF-004 (Threat, Hazard and Failure Model) | MCF-RES-013; MCF-RES-014; MCF-SEC-001; MCF-NET-015 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-OPS-001 | OPS | Building Operations and Service Management | OPS-01 | Operating model and staffing | 24x7 Coverage | Competent and authorised staff are present or available within response time, every hour of every day, in the numbers and disciplines needed to perform the time-critical tasks of the emergency procedures within the time-to-impact of the failures they address. | The operations manager shall define minimum staffing per shift and per discipline (electrical, mechanical/thermal, controls/BMS, NOC/IT infrastructure, security) derived from an emergency task analysis that lists the time-critical manual actions in each EOP (for example manual generator start or transfer, CDU failover, leak isolation, load shedding) and compares their completion time with the time-to-impact from MCF-DEP-003. The operations manager shall roster to that minimum, record every shift that falls below it and the compensating measures, and shall define on-call response times for specialists not on site. | 1) An emergency task analysis exists linking EOP time-critical actions to time-to-impact and required staff. 2) Minimum staffing per shift and discipline is derived from that analysis and approved. 3) Rosters and time-and-attendance records for the period show the minimum was met, or each shortfall is recorded with compensating measures. 4) On-call specialist response times are defined and met in call-outs during the period. 5) Fatigue limits (maximum shift length, consecutive shifts) are defined and adhered to. | Minimum on-site staff per shift [persons by discipline] default Site-specific (no default) (Derived from emergency task analysis; there is no universal staffing ratio.) On-call specialist attendance time [minutes] default 60 (Illustrative; must be shorter than the time available after on-site staff stabilise the event.) Maximum shift length [hours] default 12 (Illustrative; set with reference to HSE HSG256 guidance and local working-time law.) | Emergency task analysis.; Approved minimum staffing matrix.; Rosters and attendance records for the period.; Call-out logs with response times.; Shortfall records. | DOCUMENT_REVIEW; RECONCILIATION; SAMPLING; ANALYSIS; OBSERVATION | 1) Obtain the emergency task analysis and staffing matrix. 2) Check the analysis against EOP time-critical steps and DEP-003 time-to-impact. 3) Reconcile a sample of shifts (including nights and holidays) from access-control records to the minimum. 4) Sample call-outs and measure response times. 5) Observe a shift change and staffing on site during an unannounced visit where permitted. | PREVENTIVE | OPERATION | AL4 | COMMISSION; OPERATE; CHANGE | NORMAL; DEGRADED; MAINTENANCE; EMERGENCY; RECOVERY | Applies to all staffed facilities and NOCs supporting the Capability Instance; for provider-operated facilities assessed via MCF-DEP-018 evidence. |  | CG-13; CG-10 | Night shift below minimum when a generator fails to start; Specialist call-out takes longer than thermal ride-through; Fatigue-related operator error; Concurrent events exceed staff capacity | Resource; RequiredFunction; OperatingState | Unannounced observation shall not interfere with operations; staffing shall not be reduced to test resilience. | Missing attendance evidence for night and weekend shifts is U1, US3; escalate to US4 if a CG-05/06/10 criterion depends on manual action within ride-through. | Uptime Institute Tier Standard: Operational Sustainability; EN 50600-3-1 (management and operational information); HSE HSG256 (managing shift work) | MCF-DEP-008; MCF-OPS-004; MCF-OPS-005; MCF-DEP-003 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-OPS-002 | OPS | Building Operations and Service Management | OPS-01 | Operating model and staffing | Role Clarity | For every Required Function, dependency and operating state, it is clear who operates, who maintains, who monitors, who may approve change, who responds to alarms and who holds emergency decision authority, including across facilities, IT/NOC, tenant and provider teams. | The operations manager shall maintain a responsibility and authority matrix for every Required Function and material dependency across NORMAL, MAINTENANCE, EMERGENCY and RECOVERY states, naming the role and current holder (and deputy) for operation, maintenance, monitoring, change approval, alarm response and emergency decisions (for example authority to transfer to generator, shed load, power-cap or drain a cluster, isolate a cooling loop, or invoke an EOP). The matrix shall be consistent with GOV-02 accountability and with provider shared-responsibility records (MCF-DEP-018). | 1) A matrix covers every Required Function and material dependency for the four states. 2) Each role has a named current holder and deputy. 3) Emergency decision authorities are explicit, including cross-team decisions (facilities ordering IT load reduction and vice versa). 4) The matrix is consistent with GOV-02 and DEP-018 records. 5) Interviewed role holders can state their responsibilities and authorities consistently with the matrix. |  | Responsibility and authority matrix.; Named role holder list with deputies.; Cross-reference to GOV-02 and DEP-018.; Interview records. | DOCUMENT_REVIEW; INQUIRY; RECONCILIATION | 1) Obtain the matrix and holder list. 2) Check coverage against Required Functions and dependencies. 3) Reconcile with GOV-02 and DEP-018. 4) Interview a sample of holders using scenarios (for example cooling loss at sustained AI load). 5) Record gaps and inconsistencies. | DIRECTIVE | IMPLEMENTATION | AL3 | COMMISSION; OPERATE; CHANGE | NORMAL; MAINTENANCE; EMERGENCY; RECOVERY | Applies to all assessments. | CG-13 | CG-14 | No one authorised to order cluster power-capping during cooling loss; Facilities and NOC each assume the other responds; Deputy undefined at night | RequiredFunction; Dependency; OperatingState | Interviews only. | A Required Function with no identifiable emergency decision authority is US4 (CG-13 criterion). | ISO/IEC 20000-1 (service management system requirements); EN 50600-3-1 (management and operational information); ISO 22320 (emergency management: incident management) | MCF-GOV-005; MCF-GOV-006; MCF-DEP-018; MCF-RES-021 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-OPS-003 | OPS | Building Operations and Service Management | OPS-01 | Operating model and staffing | Shift Handover | Situational awareness is transferred completely at every shift change: plant and system state, active alarms, open permits and isolations, temporary configurations, deferred maintenance, degraded redundancy, in-progress work and expected events. | The shift lead shall conduct and record a structured handover at each shift change using a defined template covering: current operating state per system and redundancy level, active and standing alarms, open permits to work and isolations, temporary configurations and overrides, work in progress and planned work, deferred maintenance with risk, provider or tenant events, and expected events (deliveries, tests, high-load periods). Outgoing and incoming leads shall both sign, and the incoming lead shall verify critical items at the BMS/EPMS/NOC consoles. | 1) A handover template covering the listed elements exists. 2) Handover records exist for the sampled shifts, signed by both leads. 3) Open permits and temporary configurations in handover records reconcile with the permit and temporary-configuration registers at that time. 4) Incoming leads verified critical items at consoles (record or observation). |  | Handover template.; Handover records for sample.; Permit and temporary-configuration registers for the same times.; Observation of a handover. | DOCUMENT_REVIEW; RECONCILIATION; OBSERVATION; SAMPLING | 1) Obtain template and sample records. 2) Reconcile with permit and temporary-configuration registers. 3) Observe a live handover. 4) Record omissions. | PREVENTIVE | OPERATION | AL4 | OPERATE | NORMAL; DEGRADED; MAINTENANCE; EMERGENCY; RECOVERY | Applies to all shift-based operations, including NOC. |  | CG-04; CG-14 | Open isolation not handed over and re-energised; Alarm inhibit forgotten; Degraded redundancy unknown to incoming shift | OperatingState; Event; Safeguard | Observation shall not distract operators during the handover. | Missing handover records is U1, US3. | HSE HSG48 (reducing error and influencing behaviour); Uptime Institute Tier Standard: Operational Sustainability | MCF-OPS-007; MCF-OPS-019; MCF-OPS-012 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-OPS-004 | OPS | Building Operations and Service Management | OPS-01 | Operating model and staffing | Competence and Authorisation | Only people assessed as competent, and formally authorised for the task and system, perform hazardous or consequential work, including HV/LV switching, work on battery systems, liquid-cooling and pressurised fluid systems, refrigerants, and control-system changes. | The operations manager shall maintain a competence framework defining required knowledge, skills and assessment for each task class, and an authorisation register recording each person's authorisations (for example authorised person and competent person for HV/LV systems, refrigerant handling certification where legally required, liquid-cooling and CDU work, BMS/EPMS engineering), their scope, expiry and assessor. The operations manager shall verify contractor competence and authorisation before work and shall ensure permits (MCF-OPS-007) are issued only to authorised persons. | 1) Competence framework covers all hazardous and consequential task classes. 2) Authorisation register records scope, expiry and assessor for each person. 3) No authorisation in the sample has expired. 4) Permits in the sample were issued to and received by persons authorised for that task. 5) Contractor competence was verified before work for sampled jobs. | Authorisation revalidation interval [months] default 36 (Illustrative; set by site safety rules and legal requirements.) | Competence framework.; Authorisation register.; Training and assessment records.; Permit sample cross-referenced to register.; Contractor verification records. | DOCUMENT_REVIEW; RECONCILIATION; SAMPLING; INQUIRY | 1) Obtain framework and register. 2) Sample permits and reconcile issuers and receivers to authorisations. 3) Check expiry and scope. 4) Sample contractor jobs for pre-work verification. 5) Interview a sample of authorised persons on scope. | PREVENTIVE | OPERATION | AL4 | COMMISSION; OPERATE; CHANGE; DECOMMISSION | NORMAL; MAINTENANCE; EMERGENCY; RECOVERY | Applies to all hazardous and consequential work in the boundary, by staff or contractors. | CG-04 | CG-13 | Unauthorised person performs HV switching; Contractor without liquid-cooling competence breaks a pressurised loop; Expired authorisation | Resource; Safeguard; Hazard | Assessment is documentary and interview-based; no competence demonstration shall involve live hazardous work. | Inability to verify authorisation of persons receiving hazardous-energy permits is US4 (CG-04 critical). | BS EN 50110-1 (operation of electrical installations); NFPA 70E (electrical safety in the workplace); ISO 45001 (occupational health and safety management systems); HSE HSG85 (electricity at work: safe working practices) | MCF-OPS-007; MCF-OPS-008; MCF-GOV-023; MCF-DEP-008 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-OPS-005 | OPS | Building Operations and Service Management | OPS-02 | Procedure and work control | Standard Operating Procedures | Routine, alarm-response and emergency operations on critical infrastructure are performed from controlled, technically reviewed and current procedures (SOPs, alarm response procedures, EOPs) that match the as-built systems and are available at the point of use. | The operations manager shall maintain a controlled procedure set comprising SOPs for routine operation, alarm response procedures for critical alarms, and EOPs for each credible emergency scenario (including utility loss, generator failure to start, UPS failure, cooling loss at sustained AI load, CDU or secondary-loop failure, liquid leak, fire alarm and suppression interfaces, BMS/EPMS loss, and loss of NOC). Each procedure shall have an owner, technical reviewer, version and review date, shall be validated against the as-built system by walkthrough before issue, and shall be available at the point of use including when the BMS and IT systems are unavailable. | 1) The procedure set includes EOPs for each scenario in the RES-01 scenario list and alarm response procedures for each critical alarm. 2) Each procedure has owner, reviewer, version and review date within the interval. 3) A sample of procedures matches as-built equipment identifiers, valve and breaker designations and current setpoints. 4) Procedures are available in hard copy or offline form at points of use. 5) Walkthrough validation is recorded for procedures issued or revised in the period. | Procedure review interval [months] default 12 (Illustrative.) | Procedure register.; Sample procedures.; As-built cross-check records.; Walkthrough validation records.; Point-of-use inspection. | DOCUMENT_REVIEW; INSPECTION; SAMPLING; OBSERVATION | 1) Obtain register and map EOPs to scenarios. 2) Sample procedures and check control metadata. 3) Walk down sampled procedures against equipment. 4) Inspect point-of-use availability. 5) Observe an operator walk through an EOP. | DIRECTIVE | IMPLEMENTATION | AL3 | COMMISSION; OPERATE; CHANGE | NORMAL; MAINTENANCE; EMERGENCY; RECOVERY | Applies to all critical infrastructure operations. |  | CG-10; CG-13; CG-14 | EOP references removed equipment; No EOP for CDU failure; Procedures only on unavailable intranet; Operator error during alarm flood (scenario X11) | Safeguard; FailureScenario; OperatingState | Walk-downs follow site safety rules; walkthroughs shall not operate equipment. | Missing EOP for a scenario prioritised under CG-05/06/10 is a Finding (NONCONFORMING); inability to verify as-built match is US3. | Uptime Institute Tier Standard: Operational Sustainability; EN 50600-3-1 (management and operational information); ISO 22320 (emergency management: incident management) | MCF-OPS-006; MCF-OPS-013; MCF-RES-003; MCF-POW-023 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-OPS-006 | OPS | Building Operations and Service Management | OPS-02 | Procedure and work control | Method Statements | Non-routine work on critical infrastructure is executed from a task-specific method of procedure (MOP) that states the exact steps, hold points, isolation points, expected readings, redundancy exposure during the work, and back-out steps, so that maintenance and change do not cause outages. | The maintenance manager shall require an approved MOP for every non-routine task on critical infrastructure, including: scope and affected assets; the operating state and redundancy level during each step (for example N during work on one of N+1 UPS modules); preconditions (for example job checkpoint or workload drain agreed with the platform owner, spare on hand, weather); step-by-step actions with hold points and expected indications; isolation and LOTO points; back-out steps; communications plan; and approvals by engineering, operations and change control (MCF-OPS-018). The MOP shall be executed as written with each step signed off and deviations stopped and escalated. | 1) Every non-routine task in the sample had an approved MOP before work. 2) MOPs state redundancy exposure per step and preconditions including workload coordination. 3) Executed MOPs show step sign-off; deviations were stopped and escalated. 4) MOPs were reviewed by engineering and operations and linked to an approved change. 5) Back-out steps are present for each irreversible step boundary. |  | MOP register.; Sample of approved and executed MOPs.; Linked change records.; Deviation records. | DOCUMENT_REVIEW; SAMPLING; RECONCILIATION; OBSERVATION | 1) Extract non-routine work orders for the period. 2) Reconcile each to an approved MOP and change. 3) Check content against required elements. 4) Review executed sign-off and deviations. 5) Observe a MOP execution where scheduled. | PREVENTIVE | OPERATION | AL4 | COMMISSION; OPERATE; CHANGE; DECOMMISSION | MAINTENANCE; TRANSITION; DEGRADED | Applies to non-routine work on critical infrastructure. | CG-14 | CG-04 | Maintenance removes hidden shared dependency (scenario X04); Wrong breaker opened; Work during training run without checkpoint; No back-out when step fails | Safeguard; OperatingState; Event | Observation of MOP execution only from a safe position as directed by the person in charge; observers shall not operate equipment. | Non-routine work without a traceable MOP is a Finding; missing work-order data for the sample period is US4 (CG-14 critical). | Uptime Institute Tier Standard: Operational Sustainability; ISO 45001 (occupational health and safety management systems); EN 50600-3-1 (management and operational information) | MCF-OPS-007; MCF-OPS-018; MCF-OPS-020; MCF-THM-023 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-OPS-007 | OPS | Building Operations and Service Management | OPS-02 | Procedure and work control | Permit to Work | Hazardous work is authorised, controlled, coordinated and handed back through a permit-to-work system so that hazardous energy, fluids, confined spaces, hot work and work at height are controlled and conflicting work is prevented. | The facility operator shall operate a permit-to-work system for hazardous work, including electrical (HV and LV), battery and DC systems, hot work, confined spaces (for example tanks, pits, trenches, plenums), work at height, pressurised and liquid-cooling systems, refrigerants and fire-suppression systems. Each permit shall identify the work, hazards, isolations (cross-referenced to LOTO), precautions, issuer and receiver (both authorised under MCF-OPS-004), validity period, and cross-references to other live permits in the same system. Permits shall be suspended at shift change unless re-validated, and closed only after hand-back confirms the system is safe to return to service. | 1) Permit types cover all hazardous work categories present on site. 2) Sampled permits are complete and issuer and receiver are authorised. 3) Conflicting permits in the same system were cross-referenced and coordinated. 4) Permits were suspended or re-validated at shift change. 5) Hand-back records confirm the system state before return to service. 6) Periodic audits of live permits at the worksite were performed and findings closed. | Permit audit frequency [audits per month] default 4 (Illustrative.) | Permit procedure.; Permit register and sample permits.; Cross-reference to LOTO records.; Worksite permit audits. | DOCUMENT_REVIEW; SAMPLING; INSPECTION; OBSERVATION | 1) Obtain permit procedure and register. 2) Sample permits across types. 3) Check completeness, authorisation, cross-reference and hand-back. 4) Inspect live permits at worksites. 5) Review audit findings. | PREVENTIVE | OPERATION | AL4 | BUILD; COMMISSION; OPERATE; CHANGE; DECOMMISSION | NORMAL; MAINTENANCE; EMERGENCY; RECOVERY | Applies to all hazardous work in the boundary including contractors and provider staff in owner spaces. | CG-04 |  | Conflicting work on same electrical system; Confined-space entry without permit; Liquid loop opened while pressurised; System returned to service before hand-back | Safeguard; Hazard; Event | Worksite inspection only under escort of the permit issuer; assessors shall not enter the permit boundary unless included on the permit. | Missing permit records for hazardous work in the period is US4 (CG-04 critical). | HSE HSG250 (guidance on permit-to-work systems); ISO 45001 (occupational health and safety management systems); NFPA 70E (electrical safety in the workplace); BS EN 50110-1 (operation of electrical installations) | MCF-OPS-004; MCF-OPS-008; MCF-OPS-003; MCF-PHY-024 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-OPS-008 | OPS | Building Operations and Service Management | OPS-02 | Procedure and work control | Lockout and Tagout | All hazardous energy sources (electrical including back-feeds and DC/battery sources, stored energy in capacitors and UPS, mechanical, hydraulic and pneumatic, pressurised coolant, thermal) are isolated, locked, tagged and proven dead or depressurised before work, and restored only under control. | The facility operator shall define LOTO procedures for each equipment class that identify every energy source (including generator, UPS and battery back-feeds, BESS, capacitors, CDU pumps, pressurised secondary loops and facility water), the isolation points, locking devices, and the method to prove isolation (test-before-touch with a proven tester, pressure and temperature verification). Each worker shall apply a personal lock, group lockboxes shall be used for multi-worker jobs, and restoration shall follow a verified sequence. The facility operator shall audit LOTO practice at the profile interval. | 1) Equipment-specific LOTO procedures identify all energy sources including back-feeds and stored energy. 2) Sampled jobs have LOTO records with personal locks, proving tests and restoration sign-off. 3) Testers are proven before and after use (live-dead-live) and are in calibration. 4) LOTO audits were performed at the interval and findings closed. | LOTO field audit interval [months] default 3 (Illustrative.) | Equipment LOTO procedures.; LOTO records for sampled jobs.; Tester calibration records.; Audit reports. | DOCUMENT_REVIEW; SAMPLING; OBSERVATION; INSPECTION | 1) Obtain procedures and verify energy-source identification against SLDs and P&IDs for a sample. 2) Sample LOTO records. 3) Check tester calibration. 4) Observe a LOTO application from a safe position. 5) Review audits. | PREVENTIVE | OPERATION | AL4 | BUILD; COMMISSION; OPERATE; DECOMMISSION | MAINTENANCE; EMERGENCY; RECOVERY | Applies to all work requiring isolation of hazardous energy. | CG-04 |  | Back-feed from UPS output energises isolated busway; Battery DC source not isolated; Pressurised coolant released on disconnection; Isolation removed by another worker | Safeguard; Hazard; AssetInstance | Assessors shall only observe; they shall never apply, remove or test locks or test-before-touch themselves. | LOTO procedures not identifying back-feed or stored-energy sources is a Finding; missing LOTO records is US4 (CG-04 critical). | OSHA 29 CFR 1910.147 (control of hazardous energy); NFPA 70E (electrical safety in the workplace); BS EN 50110-1 (operation of electrical installations); ISO 14118 (safety of machinery: prevention of unexpected start-up) | MCF-OPS-007; MCF-OPS-004; MCF-POW-012; MCF-THM-020 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-OPS-009 | OPS | Building Operations and Service Management | OPS-03 | Maintenance and reliability | Maintenance Strategy | Each critical asset class has a maintenance strategy (preventive, predictive, condition-based or run-to-failure) justified by its failure modes and consequence, aligned with OEM requirements and recognised practice, and executable without exceeding the redundancy available in the MAINTENANCE state. | The maintenance manager shall define and approve a maintenance strategy for each critical asset class (including MV/LV switchgear and protection, transformers, UPS and batteries, generators and fuel systems, busways and PDUs, chillers, CRAH/fan walls, CDUs and secondary loops, pumps, cooling towers or dry coolers, BMS/EPMS, fire detection and suppression, and IT infrastructure hardware) stating tasks, intervals, basis (OEM, recognised practice, reliability analysis), and the operating state and redundancy level during each task. The capability owner shall confirm that each maintenance configuration leaves capacity sufficient for the declared load, or that maintenance windows are coordinated with workload reduction. | 1) A maintenance strategy exists per critical asset class with stated basis. 2) Intervals are consistent with OEM requirements or deviations are justified. 3) Each task states the redundancy level during the task and the capacity check for declared load. 4) Run-to-failure decisions are limited to items whose failure is tolerable and are approved. 5) The strategy is approved by a competent engineer. | Generator load test frequency [per year] default Per NFPA 110 or site standard (no default) (Set from the adopted standard and OEM requirements.) | Maintenance strategy documents.; OEM maintenance requirements.; Maintenance-state capacity checks.; Approval records. | DOCUMENT_REVIEW; ANALYSIS | 1) Obtain strategies. 2) Check coverage of critical classes. 3) Compare intervals with OEM requirements. 4) Check maintenance-state capacity analyses against current load. 5) Check approvals. | DIRECTIVE | DESIGN | AL2 | DESIGN; COMMISSION; OPERATE; CHANGE | NORMAL; MAINTENANCE | Applies to all critical asset classes. |  | CG-05; CG-06 | Maintenance on one CDU leaves insufficient capacity at current AI load; Battery maintenance interval exceeded; Protection relays never tested | AssetInstance; OperatingState; CapacityAssertion; Safeguard | Desk-based. | No maintenance-state capacity check for a redundant group is US3; US4 where CG-05 or CG-06 maintenance-state criteria rely on it. | NFPA 70B (electrical equipment maintenance); NFPA 110 (emergency and standby power systems); IEC 60300-3-11 (reliability centred maintenance); SAE JA1011 (RCM evaluation criteria); ISO 55001 (asset management systems) | MCF-POW-022; MCF-THM-023; MCF-OPS-010; MCF-OPS-012 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-OPS-010 | OPS | Building Operations and Service Management | OPS-03 | Maintenance and reliability | Condition Monitoring | Deterioration of critical assets is detected before functional failure through defined condition-monitoring techniques with thresholds and actions. | The maintenance manager shall operate condition monitoring for critical assets using techniques appropriate to their failure modes, for example infrared thermography of electrical connections, partial discharge monitoring on MV equipment, dissolved gas and oil analysis on transformers, battery impedance or conductance and temperature monitoring, vibration analysis on pumps, fans and chillers, coolant quality monitoring (conductivity, pH, inhibitor and biocide levels, particulates) on liquid-cooling loops, and filter differential pressure. Each technique shall have defined thresholds and response actions, and exceedances shall generate work orders. | 1) Techniques are defined per critical asset class aligned to failure modes. 2) Measurements were taken at the defined frequency in the period. 3) Thresholds and actions are defined; exceedances generated work orders that were completed. 4) Coolant quality for liquid-cooled systems is within the OEM-specified envelope or deviations were actioned. | Thermography frequency for critical switchgear and busway [per year] default 1 (Illustrative; NFPA 70B provides guidance.) Coolant quality sampling interval [weeks] default 4 (Illustrative; set from CDU and cold-plate OEM requirements.) | Condition monitoring plan.; Measurement records and reports.; Threshold definitions.; Work orders from exceedances. | DOCUMENT_REVIEW; SAMPLING; ANALYSIS | 1) Obtain plan. 2) Sample records and check frequency. 3) Trace exceedances to work orders. 4) Review coolant quality data against OEM envelope. | DETECTIVE | OPERATION | AL4 | OPERATE | NORMAL; MAINTENANCE; DEGRADED | Applies to critical asset classes. |  | CG-05; CG-06 | Hot joint on busway undetected; Coolant contamination fouls cold plates; Transformer incipient fault missed; Battery cell failure undetected | AssetInstance; Event; Safeguard | Thermography and partial-discharge surveys of energised equipment are hazardous; they shall be carried out by qualified persons under the site's electrical safety rules and, where covers are removed, under permit with appropriate arc-flash PPE. | No condition monitoring for a critical class is US3. | NFPA 70B (electrical equipment maintenance); ISO 17359 (condition monitoring and diagnostics of machines); IEC 60599 (dissolved gas analysis interpretation); IEC 60270 (partial discharge measurements); ISO 20816 (mechanical vibration); ASHRAE TC 9.9 liquid cooling guidance | MCF-OPS-009; MCF-THM-018; MCF-POW-010 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-OPS-011 | OPS | Building Operations and Service Management | OPS-03 | Maintenance and reliability | Calibration | Instruments whose readings drive control, protection, alarming, billing or assurance decisions (temperature, pressure, flow, leak, power and energy meters, CTs/VTs, protection relays, gas detectors, and the test instruments used by technicians) are calibrated to traceable standards at defined intervals, so that control loops and evidence are trustworthy. | The maintenance manager shall maintain a calibration register for critical instruments, including sensors used in BMS/EPMS/CDU control loops and alarms, protection relays (secondary injection testing), revenue and sub-meters, leak detection, and portable test equipment, stating interval, method, traceability and tolerance. Out-of-tolerance results shall trigger an impact assessment of decisions and evidence that relied on the instrument since its last good calibration. | 1) Register covers instruments in control loops, alarms, protection and evidence. 2) Calibrations in the sample were performed within interval with traceable certificates. 3) Out-of-tolerance results had impact assessments. 4) Protection relay testing records are current. | Calibration interval for control-loop temperature sensors [months] default 12 (Illustrative; set from OEM and criticality.) | Calibration register.; Calibration certificates.; Relay test reports.; Out-of-tolerance impact assessments. | DOCUMENT_REVIEW; SAMPLING; INSPECTION | 1) Obtain register. 2) Sample instruments by tag and verify certificate and date. 3) Inspect calibration labels on a sample in the field. 4) Review out-of-tolerance handling. | PREVENTIVE | OPERATION | AL4 | COMMISSION; OPERATE; CHANGE | NORMAL; MAINTENANCE | Applies to critical instruments. |  | CG-07 | Drifted supply-temperature sensor causes CDU to under-cool; Uncalibrated leak sensor; Protection relay maloperation | AssetInstance; EvidenceObject; Safeguard | Relay secondary injection and in-situ calibration of control-loop sensors require permits and control-system owner authorisation; assessors only inspect labels and records. | Unknown calibration status of control-loop sensors is US3; US4 where CG-07 relies on them. | ISO 10012 (measurement management systems); ISO/IEC 17025 (competence of testing and calibration laboratories); NFPA 70B (electrical equipment maintenance) | MCF-THM-022; MCF-POW-021; MCF-OPS-013 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-OPS-012 | OPS | Building Operations and Service Management | OPS-03 | Maintenance and reliability | Deferred Maintenance | Maintenance that is deferred, overdue or cancelled is visible, risk-assessed, approved by someone with authority, time-limited and reflected in the declared operating state, so that the accumulated risk of deferral does not silently erode resilience. | The maintenance manager shall record every deferral or overdue item of maintenance on critical assets in a deferred maintenance register with reason, risk assessment, compensating measures, approver with authority, and expiry date. Deferrals beyond the profile limit shall require re-approval by the accountable owner. Deferred safety-critical maintenance shall be reflected in the operating state (for example the system declared DEGRADED) and in handover (MCF-OPS-003). | 1) All overdue critical maintenance in the CMMS appears in the register. 2) Each deferral has risk assessment, approver and expiry. 3) No deferral exceeds the limit without re-approval. 4) Safety-critical deferrals are reflected in operating state and handover. 5) Aggregate deferral is reported to the accountable owner. | Maximum deferral without re-approval [days] default 30 (Illustrative.) | Deferred maintenance register.; CMMS overdue report.; Approvals.; Operating-state records. | RECONCILIATION; SAMPLING; DOCUMENT_REVIEW | 1) Extract overdue items from CMMS. 2) Reconcile to register. 3) Sample approvals and expiry. 4) Check operating-state reflection. | CORRECTIVE | OPERATION | AL4 | OPERATE | NORMAL; DEGRADED; MAINTENANCE | Applies to critical assets. |  | CG-05; CG-06; CG-13 | Generator maintenance repeatedly deferred; Overdue battery replacement; Hidden accumulation of deferrals | Action; OperatingState; AssetInstance | Records review; inspection of deferred assets is visual only and follows site access rules. | CMMS data unavailable is U2, US3. | ISO 55001 (asset management systems); NFPA 70B (electrical equipment maintenance) | MCF-OPS-009; MCF-OPS-003; MCF-OPS-024; MCF-GOV-007 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-OPS-013 | OPS | Building Operations and Service Management | OPS-04 | Alarm, incident and problem management | Alarm Rationalisation | Alarms from BMS, EPMS, CDU, fire, leak detection, security and NOC systems are rationalised so that every alarm is meaningful, prioritised by consequence and time to respond, has a defined response, and the alarm load on operators remains manageable in normal and upset conditions. | The control-system owner shall maintain an alarm philosophy and master alarm database for in-scope monitoring systems in which each alarm has a documented cause, consequence, priority (derived from consequence and time-to-impact per MCF-DEP-003), setpoint basis, and response procedure. The control-system owner shall measure alarm performance (alarm rates per operator in normal and upset conditions, standing alarms, chattering alarms, shelved or suppressed alarms) at the profile interval, act on exceedances, and control alarm suppression and shelving through MCF-OPS-019. | 1) An approved alarm philosophy exists covering priority definitions and performance targets. 2) Each critical alarm in a sample has cause, consequence, priority, setpoint basis and response procedure. 3) Priorities are consistent with time-to-impact (no low-priority alarm on a seconds-scale consequence). 4) Alarm performance metrics are measured at the interval in normal and upset periods, and exceedances actioned. 5) Shelved and suppressed alarms are recorded, time-limited and reviewed. 6) Critical alarms are annunciated to a continuously attended location with defined escalation. | Target average alarm rate per operator in normal operation [alarms per hour] default Per alarm philosophy (no default) (Set in the alarm philosophy with reference to IEC 62682 / ANSI/ISA-18.2 and EEMUA 191 benchmarks.) Alarm performance review interval [months] default 1 (Illustrative.) | Alarm philosophy.; Master alarm database extract.; Alarm performance reports for the period, including an upset event.; Shelving/suppression log. | DOCUMENT_REVIEW; ANALYSIS; SAMPLING; OBSERVATION | 1) Obtain philosophy and database. 2) Sample critical alarms and check rationalisation fields. 3) Cross-check priorities with DEP-003 time-to-impact. 4) Compute alarm rates and standing/chattering counts from raw logs. 5) Review shelving log. 6) Observe console annunciation and escalation. | DETECTIVE | OPERATION | AL4 | COMMISSION; OPERATE; CHANGE | NORMAL; DEGRADED; EMERGENCY; MAINTENANCE | Applies to all monitoring systems annunciating to operators for in-scope infrastructure. | CG-07 | CG-06; CG-05 | Operator error during alarm flood (scenario X11); Critical CDU alarm buried among nuisance alarms; Leak alarm shelved and forgotten; Alarm routed to unattended console | Safeguard; Event; InfrastructureSystem | Analysis of logs only; no alarms shall be generated on live systems for assessment, except under an approved test plan with operators informed. | Raw alarm logs unavailable is U1, US4 (CG-07 critical). | IEC 62682 (management of alarm systems for the process industries); ANSI/ISA-18.2 (management of alarm systems); EEMUA Publication 191 (alarm systems guide) | MCF-DEP-003; MCF-OPS-019; MCF-THM-008; MCF-POW-021 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-OPS-014 | OPS | Building Operations and Service Management | OPS-04 | Alarm, incident and problem management | Incident Response | Incidents affecting infrastructure or Service Outcomes are detected, classified by outcome impact, escalated, coordinated across facilities, NOC, platform, tenant and provider teams, and stabilised within defined timescales. | The operations manager shall operate an incident management process that classifies incidents by Service Outcome impact and safety, defines escalation timescales and authorities, establishes a joint bridge between facilities, NOC, platform and provider teams for cross-domain incidents, links to EOPs and to RES-06 crisis command, records a timeline, and requires a post-incident review for incidents above the profile threshold. | 1) Classification criteria reference Service Outcome impact and safety. 2) Escalation timescales are defined and met in sampled incidents. 3) Cross-domain incidents had a joint bridge with facilities and IT participation. 4) Incident timelines are recorded. 5) Post-incident reviews were held above threshold. | Escalation time for Service Outcome-impacting incidents [minutes] default 15 (Illustrative.) | Incident procedure.; Incident records for period.; Bridge logs.; Post-incident reviews. | DOCUMENT_REVIEW; SAMPLING; RECONCILIATION; INQUIRY | 1) Obtain procedure. 2) Sample incidents including cross-domain ones. 3) Reconstruct timelines from BMS/EPMS/NOC logs. 4) Compare escalation to timescales. 5) Review post-incident reviews. | CORRECTIVE | OPERATION | AL4 | OPERATE | DEGRADED; EMERGENCY; RECOVERY | Applies to all infrastructure incidents within the boundary, including those initiated by providers or tenants. |  | CG-10; CG-13 | Facilities and NOC work separately on a cooling incident; Escalation delayed; No timeline recorded | Event; Finding; Action | Records review and interviews; incident simulations, if used, follow RES-05 exercise controls and are announced to operators. | Incident records incomplete is US3. | ISO 22320 (emergency management: incident management); ISO/IEC 20000-1 (service management system requirements); ISO/IEC 27035 (information security incident management) | MCF-RES-021; MCF-OPS-015; MCF-OPS-005; MCF-SEC-019 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-OPS-015 | OPS | Building Operations and Service Management | OPS-04 | Alarm, incident and problem management | Root Cause Analysis | Significant incidents and near misses are analysed to their root and contributing causes, including latent design, organisational and human-factors causes, so that corrective actions address causes rather than symptoms. | The operations manager shall require a root cause analysis using a recognised method for each incident or near miss above the profile threshold, completed within the profile time, identifying direct, contributing and root causes (including procedure, competence, alarm, design, supplier and organisational factors), propagation beyond expected containment, and corrective and preventive actions with owners. RCAs of provider-caused events shall be obtained from the provider and assessed. | 1) RCAs exist for incidents above threshold, completed within time. 2) A recognised method is used and contributing human and organisational factors are considered. 3) Propagation beyond expected fault domain is identified where it occurred. 4) Actions have owners and dates. 5) Provider RCAs were obtained and assessed. | RCA completion time [working days] default 20 (Illustrative.) | RCA reports.; Action records.; Provider RCAs. | DOCUMENT_REVIEW; SAMPLING; ANALYSIS | 1) Identify incidents above threshold. 2) Check RCA existence and timeliness. 3) Assess depth of analysis for a sample. 4) Check actions. | CORRECTIVE | OPERATION | AL4 | OPERATE; CHANGE | NORMAL; RECOVERY | Applies to incidents and near misses above the profile threshold, including provider-caused events affecting the boundary. |  | CG-09 | Blame attributed to individual without systemic cause; Same failure recurs; Propagation path not understood | Finding; FailureScenario; Action | Records review; RCA interviews shall not be used to attribute individual blame. | Missing RCAs is US3. | IEC 62740 (root cause analysis); HSE HSG245 (investigating accidents and incidents); IEC 61025 (fault tree analysis) | MCF-OPS-014; MCF-OPS-016; MCF-RES-020 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-OPS-016 | OPS | Building Operations and Service Management | OPS-04 | Alarm, incident and problem management | Problem Elimination | Corrective and preventive actions from incidents, RCAs, audits and trends are implemented and verified to have eliminated or reduced recurrence, and known errors are managed until fixed. | The operations manager shall track problems and corrective/preventive actions to closure, shall verify effectiveness of closed actions by evidence that the failure mode has not recurred over a defined period or by test, shall maintain a known-error record with workarounds for unresolved problems, and shall review recurrence trends at the profile interval. | 1) Problems and actions are tracked with owners and dates. 2) Closed actions have effectiveness verification. 3) No recurrence of verified-closed failure modes in the period, or recurrence reopened the problem. 4) Known errors have workarounds communicated to operators. | Effectiveness verification period [months] default 6 (Illustrative.) | Problem register.; Action closure and verification records.; Recurrence analysis.; Known-error records. | DOCUMENT_REVIEW; ANALYSIS; SAMPLING | 1) Obtain register. 2) Sample closed actions and check verification. 3) Analyse incident data for recurrence. 4) Review known errors. | CORRECTIVE | EFFECTIVENESS | AL5 | OPERATE; CHANGE | NORMAL; DEGRADED | Applies to problems arising from incidents, RCAs, audits, assessments and trend analysis in the boundary. |  | CG-14 | Actions closed without implementation; Recurring failure; Workaround unknown to night shift | Action; Finding; ValidationResult | Effectiveness tests follow owning-domain test controls and authorisation. | No verification evidence for closed actions is US3. | ISO/IEC 20000-1 (service management system requirements); ISO 9001 (quality management systems) | MCF-OPS-015; MCF-RES-020; MCF-DEP-020 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-OPS-017 | OPS | Building Operations and Service Management | OPS-05 | Change and configuration management | Configuration Baseline | An authoritative, current baseline exists for the configuration of facility and AI infrastructure that matters to Required Functions, so that changes can be assessed against it, drift detected and known-good states restored. | The configuration manager shall maintain an approved configuration baseline covering, at minimum: as-built single-line diagrams and P&IDs; protection settings and coordination study revision; BMS/EPMS/CDU setpoints, sequences of operation and PLC logic versions; UPS, ATS and PDU settings; firmware and software versions of facility and IT infrastructure; network and fabric configurations; storage and cluster-manager configuration. The baseline shall be versioned, access-controlled, reconciled to the live state at the profile interval and after each change, and backed up outside the fault domain it describes. | 1) The baseline covers each listed category for in-scope systems. 2) Baseline items are versioned and access-controlled. 3) Live configuration in a sample reconciles to baseline, or drift is recorded and dispositioned. 4) Drawings (SLD, P&ID) match as-built for a sample walk-down. 5) Baseline backups are held outside the fault domain and restorable. | Baseline reconciliation interval [months] default 6 (Illustrative; continuous automated drift detection where available.) | Baseline repository index.; Live configuration exports for sample.; Drift reports.; Drawing walk-down record.; Backup location and restore test evidence. | DOCUMENT_REVIEW; RECONCILIATION; INSPECTION; SAMPLING | 1) Obtain baseline index. 2) Sample systems across categories. 3) Capture live configuration (read-only) and compare. 4) Walk down drawings for a sample. 5) Verify backup location and restore evidence. | PREVENTIVE | IMPLEMENTATION | AL3 | COMMISSION; OPERATE; CHANGE; DECOMMISSION | NORMAL; MAINTENANCE; RECOVERY; TRANSITION | Applies to all in-scope configurable systems. | CG-14 | CG-02; CG-07 | Protection settings differ from coordination study; CDU setpoint drift; Recovery reintroduces corrupt configuration (scenario X15); SLD out of date | ArchitectureSnapshot; AssetInstance; EvidenceObject | Configuration capture shall be read-only; reading protection relay settings requires the relay owner's procedure. | No baseline for a category of control-system configuration is US4 (CG-14 critical). | SAE EIA-649C (configuration management standard); ISO 10007 (guidelines for configuration management); ISO/IEC 20000-1 (service management system requirements) | MCF-OPS-018; MCF-NET-022; MCF-CMP-004; MCF-RES-015; MCF-SUP-013 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-OPS-018 | OPS | Building Operations and Service Management | OPS-05 | Change and configuration management | Change Assessment | Every change to critical facility or AI infrastructure is classified, impact-assessed against the dependency graph, fault domains and redundancy, scheduled in coordination with workloads, and approved by people with authority across facilities and IT before implementation. | The change manager shall operate a change process that requires, for each change to in-scope infrastructure: classification (standard, normal, emergency) with criteria; impact assessment that identifies affected Required Functions using the asset-to-function and dependency maps, redundancy and fault-domain exposure during the change, safety implications, and workload coordination (for example checkpoint or drain); a linked MOP for non-routine work; approval by a change authority with both facilities and IT representation for cross-domain changes; and conflict checking against other scheduled changes and maintenance. Emergency changes shall be retrospectively reviewed. | 1) Change classification criteria are defined. 2) Sampled changes have documented impact assessment using dependency and fault-domain data. 3) Cross-domain changes were approved with both facilities and IT representation. 4) Conflicting changes were detected and resolved by scheduling. 5) Emergency changes were reviewed retrospectively. 6) No changes to in-scope systems occurred without a change record (reconciled against configuration drift and logs). | Emergency change retrospective review time [working days] default 5 (Illustrative.) | Change procedure.; Change records for period.; CAB minutes.; Reconciliation of configuration changes to change records. | DOCUMENT_REVIEW; SAMPLING; RECONCILIATION; ANALYSIS | 1) Obtain procedure. 2) Sample changes across classes. 3) Check impact assessments for dependency and fault-domain analysis. 4) Check approvals. 5) Reconcile configuration drift and device logs to change records. 6) Review emergency changes. | PREVENTIVE | OPERATION | AL4 | OPERATE; CHANGE | NORMAL; MAINTENANCE; TRANSITION | Applies to all changes to in-scope infrastructure. | CG-14 | CG-03 | Change removes hidden shared dependency (scenario X04); IT change triggers load step without facilities approval; Concurrent changes reduce redundancy twice; Unrecorded change | Event; Dependency; FaultDomain; ReassessmentTrigger | Not applicable (records review). | Inability to reconcile changes (no logs) is US4 (CG-14 critical). | ISO/IEC 20000-1 (service management system requirements); ITIL 4 change enablement practice guide; SAE EIA-649C (configuration management standard) | MCF-OPS-006; MCF-OPS-017; MCF-OPS-020; MCF-RES-023; MCF-CAP-023 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-OPS-019 | OPS | Building Operations and Service Management | OPS-05 | Change and configuration management | Temporary Configuration | Temporary configurations (bypasses, jumpers, forced points, overrides, manual mode on automatic systems, inhibited or shelved alarms, temporary chillers or generators, load banks, temporary cabling and hoses) are approved, registered, time-limited, visible to operators and removed with verification. | The shift lead shall record every temporary configuration of critical infrastructure in a temporary configuration register with description, reason, risk assessment, approver, expiry, compensating measures and removal verification. Temporary configurations shall be visible at the operator console where technically possible, included in handover, reviewed at each expiry, and any extension shall be re-approved. Safety-system overrides (fire, leak, gas detection, emergency power off) shall require approval at the level set in the capability profile. | 1) Register exists and is current. 2) Live temporary configurations found on inspection or console are in the register. 3) Each entry has approver and expiry; expired entries were removed or re-approved. 4) Safety-system overrides had the required approval level. 5) Removal verification is recorded. | Maximum temporary configuration duration without re-approval [days] default 7 (Illustrative.) | Temporary configuration register.; BMS/EPMS forced-point and override reports.; Alarm shelving log.; Removal records. | RECONCILIATION; INSPECTION; SAMPLING; DOCUMENT_REVIEW | 1) Obtain register. 2) Extract overrides, forced points and shelved alarms from BMS/EPMS/CDU. 3) Reconcile to register. 4) Inspect plant for physical temporary configurations. 5) Check approvals and removal verification. | PREVENTIVE | OPERATION | AL4 | COMMISSION; OPERATE; CHANGE | MAINTENANCE; DEGRADED; EMERGENCY; NORMAL; RECOVERY | Applies to all critical infrastructure. |  | CG-14; CG-07; CG-04 | CDU left in manual after maintenance; Fire alarm zone isolated and forgotten; UPS left on maintenance bypass; Forced BMS point masks failure | OperatingState; Safeguard; Event | Inspection is visual; assessors shall not remove or alter any temporary configuration. | Inability to extract overrides from a control system is US3; US4 if a safety-system override cannot be ruled out. | IEC 62682 (management of alarm systems); HSE HSG250 (guidance on permit-to-work systems) | MCF-OPS-003; MCF-OPS-013; MCF-POW-012; MCF-OPS-017 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-OPS-020 | OPS | Building Operations and Service Management | OPS-05 | Change and configuration management | Rollback and Validation | Each material change can be reversed to a known-good state when it fails, and its success is validated by defined post-change tests and observation before the change is closed and redundancy is declared restored. | The change manager shall require each material change to define back-out criteria, a back-out procedure tested or rehearsed where practicable, and post-change validation (functional checks, telemetry review, alarm review, redundancy restoration check, and for IT infrastructure job or health checks) with evidence attached before closure. Failed validations shall trigger back-out or an incident, and post-implementation review shall be held for failed or backed-out changes. | 1) Sampled material changes define back-out criteria and procedure. 2) Post-change validation evidence is attached before closure. 3) Redundancy restoration was confirmed for changes affecting redundant systems. 4) Failed validations led to back-out or incident. 5) Back-out procedures for high-risk changes were rehearsed or tested. | Post-change observation period for facility control changes [hours] default 24 (Illustrative.) | Change records with back-out plans.; Validation evidence.; Back-out rehearsal records.; Post-implementation reviews. | DOCUMENT_REVIEW; SAMPLING; REPERFORMANCE; ANALYSIS | 1) Sample material changes. 2) Check back-out and validation evidence. 3) Reperform a validation check from telemetry for a sample. 4) Review failed changes. | CORRECTIVE | EFFECTIVENESS | AL5 | CHANGE; OPERATE | MAINTENANCE; TRANSITION; NORMAL; RECOVERY | Applies to material changes. | CG-14 | CG-10 | Change closed while redundancy not restored; No back-out for firmware change; Silent degradation after change | ValidationResult; TestRecord; Event | Back-out rehearsals on facility systems require MOP, permit and change approval. | Closed material changes without validation evidence is US4 (CG-14 critical). | ISO/IEC 20000-1 (service management system requirements); SAE EIA-649C (configuration management standard) | MCF-OPS-018; MCF-CMP-016; MCF-SEC-024; MCF-SUP-015 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-OPS-021 | OPS | Building Operations and Service Management | OPS-06 | Capacity and service operations | Capacity Review | Power, cooling, space, network and contracted utility capacity is reviewed against measured demand and committed growth, by operating state, so that new deployments are admitted only where capacity including maintenance and failure states is available. | The capacity manager shall review at the profile interval rated, available, reserved, consumed and headroom capacity for each capacity-bearing element (utility contract, transformers, UPS systems, busways and PDUs, generator capacity, chiller and heat-rejection plant, CDU and secondary loops, air cooling, floor loading, network ports and optics), considering N and N-1 (maintenance) states and transient AI load behaviour (for example synchronous training power swings). New deployments shall pass a capacity admission check against these values before installation. | 1) Capacity is recorded per element with rated, available, reserved, consumed and headroom values from measured data. 2) N-1 and maintenance-state headroom is calculated. 3) Transient and peak AI load behaviour is considered (from CAP-04 and POW-05). 4) Deployments in the period passed a documented admission check. 5) Elements approaching threshold triggered action. | Capacity planning threshold [% of N-1 available capacity] default 80 (Illustrative.) | Capacity reports.; Measured demand data (EPMS, BMS, CDU telemetry).; Admission check records.; Actions for elements above threshold. | ANALYSIS; SAMPLING; RECONCILIATION; DOCUMENT_REVIEW | 1) Obtain capacity reports. 2) Recompute headroom from telemetry for a sample. 3) Check N-1 analysis. 4) Sample deployments and check admission. 5) Check actions above threshold. | DETECTIVE | OPERATION | AL4 | PLAN; OPERATE; CHANGE | NORMAL; MAINTENANCE; DEGRADED | Applies to all capacity-bearing elements. |  | CG-05; CG-06 | Deployment exceeds N-1 UPS capacity; CDU loop above capacity in maintenance; Expansion creates stranded compute (scenario X17) | CapacityAssertion; Resource; OperatingState | Analysis only. | No measured data for a capacity element is US3; US4 where CG-05/06 capacity criteria rely on it. | ISO/IEC 20000-1 (service management system requirements); EN 50600-3-1 (management and operational information) | MCF-CAP-014; MCF-POW-015; MCF-THM-010; MCF-OPS-023 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-OPS-022 | OPS | Building Operations and Service Management | OPS-06 | Capacity and service operations | Service Level Monitoring | Service Outcome indicators (for example accelerator availability per partition, job interruption rate attributable to infrastructure, inference latency and availability, environmental envelope compliance at the IT inlet or coolant supply, power and cooling availability to tenants) are measured accurately and visibly to the NOC and BMS operators. | The operations manager shall define and measure indicators for each Service Outcome, with measurement method, source, and data quality checks, shall display them to NOC and BMS operators in an integrated view, and shall report performance against tolerance at the profile interval. | 1) Indicators are defined for each Service Outcome with method and source. 2) Measurement data quality (gaps, clock alignment) is checked. 3) Operators have an integrated view of facility and IT indicators. 4) Performance against tolerance is reported. | Indicator reporting interval [months] default 1 (Illustrative.) | Indicator definitions.; Measurement data.; Dashboard observation.; Reports. | ANALYSIS; OBSERVATION; DOCUMENT_REVIEW | 1) Obtain definitions. 2) Recompute a sample. 3) Observe operator view. 4) Review reports. | DETECTIVE | OPERATION | AL4 | COMMISSION; OPERATE | NORMAL; DEGRADED; RECOVERY | Applies to all declared Service Outcomes. |  |  | Outcome degradation invisible to facilities operators; Indicator computed from incomplete data | ServiceOutcome; Event; EvidenceObject | Observation of operator displays only; assessors shall not interact with operator consoles. | No measurement for a Service Outcome is US3 (it limits OPERATION claims across domains). | ISO/IEC 20000-1 (service management system requirements); ASHRAE TC 9.9 thermal guidelines | MCF-CAP-005; MCF-CAP-006; MCF-OPS-024; MCF-EVA-023 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-OPS-023 | OPS | Building Operations and Service Management | OPS-06 | Capacity and service operations | Resource Balancing | Load is placed and balanced across phases, PDUs, UPS modules, busways, CDU loops and rows so that no element exceeds its rating in N or N-1 states, capacity is not stranded, and AI workload controls (power capping, placement constraints) are coordinated with facility limits. | The capacity manager shall define placement rules and balance limits (phase imbalance, per-PDU and per-UPS load, per-CDU flow and heat load) for in-scope infrastructure, shall monitor balance continuously or at the profile interval, and shall coordinate with the platform owner on workload controls (scheduler placement, power capping) so that facility limits are respected. Imbalance or exceedance shall be corrected through change control. | 1) Placement rules and balance limits are defined. 2) Monitoring shows balance within limits or exceedances corrected. 3) Workload controls (power capping, placement constraints) are configured to respect facility limits where used. 4) Corrections were made through change control. | Maximum phase imbalance [%] default Site-specific (no default) (Set from UPS and transformer OEM limits.) | Placement rules.; Balance monitoring data.; Scheduler or power-cap configuration.; Correction change records. | ANALYSIS; RECONCILIATION; INSPECTION | 1) Obtain rules. 2) Extract balance data. 3) Inspect workload control configuration. 4) Review corrections. | PREVENTIVE | OPERATION | AL4 | OPERATE; CHANGE | NORMAL; MAINTENANCE; DEGRADED | Applies to in-scope power and cooling distribution. |  | CG-05; CG-06; CG-09 | Phase imbalance overloads UPS; Single PDU overloaded on failover; Stranded capacity on one CDU loop | CapacityAssertion; Resource; FaultDomain | Data extraction is read-only; no load shall be moved or capped to test balance limits. | No balance data is US3. | EN 50600-2-2 (power distribution); ASHRAE TC 9.9 liquid cooling guidance | MCF-OPS-021; MCF-CMP-010; MCF-DEP-019; MCF-POW-015 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-OPS-024 | OPS | Building Operations and Service Management | OPS-06 | Capacity and service operations | Operational Reporting | Accountable owners receive accurate, traceable periodic reports on operational risk and performance (incidents and near misses, Service Outcome performance, capacity headroom, deferred maintenance, temporary configurations, open findings and actions, staffing shortfalls, supplier performance) on which they can make decisions. | The operations manager shall issue operational reports to accountable owners at the profile interval containing the listed indicators with data sources and lineage, trends and exceptions, and shall record decisions or actions arising. | 1) Reports were issued at the interval with the listed content. 2) Figures trace to source systems. 3) Exceptions are highlighted with recommendations. 4) Decisions arising are recorded. | Operational reporting interval [months] default 1 (Illustrative.) | Operational reports.; Source data for sampled figures.; Decision records. | DOCUMENT_REVIEW; RECONCILIATION; SAMPLING | 1) Obtain reports. 2) Trace sampled figures to sources. 3) Review decisions arising. | DIRECTIVE | OPERATION | AL4 | OPERATE | NORMAL | Applies to the operations function reporting to accountable owners named under GOV-02. |  | CG-13 | Accountable owner unaware of deferred maintenance backlog; Report figures inconsistent with source | AssuranceReport; EvidenceObject; Action | Records review only. | Reports whose figures cannot be traced to source systems are US2 (confidence ceiling CONF-2 on dependent OPERATION claims) unless a decision condition relies on the reported figures, in which case US3. | ISO/IEC 20000-1 (service management system requirements); EN 50600-3-1 (management and operational information) | MCF-OPS-012; MCF-OPS-022; MCF-GOV-003; MCF-DEP-022 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-RES-001 | RES | Resilience, Continuity and Recovery | RES-01 | Resilience strategy | Minimum Service Outcome | Ensure every in-scope Capability Instance has a defined minimum service outcome and impact tolerance (maximum tolerable disruption, minimum capacity, maximum lost work, maximum data loss) that resilience design, testing and recovery claims can be measured against. | The capability owner shall define and approve, for each in-scope Capability Instance, the minimum service outcome to be sustained under DEGRADED and EMERGENCY states and the impact tolerance, expressed as maximum tolerable duration of disruption, minimum retained capacity (for example accelerator-hours or tokens per second), maximum tolerable lost training progress, recovery time and recovery point objectives, and the business-impact basis for each. The resilience owner shall ensure every RES-02 to RES-05 control and every NET, POW, THM, CMP and STO recovery claim references these tolerances. | 1) Each in-scope Capability Instance has an approved minimum service outcome and impact tolerance with measurable units. 2) Tolerances are derived from a business-impact analysis that considers customers, contractual commitments and dependent services. 3) RTO and RPO (or maximum lost work) are stated and consistent with each other and with checkpoint strategy (RES-016). 4) Minimum outcomes are stated per declared operating state (NORMAL, DEGRADED, EMERGENCY, RECOVERY). 5) Resilience and recovery controls reference the tolerances explicitly. | Maximum tolerable disruption (training outcome) [h] default Business-impact derived (illustrative 24) (ISO/TS 22317-style impact analysis; capability-specific.) Maximum tolerable disruption (inference outcome) [min] default Business-impact derived (illustrative 15) (Capability-specific.) Maximum lost training progress [h of cluster time] default Equal to checkpoint interval plus restart time (illustrative 2) (Links to RES-016.) Minimum retained capacity in DEGRADED state [% of nominal] default 50 (illustrative) (Capability-profile parameter.) | Approved minimum service outcome and impact tolerance statement per Capability Instance; Business-impact analysis; Mapping of tolerances to resilience and recovery controls | DOCUMENT_REVIEW; INQUIRY; ANALYSIS | 1) Obtain the tolerance statement for each Capability Instance and confirm approval. 2) Review the business-impact analysis and trace each tolerance to it. 3) Check internal consistency of RTO, RPO, lost-work and checkpoint strategy. 4) Confirm state-specific minimum outcomes are defined. 5) Sample resilience and recovery controls to confirm they reference tolerances. | DIRECTIVE | DESIGN | AL2 | PLAN; DESIGN; CHANGE | NORMAL; DEGRADED; EMERGENCY; RECOVERY | Applies to every in-scope Capability Instance. Service Outcomes themselves are defined under CAP-02; this control defines the resilience minimum and tolerance. |  | CG-01; CG-10; CG-09 | Recovery tested against no defined objective; RPO inconsistent with checkpoint interval; Tolerances set without business basis; DEGRADED state with no defined minimum | ServiceOutcome; CapabilityInstance; OperatingState; CapacityAssertion | Document-based; no operational testing. | Where any in-scope Capability Instance lacks an approved tolerance, record a US5 UNKNOWN and do not assess recovery or containment controls as CONFORMING against an assumed tolerance. | ISO 22301 (Business continuity management systems: requirements); ISO/TS 22317 (Business impact analysis guidelines); UK PRA/FCA operational resilience policy (important business services and impact tolerances); Regulation (EU) 2022/2554 (Digital Operational Resilience Act) | MCF-CAP-008; MCF-CAP-010; MCF-RES-002; MCF-RES-016; MCF-RES-012 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-RES-002 | RES | Resilience, Continuity and Recovery | RES-01 | Resilience strategy | Graceful Degradation | Ensure that partial loss of power, cooling, compute, storage or network capacity results in planned, controlled reduction of AI service (load shedding, job preemption, throttling, reduced replicas) rather than uncontrolled failure. | The resilience owner shall define graceful-degradation modes for each Capability Instance, stating the trigger condition (for example loss of one cooling string, utility loss on UPS autonomy, loss of a fabric plane), the action (power capping, job preemption by priority, checkpoint-and-drain, inference replica reduction, admission control), the owner of the decision and the expected residual capacity. The platform operations lead shall implement the actions as tested automation or procedures and shall demonstrate by test or analysed event that each mode achieves the expected residual capacity within the time available before the triggering constraint is exceeded. | 1) Degradation modes are defined per Capability Instance with trigger, action, decision owner and residual capacity. 2) Each mode's time-to-act is shorter than the time available (for example UPS autonomy or thermal ride-through). 3) Actions are implemented as tested automation or procedures, with job-priority classes defined in the scheduler. 4) Tests or events in the period demonstrated achieved residual capacity and time-to-act. 5) Power capping or throttling actions are verified not to create unsafe electrical or thermal transients. | Time to shed load to residual target [min] default Less than UPS autonomy minus margin (illustrative 5) (Derived from POW and THM ride-through.) Accelerator power-cap floor [% of TDP] default Vendor-supported range (illustrative 60) (Capability-profile parameter; vendor limits apply.) | Degradation mode catalogue; Scheduler priority and preemption configuration; Power-capping and checkpoint-and-drain automation; Test or event records with measured residual capacity and timings | DOCUMENT_REVIEW; TEST; SCENARIO_EXERCISE; ANALYSIS | 1) Review the degradation catalogue against declared failure scenarios. 2) Compare time-to-act with available ride-through from POW/THM evidence. 3) Review scheduler and power-capping configuration. 4) Review or witness a degradation test and measure residual capacity. 5) Check for adverse transients created by the action. | CORRECTIVE | EFFECTIVENESS | AL5 | DESIGN; COMMISSION; OPERATE; CHANGE | DEGRADED; EMERGENCY; TRANSITION | Applies to every Capability Instance whose infrastructure can lose partial capacity. Not applicable where the declared outcome is all-or-nothing and that is explicitly accepted. |  | CG-09; CG-10 | Load not shed before UPS exhaustion; All jobs killed instead of priority preemption; Power cap causing simultaneous load step; Thermal ride-through exceeded | Safeguard; OperatingState; CapacityAssertion; TestRecord | Degradation tests that cap power or preempt jobs affect workloads and require capability owner authorisation; tests that remove power or cooling capacity require facility authorisation under OPS-007 and engineering safety review. | If time-to-act has not been measured, treat the mode as unavailable (U1) for scenarios where available time is shorter than the estimated time-to-act. | ISO 22316 (Organizational resilience: principles and attributes); ISO/IEC 27031 (ICT readiness for business continuity); AIDCF-004 (Threat, Hazard and Failure Model) | MCF-RES-001; MCF-CMP-010; MCF-POW-011; MCF-THM-003; MCF-POW-020 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-RES-003 | RES | Resilience, Continuity and Recovery | RES-01 | Resilience strategy | Resilience Scenarios | Ensure a maintained library of credible single, compound and common-mode scenarios is used to design and test resilience, including the AIDCF-004 cross-domain scenarios relevant to the site. | The resilience owner shall maintain a scenario library for each site and Capability Instance that includes, at minimum, the applicable AIDCF-004 cross-domain scenarios (X01 to X20), site-specific hazards, and maintenance-induced and recovery-induced scenarios; each scenario shall have an initiating event, initial operating state, propagation path, safeguards, residual capability and recovery path. The resilience owner shall prioritise scenarios using the AIDCF-004 prioritisation criteria and shall review the library annually and after major incidents. | 1) A scenario library exists with the minimum record fields from AIDCF-004. 2) Applicable cross-domain scenarios X01–X20 are included or excluded with rationale. 3) Maintenance-induced, recovery-induced and compound scenarios are represented. 4) Scenarios are prioritised and linked to tests (RES-017/RES-018) and exercises (RES-019). 5) The library was reviewed in the last 12 months and after major incidents. |  | Scenario library; Applicability rationale for X01–X20; Prioritisation record; Review records | DOCUMENT_REVIEW; ANALYSIS; INQUIRY | 1) Review library completeness against AIDCF-004 fields. 2) Check applicability rationale for each X-scenario. 3) Confirm maintenance- and recovery-induced scenarios exist. 4) Trace prioritised scenarios to tests and exercises. 5) Confirm review history. | DIRECTIVE | DESIGN | AL2 | PLAN; DESIGN; OPERATE; CHANGE | NORMAL; DEGRADED; MAINTENANCE; EMERGENCY; RECOVERY; TRANSITION | Applies to every in-scope site and Capability Instance; scenario libraries may be shared across sites of identical design if site-specific hazards are added. |  | CG-09; CG-10; CG-03 | Compound scenario never considered; Recovery-induced failure not anticipated; Library not updated after incident | FailureScenario; Threat; Hazard; FaultDomain | Scenario development is analytical. Where scenario parameters are validated against live telemetry, collection shall be read-only. | Scenarios whose propagation path crosses an unanalysed dependency are recorded with U10 and flagged for DEP analysis. | AIDCF-004 (Threat, Hazard and Failure Model); IEC 31010 (Risk management: risk assessment techniques); IEC 60812 (Failure modes and effects analysis); IEC 61025 (Fault tree analysis) | MCF-RES-018; MCF-RES-019; MCF-DEP-002; MCF-RES-007 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-RES-004 | RES | Resilience, Continuity and Recovery | RES-01 | Resilience strategy | Resilience Ownership | Ensure resilience of each Capability Instance has a single accountable owner with authority across facility, IT and provider boundaries and that resilience responsibilities are explicit for every contributing domain. | The executive sponsor shall appoint an accountable resilience owner for each site or Capability Instance with authority to set resilience requirements, approve accepted limitations and direct cross-domain testing. The resilience owner shall maintain a resilience responsibility matrix naming the responsible owner for power, cooling, network, compute, storage, control-plane and provider elements of each resilience and recovery capability, including colocation and cloud provider responsibilities. | 1) An accountable resilience owner is appointed in writing with defined authority. 2) A resilience responsibility matrix covers all contributing domains and providers. 3) Provider responsibilities are reflected in contracts or service descriptions. 4) Accepted resilience limitations are approved by the resilience owner or higher authority. 5) Owners named in the matrix confirm awareness (sampled). |  | Appointment record; Resilience responsibility matrix; Provider contract or service description extracts; Accepted limitation register | DOCUMENT_REVIEW; INQUIRY | 1) Review appointment and authority. 2) Review matrix coverage against domains and providers. 3) Check provider contract alignment. 4) Interview a sample of owners. | DIRECTIVE | DESIGN | AL2 | PLAN; OPERATE; CHANGE | NORMAL; EMERGENCY; RECOVERY | Applies to all in-scope sites and Capability Instances. |  | CG-13 | Colocation responsibility gap (X14); No one owns cross-domain recovery; Limitations accepted by unauthorised staff | CapabilityInstance; Dependency; Control | Not applicable (governance control). | Any recovery-critical element with no named owner is recorded as a US4 UNKNOWN for CG-13. | ISO 22301 (Business continuity management systems: requirements); ISO 22316 (Organizational resilience: principles and attributes) | MCF-GOV-006; MCF-GOV-005; MCF-DEP-018; MCF-RES-021 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-RES-005 | RES | Resilience, Continuity and Recovery | RES-02 | Fault-domain and containment design | Fault-Domain Definition | Ensure the site-level fault-domain model (power, cooling, fire, water, network, compute, storage and control-plane domains) is defined and reconciled to the as-built infrastructure, so that redundancy and independence claims are traceable. | The resilience owner shall maintain a site fault-domain model that defines each fault domain (for example electrical distribution paths, UPS systems, cooling strings and CDU groups, fire compartments, water zones, network planes, compute pods, storage failure domains, control-plane clusters) with its members, and records which domains overlap. The resilience owner shall reconcile the model to as-built evidence (single-line diagrams, P&IDs, rack power and cooling mapping, fabric topology, scheduler and storage placement) at commissioning and after material change, and shall flag every redundancy claim whose members share a fault domain. | 1) A fault-domain model exists covering all infrastructure classes. 2) Domain membership is reconciled to as-built evidence for each class. 3) Overlaps between domains (for example a network plane inside a single power path) are recorded. 4) Every redundancy claim is checked for members sharing a fault domain, and such cases are dispositioned. 5) The model was updated after each material change in the period. | Fault-domain model reconciliation age [days] default 180 (illustrative) (Capability-profile parameter.) | Fault-domain model; As-built references used in reconciliation (SLD, P&ID, rack maps, topology, placement); Overlap and shared-domain register; Change-linked updates | DOCUMENT_REVIEW; RECONCILIATION; ANALYSIS; INSPECTION | 1) Review model coverage across infrastructure classes. 2) Reconcile a sample of domains to primary as-built sources. 3) Examine overlaps and shared-domain register. 4) Test a sample of redundancy claims for shared membership. 5) Confirm update after recent changes. | PREVENTIVE | IMPLEMENTATION | AL3 | DESIGN; BUILD; COMMISSION; CHANGE | NORMAL; MAINTENANCE; DEGRADED | Applies to every in-scope site. Domain-specific fault-domain controls (NET-004, CMP-008) feed this model. | CG-09 | CG-03; CG-02 | Redundant spines on one UPS path; Dual-fed racks on PDUs from one switchboard; Storage replicas in one fire compartment; Control-plane quorum in one rack | FaultDomain; Dependency; ArchitectureSnapshot; InfrastructureSystem | Reconciliation is non-intrusive; physical verification of power feeds shall use visual inspection or EPMS data only, never live disconnection. | Domain membership that cannot be reconciled is recorded as U1 or U3 and the affected redundancy claims are treated as unproven. | IEC 31010 (Risk management: risk assessment techniques); ANSI/TIA-942 (Telecommunications infrastructure standard for data centres); EN 50600 series / ISO/IEC 22237 series (Data centre facilities and infrastructures); AIDCF-013 (AI Data Centre Assurance Reference Architecture) | MCF-NET-004; MCF-CMP-008; MCF-DEP-005; MCF-RES-007; MCF-RES-006 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-RES-006 | RES | Resilience, Continuity and Recovery | RES-02 | Fault-domain and containment design | Containment Boundaries | Ensure physical, electrical, thermal, network and logical boundaries that are intended to stop propagation are implemented as designed, with their isolating devices identified and maintained. | The resilience owner shall identify each containment boundary relied upon (for example fire compartment, electrical protection discrimination point, cooling-loop isolation valves, fabric partition, security zone, scheduler placement constraint, storage failure domain) together with the isolating device or mechanism and its required response. The domain owners shall confirm that each mechanism is installed, configured and maintained as designed and shall record mechanisms in bypass or override as temporary configurations under OPS-019. | 1) A containment-boundary register lists boundaries, isolating mechanisms and intended response. 2) Mechanisms are installed and configured as designed (sampled inspection or configuration extract). 3) Maintenance status of isolating devices is current. 4) Mechanisms in bypass or override are recorded as temporary configurations with expiry. 5) Scheduler and storage placement constraints that enforce logical containment are configured and verified. |  | Containment-boundary register; Inspection or configuration evidence per mechanism; Maintenance records; Temporary configuration register | DOCUMENT_REVIEW; INSPECTION; RECONCILIATION; SAMPLING | 1) Review the register for completeness against the scenario library. 2) Sample mechanisms and verify installation and configuration. 3) Check maintenance records. 4) Review bypass/override records. 5) Verify logical placement constraints in scheduler and storage. | PREVENTIVE | IMPLEMENTATION | AL3 | DESIGN; BUILD; COMMISSION; OPERATE | NORMAL; MAINTENANCE; DEGRADED | Applies to every containment boundary relied upon in fault-domain or blast-radius claims. |  | CG-09 | Isolation valve seized; Breaker discrimination lost after setting change; Fire damper not closing; Placement constraint removed from scheduler | Safeguard; FaultDomain; AssetInstance | Operating isolating devices is not part of this control; functional tests belong to RES-008 and require authorisation. | Boundaries whose mechanism status is unknown are treated as absent in blast-radius analysis. | IEC 31010 (Risk management: risk assessment techniques); EN 50600 series / ISO/IEC 22237 series (Data centre facilities and infrastructures) | MCF-RES-005; MCF-RES-008; MCF-OPS-019; MCF-NET-012; MCF-THM-020 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-RES-007 | RES | Resilience, Continuity and Recovery | RES-02 | Fault-domain and containment design | Blast Radius | Ensure the maximum consequence of each credible failure is quantified in capability terms (accelerators, jobs, tenants, inference capacity, data) and compared with the impact tolerance. | The resilience owner shall perform and maintain a blast-radius analysis for each prioritised scenario and each fault domain, stating the affected assets, the affected Capability Instances, the capability consequence in outcome units and comparison with impact tolerance, including common-cause and common-mode failures (for example firmware rollout, shared controller, shared identity provider). The resilience owner shall record every blast radius exceeding tolerance as a Finding with a treatment plan or approved limitation. | 1) Blast-radius analysis covers every prioritised scenario and fault domain. 2) Consequences are stated in outcome units and compared with impact tolerance. 3) Common-cause and common-mode cases (software, firmware, configuration, identity, automation) are included. 4) Analysis is reconciled to the current fault-domain model (RES-005). 5) Exceedances have treatment plans or approved limitations. | Maximum blast radius per single credible failure [% of Capability Instance capacity] default Impact-tolerance derived (illustrative 25) (Capability-profile parameter.) | Blast-radius analysis; Reconciliation to fault-domain model; Exceedance register and treatment plans | ANALYSIS; DOCUMENT_REVIEW; RECONCILIATION | 1) Review coverage against scenarios and domains. 2) Recompute blast radius for a sample of scenarios from the fault-domain model. 3) Check common-mode inclusion. 4) Compare with tolerances and review exceedances. | PREVENTIVE | IMPLEMENTATION | AL3 | DESIGN; OPERATE; CHANGE | NORMAL; DEGRADED; MAINTENANCE; FAILED | Applies to all in-scope Capability Instances, including multi-tenant platforms where blast radius is expressed per tenant. | CG-09 | CG-03 | Firmware update bricking all nodes; Shared identity provider outage blocking all operations; Single cooling loop serving whole cluster; Concentration of tenant capacity in one hall | FailureScenario; FaultDomain; CapacityAssertion; Finding | Analytical. | If a scenario's blast radius depends on an unresolved dependency, record U10 and use the worst credible case. | IEC 31010 (Risk management: risk assessment techniques); IEC 60812 (Failure modes and effects analysis); IEC 61025 (Fault tree analysis); AIDCF-004 (Threat, Hazard and Failure Model) | MCF-RES-005; MCF-RES-003; MCF-NET-004; MCF-DEP-013 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-RES-008 | RES | Resilience, Continuity and Recovery | RES-02 | Fault-domain and containment design | Isolation Validation | Ensure containment boundaries actually stop propagation when demanded, verified by representative tests, analysed incidents or safe simulations. | The resilience owner shall maintain an isolation validation plan that assigns a validation method from the AIDCF-004 safe validation hierarchy (V0–V7) to each containment boundary, with the highest safe level for gate-critical boundaries, and shall execute the plan over a defined cycle. The domain owners shall record results, including failed or partial isolation, and shall retest after remediation. | 1) Each boundary has an assigned validation method and level. 2) Gate-critical boundaries are validated at V5 (component functional test) or above, or the shortfall is justified and recorded. 3) Validation in the cycle demonstrated isolation within the expected response. 4) Failed or partial isolation results led to remediation and retest. 5) Network and logical isolation (fabric partitions, security zones, scheduler placement) are included alongside physical boundaries. | Isolation validation cycle [months] default 24 (illustrative) (Capability-profile parameter.) | Isolation validation plan; Test, incident or simulation records; Remediation and retest records | TEST; SCENARIO_EXERCISE; ANALYSIS; DOCUMENT_REVIEW | 1) Review the plan and assigned levels. 2) Sample gate-critical boundaries and review results. 3) Check failed/partial results for remediation and retest. 4) Confirm logical boundaries are included. | DETECTIVE | RESILIENCE | AL5 | COMMISSION; OPERATE; CHANGE | NORMAL; DEGRADED; MAINTENANCE; FAILED; EMERGENCY | Applies to all containment boundaries in the RES-006 register. | CG-09 | CG-04 | Boundary passes design review but fails on demand; Fire damper fails to close; Fabric partition leaks traffic; Protection fails to discriminate | TestRecord; Safeguard; FaultDomain | Isolation tests involving electrical protection, fire systems, fluid isolation or production fabrics are hazardous or disruptive; they require written authorisation from the facility owner and the relevant engineering authority, permit-to-work, method statements, and a safety and rollback plan. Tests at V6/V7 require additional executive authorisation. | Boundaries validated only at V0–V2 are recorded with U8 for effectiveness claims. | AIDCF-004 (Threat, Hazard and Failure Model); IEC 31010 (Risk management: risk assessment techniques); EN 50600 series / ISO/IEC 22237 series (Data centre facilities and infrastructures) | MCF-RES-006; MCF-RES-017; MCF-RES-018; MCF-NET-012; MCF-SEC-019 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-RES-009 | RES | Resilience, Continuity and Recovery | RES-03 | Continuity planning | Continuity Strategy | Ensure an approved continuity strategy states how each Capability Instance's minimum outcome will be sustained or resumed across site loss, provider loss and major infrastructure loss. | The resilience owner shall maintain an approved continuity strategy for each Capability Instance that selects and justifies the continuity approach (for example in-site redundancy, active-active multi-site inference, warm standby training capacity, checkpoint replication to an alternate site, contracted cloud burst, or accepted suspension), states the dependencies of the chosen approach, and is consistent with the impact tolerances in RES-001. | 1) An approved strategy exists per Capability Instance with the selected approach and justification. 2) The strategy meets or explicitly accepts shortfall against impact tolerances. 3) Dependencies of the strategy (alternate site, provider, data replication, staff) are listed. 4) The strategy addresses site loss, major provider loss and loss of the AI control plane. |  | Continuity strategy; Tolerance comparison; Strategy dependency list | DOCUMENT_REVIEW; ANALYSIS; INQUIRY | 1) Review strategy and approval. 2) Compare with tolerances. 3) Review dependencies and coverage of site, provider and control-plane loss. | DIRECTIVE | DESIGN | AL2 | PLAN; DESIGN; CHANGE | EMERGENCY; FAILED; RECOVERY | Applies to all in-scope Capability Instances, including those whose approved strategy is accepted suspension (the acceptance itself is assessed). |  | CG-10; CG-01 | No plan for site loss; Strategy relies on unavailable alternate capacity; Control-plane loss not considered | CapabilityInstance; Dependency; Safeguard | Strategy review is analytical; feasibility of the selected approach is tested under RES-010 and RES-018 with their own authorisation requirements. | Strategies that rely on an unverified dependency are recorded with U10. | ISO 22301 (Business continuity management systems: requirements); ISO 22313 (Business continuity management systems: guidance); ISO/IEC 27031 (ICT readiness for business continuity); NIST SP 800-34 Rev. 1 (Contingency planning guide for federal information systems) | MCF-RES-001; MCF-RES-010; MCF-RES-011; MCF-DEP-016 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-RES-010 | RES | Resilience, Continuity and Recovery | RES-03 | Continuity planning | Alternative Capacity | Ensure alternate compute, storage and network capacity relied upon by the continuity strategy exists, is compatible and can be brought into service within tolerance. | The capability owner shall identify the alternate capacity relied upon (alternate cluster, partitioned reserve, alternate site, cloud contract) with its size, compatibility (accelerator generation, software stack, fabric, storage access) and activation time, and shall secure it by reservation or contract. The platform operations lead shall demonstrate by test at a defined interval that a representative workload can be relocated to alternate capacity and resumed from checkpoint or served within the activation time. | 1) Alternate capacity is identified with size, compatibility and activation time. 2) Capacity is reserved or contracted, with terms that hold during regional demand surges. 3) Software stack, images and data access on alternate capacity are kept compatible. 4) A relocation test in the interval demonstrated resumption within activation time. 5) Data transfer or replication capacity for relocation is sufficient (checkpoint size over link capacity). | Alternate capacity activation time [h] default Within maximum tolerable disruption (illustrative 8) (Derived from RES-001.) Relocation test interval [months] default 12 (illustrative) (Capability-profile parameter.) | Alternate capacity register; Reservation or contract terms; Compatibility matrix; Relocation test records | DOCUMENT_REVIEW; TEST; ANALYSIS | 1) Review register and contract terms. 2) Check compatibility of stack, images and data access. 3) Review or witness a relocation test. 4) Recompute data transfer time for relocation. | RECOVERY | EFFECTIVENESS | AL5 | PLAN; OPERATE; CHANGE | EMERGENCY; RECOVERY; FAILED | Applies where the continuity strategy relies on alternate capacity. Not applicable where accepted suspension is the approved strategy. |  | CG-10; CG-03 | Alternate cloud capacity unavailable during regional surge; Incompatible accelerator generation; Checkpoint transfer exceeds tolerance; Images outdated on standby cluster | Resource; CapacityAssertion; Dependency; TestRecord | Relocation tests consume alternate capacity and may incur cost; production workloads shall not be moved without capability owner authorisation. | Alternate capacity with no test is recorded as U1 for activation-time claims. | ISO 22301 (Business continuity management systems: requirements); ISO/IEC 27031 (ICT readiness for business continuity); Regulation (EU) 2022/2554 (Digital Operational Resilience Act) | MCF-RES-009; MCF-DEP-012; MCF-DEP-016; MCF-STO-014 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-RES-011 | RES | Resilience, Continuity and Recovery | RES-03 | Continuity planning | Site and Provider Continuity | Ensure the continuity arrangements of sites, colocation operators, utilities, carriers and critical service providers are known, evidenced and compatible with the Capability Instance's tolerances. | The resilience owner shall obtain, for each site operator and critical provider (colocation, utility, carrier, cloud, OEM support), evidence of their continuity arrangements relevant to the outcome (for example operator emergency response, fuel contracts, carrier restoration commitments, provider recovery objectives), and shall reconcile provider objectives with the Capability Instance's tolerances. The resilience owner shall record every mismatch as a dependency limitation. | 1) Each critical site operator and provider has continuity evidence on file. 2) Provider recovery objectives are compared with tolerances. 3) Mismatches are recorded as limitations or treated. 4) Evidence rights and incident notification are contractually defined (SUP-006, SUP-007). 5) Provider evidence is current within the evidence-age parameter. | Provider continuity evidence age [months] default 12 (illustrative) (Capability-profile parameter.) | Provider continuity evidence; Tolerance reconciliation; Limitation register | DOCUMENT_REVIEW; INQUIRY; ANALYSIS | 1) List critical providers. 2) Review continuity evidence and currency. 3) Reconcile objectives with tolerances. 4) Review limitations and contractual rights. | PREVENTIVE | IMPLEMENTATION | AL3 | PLAN; OPERATE; CHANGE | EMERGENCY; FAILED; RECOVERY | Applies to all critical providers and site operators. |  | CG-03; CG-10 | Carrier restoration time beyond tolerance; Colocation fuel contract shared with neighbours; OEM support unavailable in crisis (X18) | Dependency; Interface; Resource | Provider evidence is reviewed as documents; any joint failover exercise with a provider requires a jointly approved test plan and provider authorisation. | Providers refusing evidence are recorded with U2 and treated as single points of failure in strategy analysis. | ISO 22301 (Business continuity management systems: requirements); Regulation (EU) 2022/2554 (Digital Operational Resilience Act); ISO/IEC 27031 (ICT readiness for business continuity) | MCF-DEP-009; MCF-DEP-010; MCF-DEP-011; MCF-SUP-006; MCF-NET-002 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-RES-012 | RES | Resilience, Continuity and Recovery | RES-03 | Continuity planning | Crisis Priorities | Ensure pre-agreed restoration and allocation priorities exist for when capacity is scarce, so that crisis decisions on which workloads, tenants and services are protected or restored first are not improvised. | The capability owner shall approve a priority scheme stating, for scarce power, cooling, compute and network capacity during DEGRADED, EMERGENCY and RECOVERY states, which workloads, tenants and services are protected, preempted and restored first, consistent with contractual commitments and life-safety precedence. The platform operations lead shall implement the scheme in scheduler priority classes and runbooks. | 1) An approved priority scheme exists covering protection, preemption and restoration order. 2) The scheme is consistent with contractual commitments and life-safety precedence. 3) Scheduler priority classes and runbooks implement the scheme. 4) Crisis command (RES-021) uses the scheme in exercises. |  | Priority scheme; Scheduler configuration; Runbook extracts; Exercise records using the scheme | DOCUMENT_REVIEW; INQUIRY; RECONCILIATION | 1) Review scheme and approval. 2) Check consistency with commitments. 3) Reconcile to scheduler configuration. 4) Review exercise use. | DIRECTIVE | DESIGN | AL2 | PLAN; DESIGN; OPERATE | DEGRADED; EMERGENCY; RECOVERY | Applies to all shared or multi-workload Capability Instances. |  | CG-10; CG-01 | Low-priority jobs restored before critical inference; Contractual breach during shedding; Improvised priorities under pressure | ServiceOutcome; OperatingState; Control | Priority review is document-based; testing preemption against live workloads is governed by RES-002 and requires capability owner authorisation. | If the scheme is not reflected in scheduler configuration, record a Finding; claims of priority-based shedding are limited to DESIGN. | ISO 22301 (Business continuity management systems: requirements); ISO 22320 (Emergency management: guidelines for incident management) | MCF-RES-001; MCF-RES-002; MCF-RES-021; MCF-GOV-021 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-RES-013 | RES | Resilience, Continuity and Recovery | RES-04 | Recovery planning | Recovery Dependencies | Ensure every prerequisite for recovering each Capability Instance (power, cooling, network, time, identity, DNS, storage metadata, controllers, images, licences, people and providers) is identified, including circular and cold-start dependencies. | The recovery manager shall maintain a recovery dependency map for each Capability Instance, derived from DEP-004, listing every prerequisite system, service, credential, artefact, person and provider required to restore the outcome from a cold or failed state, and shall identify circular dependencies (for example identity provider hosted on the cluster it unlocks, DNS required to reach the time source, BMC firmware repository on the failed storage) and the means by which each is broken. The recovery manager shall verify the map against the last integrated recovery test. | 1) A recovery dependency map exists per Capability Instance covering infrastructure, services, credentials, artefacts, people and providers. 2) Circular and cold-start dependencies are identified with a documented break (for example offline copy, local fallback, out-of-band path). 3) Each dependency has an owner and a recovery path. 4) The map was verified against the most recent integrated recovery test and updated with discovered dependencies. 5) Offline artefacts (images, configuration backups, credentials) are stored outside the failure domain they recover. |  | Recovery dependency map; Circular-dependency analysis and breaks; Integrated test discrepancy log; Offline artefact inventory and location | DOCUMENT_REVIEW; ANALYSIS; RECONCILIATION; INQUIRY | 1) Review the recovery dependency map for completeness against DEP-004. 2) Run or review cycle detection for circular dependencies. 3) Verify breaks for each cycle (offline copies, local auth, OOB). 4) Check offline artefact locations against fault domains. 5) Compare the map with the last integrated test discrepancies. | RECOVERY | IMPLEMENTATION | AL3 | DESIGN; OPERATE; CHANGE | FAILED; RECOVERY; SHUTDOWN; EMERGENCY | Applies to every in-scope Capability Instance. | CG-10 | CG-03 | Identity provider on the failed cluster (X19); Images only on failed storage; Licence server unreachable; Key personnel unavailable | Dependency; RequiredFunction; FaultDomain; Resource | Analytical; verification draws on RES-018 tests. | Any recovery prerequisite whose location or availability in a failure state is unknown is recorded as U10 at US4 against CG-10. | ISO/IEC 27031 (ICT readiness for business continuity); NIST SP 800-34 Rev. 1 (Contingency planning guide for federal information systems); AIDCF-004 (Threat, Hazard and Failure Model) | MCF-DEP-004; MCF-RES-014; MCF-NET-015; MCF-NET-024; MCF-SEC-004 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-RES-014 | RES | Resilience, Continuity and Recovery | RES-04 | Recovery planning | Recovery Sequencing | Ensure a tested, ordered restoration sequence exists from total or partial loss through power, cooling, network, storage, compute and control plane to validated service, with hold points and safety checks between stages. | The recovery manager shall maintain a black-start and restoration sequence for each site and Capability Instance that orders restoration through power (utility or generation, distribution, UPS), cooling (heat rejection, facility water, CDUs and liquid loops before IT load), out-of-band and core network, time and identity services, storage (metadata and quorum before data services), compute (BMC, firmware validation, health checks, burn-in) and AI control plane (cluster manager, scheduler), with entry criteria, hold points, load-step limits and safety checks at each stage. The recovery manager shall demonstrate the sequence by integrated test or exercise at a defined interval and shall record achieved stage durations against the recovery time objective. | 1) A restoration sequence exists covering power, cooling, network, storage, compute and control plane with entry criteria and hold points. 2) Cooling capacity is confirmed before IT load is restored at each step, and load-step limits respect generator and UPS capability. 3) The sequence references POW-024, THM-024, STO-019, CMP-023 and NET restoration runbooks consistently. 4) An integrated test or exercise in the interval executed the sequence (fully or in representative segments) and recorded stage durations. 5) Total achieved duration is within the recovery time objective, or the shortfall is a Finding. 6) Validation at the end of the sequence confirms Service Outcome restoration, not only system availability. | Target black-start-to-service time [h] default Within RTO (illustrative 12) (Derived from RES-001.) Maximum IT load step during restoration [% of generator rating] default Generator- and UPS-specific (illustrative 25) (From POW-020 load-step analysis.) Integrated restoration test interval [months] default 24 (illustrative) (Capability-profile parameter.) | Restoration sequence document; Cross-references to domain restoration runbooks; Integrated test or exercise records with stage timings; Validation records | DOCUMENT_REVIEW; SCENARIO_EXERCISE; TEST; ANALYSIS; OBSERVATION | 1) Review the sequence for order, entry criteria, hold points and safety checks. 2) Cross-check against domain restoration runbooks for consistency. 3) Check load-step and cooling-before-load constraints. 4) Review or observe an integrated test and extract stage durations. 5) Compare total duration with RTO. 6) Confirm service-outcome validation at completion. | RECOVERY | RESILIENCE | AL5 | DESIGN; COMMISSION; OPERATE; CHANGE | SHUTDOWN; FAILED; RECOVERY; TRANSITION; EMERGENCY | Applies to every in-scope site and Capability Instance. Single-system recovery runbooks remain under their domain controls. | CG-10 | CG-05; CG-06 | IT load restored before cooling, causing thermal trip; Simultaneous node power-on exceeding generator load-step; Control plane restored before identity and time; Storage data services started before metadata quorum | RequiredFunction; Action; OperatingState; TestRecord | Black-start tests involve hazardous energy and site-wide disruption and require written authorisation from the facility owner, the electrical and mechanical engineering authorities and the capability owner, permit-to-work, a safety case and a rollback plan. Segmented and simulation-based tests are preferred where full tests are not authorised. | Stages never executed in test are recorded with U5 and the sequence is assessed only to DESIGN for those stages. | ISO/IEC 27031 (ICT readiness for business continuity); NIST SP 800-34 Rev. 1 (Contingency planning guide for federal information systems); ISO 22301 (Business continuity management systems: requirements); AIDCF-013 (AI Data Centre Assurance Reference Architecture) | MCF-POW-024; MCF-THM-024; MCF-STO-019; MCF-CMP-023; MCF-NET-015 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-RES-015 | RES | Resilience, Continuity and Recovery | RES-04 | Recovery planning | Configuration Restoration | Ensure the configuration of infrastructure and control-plane systems can be restored from a known-good, integrity-verified baseline, avoiding reintroduction of corrupt or malicious configuration. | The recovery manager shall ensure that configuration backups of network devices, controllers, BMS/EPMS, CDU controllers, storage controllers, cluster managers and identity systems are taken at a defined interval, are integrity-protected (hashed or signed), are stored outside the failure and compromise domain they protect, and are tagged with the approved baseline they correspond to. The recovery manager shall test restoration of a sample of each system class at a defined interval, including verification that the restored configuration matches the approved baseline and not a compromised or drifted state. | 1) Backups exist for every system class with defined interval. 2) Backups are integrity-protected and stored outside the protected failure/compromise domain. 3) Backups are tagged to an approved baseline and integrity is verified before restore. 4) Restore tests per system class in the interval succeeded and were verified against baseline. 5) A procedure exists for selecting a pre-compromise baseline when compromise is suspected (X15). | Configuration backup interval [h] default 24 or on change (illustrative) (Capability-profile parameter.) Restore test interval per class [months] default 12 (illustrative) (Capability-profile parameter.) | Backup inventory and schedules; Integrity mechanism evidence; Storage location analysis; Restore test records; Pre-compromise baseline selection procedure | DOCUMENT_REVIEW; TEST; REPERFORMANCE; SAMPLING | 1) Review backup inventory coverage. 2) Verify integrity protection and storage location. 3) Review or reperform a restore and compare to baseline. 4) Review pre-compromise baseline procedure. | RECOVERY | EFFECTIVENESS | AL5 | OPERATE; CHANGE | RECOVERY; FAILED; MAINTENANCE | Applies to all configuration-bearing infrastructure and control-plane systems in scope. |  | CG-10; CG-07; CG-14 | Restoring compromised configuration (X15); Backups on the same failed storage; BMS controller backup never restored; Restored config drifted from baseline | ArchitectureSnapshot; Safeguard; TestRecord; EvidenceObject | Restores to OT controllers (BMS, EPMS, CDU, PLC) shall be performed only on test benches or spare controllers unless a maintenance window is authorised by the facility owner with plant in a safe state. | Systems with backups but no restore test are recorded as U1 for restore claims. | ISO/IEC 27031 (ICT readiness for business continuity); NIST SP 800-34 Rev. 1 (Contingency planning guide for federal information systems); ISA/IEC 62443-2-1 (Security programme requirements for IACS asset owners) | MCF-NET-022; MCF-SEC-024; MCF-OPS-020; MCF-STO-012; MCF-CMP-016 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-RES-016 | RES | Resilience, Continuity and Recovery | RES-04 | Recovery planning | Data and Checkpoint Recovery | Ensure training state (checkpoints, optimiser state, data-loader position), model artefacts and essential datasets can be recovered within the recovery point and time objectives and that restarted jobs resume correctly. | The capability owner shall set a checkpoint policy per training Capability Instance stating checkpoint interval (justified against failure rate, checkpoint cost and maximum lost work, for example using a Young/Daly-style optimisation), checkpoint retention, and the number and placement of durable copies outside the training cluster's failure domain. The platform operations lead shall verify checkpoint integrity at write and before restore, and shall test at a defined interval that a representative job can be restarted from checkpoint (including on a different set of nodes) and reaches equivalent training state within RTO and lost-work tolerance. | 1) Checkpoint interval, retention and copy placement are defined and justified against lost-work tolerance. 2) Durable copies are stored outside the training cluster's power, storage and compromise domain. 3) Checkpoint integrity is verified at write and before restore. 4) Restart tests in the interval achieved resumption within RTO and lost-work tolerance, including on alternate nodes. 5) Model artefacts and essential datasets have recovery copies meeting RPO. 6) Inference model artefacts can be redeployed within the inference RTO. | Checkpoint interval [min] default Optimised from failure rate and checkpoint cost (illustrative 60) (Young/Daly-style approximation; capability-specific.) Durable checkpoint copies outside cluster failure domain [count] default 1 (illustrative) (Capability-profile parameter.) Restart-from-checkpoint time [min] default Within RTO (illustrative 30) (Derived from RES-001.) | Checkpoint policy and justification; Copy placement evidence; Integrity verification logs; Restart test records; Artefact and dataset recovery-copy evidence | DOCUMENT_REVIEW; TEST; ANALYSIS; SAMPLING | 1) Review the checkpoint policy and interval justification. 2) Verify copy placement against fault domains. 3) Sample integrity logs. 4) Review or witness a restart test including alternate nodes. 5) Review artefact and dataset recovery copies. | RECOVERY | RESILIENCE | AL5 | DESIGN; OPERATE; CHANGE | NORMAL; FAILED; RECOVERY; DEGRADED | Applies to training and fine-tuning Capability Instances, and to inference for model artefact recovery. | CG-10 | CG-08 | Corrupt checkpoint discovered only at restore; All checkpoints on the failed storage; Restart fails on different topology; Lost-work exceeds tolerance due to long interval | Resource; RequiredFunction; TestRecord; Safeguard | Restart tests consume capacity and shall be scheduled with the capability owner; do not delete or overwrite production checkpoints during tests. | Checkpoints without integrity verification are recorded as U7 and do not support recovery claims. | ISO/IEC 27031 (ICT readiness for business continuity); NIST SP 800-34 Rev. 1 (Contingency planning guide for federal information systems) | MCF-STO-017; MCF-STO-018; MCF-STO-016; MCF-NET-009; MCF-RES-001 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-RES-017 | RES | Resilience, Continuity and Recovery | RES-05 | Testing and exercising | Component Tests | Ensure resilience-relevant components (generators, UPS, transfer switches, CDU pumps, valves, fabric failover, controller failover, storage failover) are functionally tested on a defined programme and results tracked. | The resilience owner shall maintain a component test programme listing each resilience-relevant component class, the test method, frequency and acceptance criteria, coordinated with domain maintenance programmes. Domain owners shall execute tests per programme, record results, and raise and close defects; the resilience owner shall review programme adherence quarterly. | 1) A component test programme exists with class, method, frequency and acceptance criteria. 2) Tests were executed per schedule in the period (adherence rate meets target). 3) Failed tests raised defects that were closed or have approved deferral. 4) Quarterly adherence reviews occurred. | Programme adherence target [% of scheduled tests completed on time] default 95 (illustrative) (Capability-profile parameter.) | Component test programme; Test records for the period; Defect records; Adherence reviews | SAMPLING; DOCUMENT_REVIEW; ANALYSIS | 1) Review programme coverage. 2) Sample components from asset registers and trace tests. 3) Review defects and closure. 4) Review adherence reviews. | DETECTIVE | OPERATION | AL4 | COMMISSION; OPERATE | NORMAL; MAINTENANCE | Applies to all resilience-relevant components across domains. |  | CG-10; CG-05; CG-06 | Latent failure of untested component (generator no-start); Test failures not remediated; Programme drift | TestRecord; AssetInstance; Action | Component tests involving hazardous energy require permit-to-work and authorised persons under OPS-007; disruptive IT failover tests require change approval. | Components with no test record in the period are recorded as U1 for operational claims. | NIST SP 800-84 (Guide to test, training and exercise programs for IT plans and capabilities); ISO 22301 (Business continuity management systems: requirements) | MCF-POW-006; MCF-THM-010; MCF-NET-021; MCF-OPS-009 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-RES-018 | RES | Resilience, Continuity and Recovery | RES-05 | Testing and exercising | Integrated Scenario Tests | Ensure prioritised cross-domain scenarios are exercised as integrated tests across power, cooling, network, compute, storage and control plane, demonstrating that the Capability Instance stays within or recovers within tolerance. | The resilience owner shall plan and execute integrated scenario tests for prioritised scenarios from RES-003 (for example utility loss with generator start and UPS transfer under AI load, cooling string loss at sustained load, fabric plane loss during checkpoint, control-plane loss), measuring capability-level outcomes (job survival, lost work, inference availability, restoration time) as well as system behaviour. The resilience owner shall define test objectives, safety case, abort criteria and success criteria tied to impact tolerances before each test and shall record results and defects. | 1) Integrated tests cover the highest-priority scenarios on a defined cycle. 2) Each test has objectives, safety case, abort criteria and success criteria tied to tolerances. 3) Tests measure capability-level outcomes, not only component behaviour. 4) Results demonstrated outcomes within tolerance, or Findings were raised. 5) Defects discovered are tracked to closure and retest (RES-020). 6) Tests are conducted at representative load or the load difference is analysed. | Integrated test cycle [months] default 24 (illustrative) (Capability-profile parameter.) Representative load during test [% of design IT load] default As high as safely authorised (illustrative 70) (Load banks or real workload; site-specific.) | Integrated test plans with safety cases; Test records with capability-level measurements; Defect and retest records; Load representativeness analysis | SCENARIO_EXERCISE; TEST; OBSERVATION; ANALYSIS | 1) Review test plans, safety cases and success criteria. 2) Observe or review test execution records. 3) Verify capability-level measurements. 4) Assess load representativeness. 5) Review defect closure and retest. | DETECTIVE | RESILIENCE | AL5 | COMMISSION; OPERATE; CHANGE | NORMAL; DEGRADED; EMERGENCY; FAILED; RECOVERY; TRANSITION | Applies to every in-scope Capability Instance with gate-critical outcomes. | CG-10 | CG-09; CG-05; CG-06 | Cross-domain interaction not revealed by component tests; Generator stable on load bank but unstable on AI load steps; Jobs fail on UPS transfer despite systems passing; Hidden shared dependency (X04) | TestRecord; FailureScenario; ServiceOutcome; Event | Integrated tests are disruptive and may be hazardous; they require written authorisation from the facility owner, engineering authorities and capability owner, a safety case, permit-to-work for energised work, a defined abort authority, and communication to affected tenants. Live capability exercises (AIDCF-004 V7) require executive authorisation. | Scenarios tested only at reduced load without representativeness analysis are recorded with U5. | NIST SP 800-84 (Guide to test, training and exercise programs for IT plans and capabilities); ISO 22301 (Business continuity management systems: requirements); AIDCF-004 (Threat, Hazard and Failure Model) | MCF-RES-003; MCF-RES-014; MCF-RES-020; MCF-POW-020; MCF-THM-003 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-RES-019 | RES | Resilience, Continuity and Recovery | RES-05 | Testing and exercising | Tabletop Exercises | Ensure decision-makers, operators and providers rehearse response to scenarios that cannot safely be tested live, including cyber-physical, compound and site-loss events. | The resilience owner shall run tabletop exercises on a defined cycle covering scenarios not testable live, including at least one cyber-physical scenario (for example BMS/EPMS compromise, X05) and one compound event (X20) per cycle, with participation of crisis command, facility, IT, security and key providers. The resilience owner shall record decisions, timings, gaps and actions and shall track actions to closure. | 1) Exercises occurred on the defined cycle with documented scenarios and objectives. 2) Each cycle includes a cyber-physical and a compound scenario. 3) Participants include crisis command, facility, IT, security and key providers. 4) Gaps and actions are recorded and tracked to closure. | Tabletop cycle [months] default 6 (illustrative) (Capability-profile parameter.) | Exercise plans and scenarios; Attendance records; Exercise reports with gaps and actions; Action tracker | DOCUMENT_REVIEW; OBSERVATION; INQUIRY | 1) Review exercise schedule and scenarios. 2) Check scenario mix and participation. 3) Review reports and action closure. 4) Interview participants. | DETECTIVE | OPERATION | AL4 | OPERATE | EMERGENCY; RECOVERY; FAILED | Applies to every in-scope site and Capability Instance; exercises may be combined across sites where crisis command is shared. |  | CG-10; CG-13 | Decision paralysis in cyber-physical event; Provider roles unclear; Actions from exercises never closed | TestRecord; FailureScenario; Action | Tabletop exercises are non-intrusive; do not issue live commands to systems during exercises. | Tabletop results support OPERATION claims for decision processes only, not technical recovery effectiveness. | NIST SP 800-84 (Guide to test, training and exercise programs for IT plans and capabilities); ISO 22320 (Emergency management: guidelines for incident management); ISO 22301 (Business continuity management systems: requirements) | MCF-RES-021; MCF-RES-020; MCF-SEC-019; MCF-RES-003 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-RES-020 | RES | Resilience, Continuity and Recovery | RES-05 | Testing and exercising | Lessons and Retest | Ensure that defects and lessons from tests, exercises and real incidents are tracked to closure, reflected in plans and designs, and verified by retest. | The resilience owner shall maintain a lessons register capturing every defect and lesson from tests, exercises and incidents with owner, due date, and the plan, runbook, design or control affected. The resilience owner shall require retest or equivalent verification before closure of any lesson affecting a gate-critical safeguard and shall report overdue items to governance monthly. | 1) All defects and lessons from the period are in the register with owner and due date. 2) Affected plans, runbooks and designs were updated. 3) Gate-critical items were closed only after retest or equivalent verification. 4) Overdue items were reported to governance. | Maximum age of open gate-critical lesson [days] default 90 (illustrative) (Capability-profile parameter.) | Lessons register; Updated plan/runbook versions; Retest records; Governance reports | DOCUMENT_REVIEW; SAMPLING; RECONCILIATION | 1) Trace defects from test, exercise and incident reports into the register. 2) Sample closed items for plan updates and retest. 3) Review overdue items and governance reporting. | CORRECTIVE | OPERATION | AL4 | OPERATE; CHANGE | NORMAL; RECOVERY | Applies to all resilience tests, exercises and incidents in scope. |  | CG-10; CG-14 | Same defect recurring in successive tests; Lessons closed without verification | Finding; Action; TestRecord | Retests follow the safety requirements of the original test control. | Items closed without verification evidence are reopened as UNKNOWN U1. | ISO 22301 (Business continuity management systems: requirements); NIST SP 800-84 (Guide to test, training and exercise programs for IT plans and capabilities) | MCF-RES-018; MCF-RES-019; MCF-RES-024; MCF-OPS-016 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-RES-021 | RES | Resilience, Continuity and Recovery | RES-06 | Crisis and adaptive response | Crisis Command | Ensure a crisis command structure with defined levels, authority, activation criteria and facilities can take timely decisions during major infrastructure and cyber-physical events. | The executive sponsor shall establish a crisis command structure with strategic, tactical and operational levels, named primary and alternate role holders, activation criteria, decision authority (including authority to shed load, suspend tenants, invoke alternate capacity and order controlled shutdown), and command facilities and communication channels that remain available when site systems, corporate identity or primary communications fail. The crisis management lead shall demonstrate activation and decision timings in exercises or real events. | 1) The command structure defines levels, roles, alternates and decision authority. 2) Activation criteria are defined and linked to monitoring and incident triggers. 3) Command facilities and communications are available independently of site systems and corporate identity. 4) Exercises or events in the period demonstrated activation within the target time and decisions within authority. 5) Decision logs were maintained. | Crisis command activation time [min from trigger] default 30 (illustrative) (Capability-profile parameter.) | Crisis command plan; Role and alternate roster; Communication channel independence analysis; Exercise/event records with timings and decision logs | DOCUMENT_REVIEW; SCENARIO_EXERCISE; OBSERVATION; INQUIRY | 1) Review plan, roles and authority. 2) Check communication independence. 3) Review exercise or event timings and decision logs. 4) Interview role holders on authority. | CORRECTIVE | EFFECTIVENESS | AL5 | PLAN; OPERATE | EMERGENCY; FAILED; RECOVERY | Applies to every in-scope organisation and site. |  | CG-13; CG-10 | No one authorised to order controlled shutdown; Crisis bridge relies on failed identity provider; Alternate role holders untrained | Safeguard; Action; Event | Exercises shall be clearly labelled to prevent confusion with real events; live notifications to customers or authorities during exercises require prior approval. | If command communications depend on an unanalysed service, record U10 against crisis command availability. | ISO 22320 (Emergency management: guidelines for incident management); ISO 22301 (Business continuity management systems: requirements); NIST SP 800-61 Rev. 3 (Incident response recommendations) | MCF-RES-022; MCF-RES-012; MCF-OPS-014; MCF-GOV-002 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-RES-022 | RES | Resilience, Continuity and Recovery | RES-06 | Crisis and adaptive response | Stakeholder Communications | Ensure timely, accurate communication to customers, tenants, regulators, providers and staff during disruption, consistent with contractual and regulatory notification obligations. | The crisis management lead shall maintain a communications plan listing stakeholders, notification obligations and deadlines (contractual and regulatory), approved message templates, approval authority and channels that remain available during site and identity failures. The crisis management lead shall record each notification issued during events and exercises with timestamp and approver and shall review timeliness against obligations. | 1) A communications plan lists stakeholders, obligations, deadlines and channels. 2) Templates and approval authorities are defined. 3) Notifications in events and exercises in the period met deadlines. 4) Channels are available independently of site and corporate identity systems. |  | Communications plan; Obligation register; Notification logs | DOCUMENT_REVIEW; RECONCILIATION; INQUIRY | 1) Review the plan and obligation register. 2) Reconcile notification logs with deadlines. 3) Check channel independence. | CORRECTIVE | OPERATION | AL4 | PLAN; OPERATE | EMERGENCY; RECOVERY | Applies to every in-scope organisation. |  | CG-13 | Missed regulatory notification; Inconsistent customer messaging; Communication channel lost with site | Action; Event; Interface | Exercise messages shall be marked as exercise and not sent externally without approval. | Obligations without a known deadline are recorded as U9 pending legal interpretation. | ISO 22320 (Emergency management: guidelines for incident management); Regulation (EU) 2022/2554 (Digital Operational Resilience Act); ISO 22301 (Business continuity management systems: requirements) | MCF-RES-021; MCF-GOV-019; MCF-GOV-022; MCF-SUP-007 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-RES-023 | RES | Resilience, Continuity and Recovery | RES-06 | Crisis and adaptive response | Emergency Change | Ensure changes made under emergency conditions are authorised by defined emergency authority, minimal, recorded, and reconciled back to baseline after the event. | The change authority shall define an emergency change procedure stating who may authorise emergency changes to infrastructure, OT and control-plane systems, the minimum record to be captured at the time, and the deadline for retrospective review. The recovery manager shall ensure every emergency change is retrospectively reviewed, either reverted or formalised, and that baselines and evidence are updated, and shall report unreconciled emergency changes. | 1) An emergency change procedure defines authority, minimum records and retrospective review deadline. 2) Emergency changes in the period were authorised by defined authority. 3) Each emergency change was reviewed within the deadline and reverted or formalised. 4) Baselines (NET-022, OPS-017) were updated after formalised emergency changes. | Emergency change retrospective review deadline [working days] default 5 (illustrative) (Capability-profile parameter.) | Emergency change procedure; Emergency change records; Retrospective reviews; Baseline updates | SAMPLING; RECONCILIATION; DOCUMENT_REVIEW | 1) Review procedure. 2) Identify emergency changes from logs and drift. 3) Check authorisation and retrospective review. 4) Verify baseline updates. | CORRECTIVE | OPERATION | AL4 | OPERATE; CHANGE | EMERGENCY; RECOVERY | Applies to all infrastructure, OT and control-plane systems in scope. |  | CG-14 | Emergency bypass left in place; Unrecorded emergency configuration becoming latent fault; Emergency authority exceeded | Action; Event; ArchitectureSnapshot | Records-based. | Emergency changes identified from drift with no record are Findings; if logs are unavailable, record U2. | ISO 22301 (Business continuity management systems: requirements); NIST SP 800-61 Rev. 3 (Incident response recommendations) | MCF-OPS-018; MCF-OPS-019; MCF-NET-022; MCF-SEC-022 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-RES-024 | RES | Resilience, Continuity and Recovery | RES-06 | Crisis and adaptive response | Post-Event Adaptation | Ensure that after material events the organisation analyses root causes and systemic contributors, adapts design, operations and assurance, and triggers reassessment of affected claims. | The resilience owner shall require a post-event review within a defined time after every material event, covering timeline, root and contributing causes, safeguard performance against expectation, recovery performance against tolerance, and required adaptations to design, operations, controls and evidence. The resilience owner shall raise reassessment triggers for affected controls and gate results and shall track adaptations to completion. | 1) Post-event reviews were completed for every material event within the defined time. 2) Reviews compare safeguard and recovery performance with expectation and tolerance. 3) Adaptations are tracked to completion. 4) Reassessment triggers were raised for affected controls and gates. | Post-event review deadline [days] default 30 (illustrative) (Capability-profile parameter.) | Post-event review reports; Adaptation tracker; Reassessment trigger records | DOCUMENT_REVIEW; SAMPLING; INQUIRY | 1) List material events from incident systems. 2) Check review completion and content. 3) Trace adaptations and reassessment triggers. | CORRECTIVE | OPERATION | AL4 | OPERATE; CHANGE | RECOVERY; NORMAL | Applies to all material events affecting in-scope outcomes. |  | CG-14 | Repeat incidents from unaddressed systemic causes; Evidence relied on despite invalidating event | Event; ReassessmentTrigger; Finding; Action | Post-event reviews are non-intrusive; any reproduction of the event to confirm causes is a test governed by RES-018 authorisation requirements. | Events without a completed review mark the evidence of affected controls as STALE until reviewed. | ISO 22316 (Organizational resilience: principles and attributes); ISO 22301 (Business continuity management systems: requirements); NIST SP 800-61 Rev. 3 (Incident response recommendations) | MCF-RES-020; MCF-OPS-015; MCF-EVA-022; MCF-OPS-016 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-SUP-001 | SUP | Supply Chain, OEM and Ecosystem Assurance | SUP-01 | Supplier due diligence | Supplier Capability | Suppliers of critical equipment and services are shown, before award and at renewal, to have the technical, manufacturing, integration, installation and field-support capability required by the Capability Instance at the site and scale proposed. | The procurement lead shall perform and record a capability assessment for each supplier of a critical asset class or service before award and at renewal, covering engineering competence, manufacturing and test capacity (including factory acceptance testing), rack-scale or skid integration capability where applicable, installation and commissioning resources, field-service coverage and response at the site, and references for comparable deployments. A competent engineer shall approve the technical part of the assessment. | 1) A capability assessment exists for each critical supplier, dated before award or last renewal. 2) The assessment addresses manufacturing/test capacity, integration, installation/commissioning and field-service coverage for the specific site. 3) Factory acceptance test (FAT) capability and witness arrangements are confirmed for equipment where FAT is specified (for example switchgear, UPS, CDUs, rack-scale systems). 4) Technical approval by a competent engineer is recorded. 5) Identified capability gaps have conditions in the contract or an accepted risk. |  | Supplier capability assessments.; FAT plans or capability statements.; Field-service coverage statements.; Engineering approval records. | DOCUMENT_REVIEW; INQUIRY; SAMPLING | 1) List critical suppliers from DEP-011/DEP-014. 2) Obtain capability assessments and approvals. 3) Check coverage of manufacturing, integration, installation and field service. 4) Verify gaps have contractual conditions or acceptance. | PREVENTIVE | DESIGN | AL2 | PLAN; DESIGN; BUILD; CHANGE | NORMAL | Applies to suppliers of critical asset classes and services; non-critical suppliers follow standard procurement. |  | CG-03 | Integrator lacks capacity to test rack-scale systems before delivery; No field engineer within response time of the site; Supplier cannot perform specified FAT | Dependency; Resource; AssetInstance | Not applicable (documentary assessment). | Missing capability assessment for a critical supplier is U1, US3. | ISO 9001 (quality management systems); ISO 44001 (collaborative business relationship management); ISO/IEC 27036-2 (supplier relationships: requirements) | MCF-SUP-002; MCF-SUP-003; MCF-DEP-011; MCF-CAP-022 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-SUP-002 | SUP | Supply Chain, OEM and Ecosystem Assurance | SUP-01 | Supplier due diligence | Financial and Operational Resilience | The financial health, manufacturing footprint, allocation exposure and business-continuity capability of critical suppliers are monitored so that supplier distress or disruption is detected early enough to act. | The supplier manager shall monitor each critical supplier at the profile interval for financial distress indicators, manufacturing and logistics concentration (single plant or region), allocation or quota exposure (for example accelerator allocations), sanctions and export-control exposure, and business-continuity arrangements, and shall escalate adverse changes to the capability owner with a proposed treatment. | 1) Each critical supplier has monitoring records at the interval for the period. 2) Manufacturing and logistics concentration is recorded per supplier. 3) Allocation, sanctions and export-control exposure is assessed for supply-constrained classes. 4) Supplier business-continuity evidence has been obtained for the most critical suppliers. 5) Adverse changes in the period were escalated with treatment. | Supplier monitoring interval [months] default 6 (Illustrative; quarterly for sole-source suppliers.) | Supplier monitoring records.; Financial risk reports (credit agency or equivalent).; Supplier BCP summaries.; Escalation records. | DOCUMENT_REVIEW; ANALYSIS; INQUIRY | 1) Obtain monitoring records. 2) Check interval adherence and coverage. 3) Review export and allocation exposure analyses. 4) Trace adverse changes to escalation. | DETECTIVE | OPERATION | AL4 | PLAN; OPERATE; CHANGE | NORMAL | Applies to critical suppliers. |  | CG-03 | Supplier insolvency halts spares; Single plant outage stops supply; Export restriction blocks accelerator deliveries | Dependency; Threat; Resource | Desk-based monitoring; no site testing is involved. | No monitoring of a sole-source supplier is US3. | ISO 22318 (guidelines for supply chain continuity); ISO 22301 (business continuity management systems); NIST SP 800-161r1 (cyber supply chain risk management) | MCF-SUP-001; MCF-DEP-014; MCF-SUP-018 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-SUP-003 | SUP | Supply Chain, OEM and Ecosystem Assurance | SUP-01 | Supplier due diligence | Security and Quality Posture | Critical suppliers operate quality management and secure development practices adequate for products that will run, control or protect AI infrastructure, including product security incident response for firmware and control software. | The procurement lead shall obtain and evaluate evidence of each critical supplier's quality management system, product security development lifecycle for firmware and control software, product security incident response (PSIRT) and vulnerability disclosure process, and factory test and outgoing quality controls. The procurement lead shall record identified gaps with contract conditions and shall track incoming quality (defects on receipt, early-life failures) for each supplier. | 1) Quality management evidence (certificate or audit) is current for each critical supplier. 2) Secure development lifecycle evidence exists for suppliers of firmware or control software. 3) A PSIRT or equivalent contact and disclosure process exists for each firmware or software supplier. 4) Incoming quality data is tracked and reviewed. 5) Gaps have contractual conditions. |  | QMS certificates or audit reports.; Secure development evidence (for example IEC 62443-4-1 assessment or equivalent attestation).; PSIRT contacts and disclosure policy.; Incoming quality records. | DOCUMENT_REVIEW; INQUIRY; ANALYSIS | 1) Obtain supplier posture evidence. 2) Check currency and scope. 3) Review incoming quality data. 4) Check gap conditions. | PREVENTIVE | IMPLEMENTATION | AL3 | PLAN; BUILD; OPERATE | NORMAL | Applies to critical hardware, firmware and control-software suppliers. |  | CG-08; CG-15 | Supplier without vulnerability disclosure process; Batch quality escape in optics or memory; Uncontrolled firmware build process | Dependency; Threat; AssetInstance | Desk-based evaluation; any supplier site audit follows the supplier's site safety rules. | Missing PSIRT evidence for a firmware supplier is US3. | ISO 9001 (quality management systems); IEC 62443-4-1 (secure product development lifecycle); NIST SP 800-218 (Secure Software Development Framework); ISO/IEC 29147 (vulnerability disclosure); ISO/IEC 30111 (vulnerability handling processes) | MCF-SUP-016; MCF-SUP-013; MCF-SEC-014 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-SUP-004 | SUP | Supply Chain, OEM and Ecosystem Assurance | SUP-01 | Supplier due diligence | Sub-Tier Visibility | Critical sub-tier dependencies behind first-tier suppliers (for example high-bandwidth memory and advanced packaging for accelerators, laser and optical components, transformer core steel and bushings, switchgear breaker mechanisms, CDU pumps and heat exchangers, battery cells, controller chipsets, and contract manufacturers) are known well enough to reveal shared sub-tier sources across nominally diverse suppliers. | The procurement lead shall obtain, for each critical asset class, disclosure of material sub-tier suppliers and manufacturing locations from first-tier suppliers, record them in the dependency graph, and identify sub-tier sources shared across nominally diverse first-tier suppliers. Where a supplier declines disclosure, the procurement lead shall record an UNKNOWN Record and the capability owner shall decide on treatment. | 1) Sub-tier disclosure has been requested and recorded for each critical asset class. 2) Shared sub-tier sources across diverse first-tier suppliers are identified. 3) Sub-tier information is in the dependency graph and used in DEP-014 concentration analysis. 4) Declined or partial disclosures are UNKNOWN Records with treatment decisions. | Sub-tier depth for critical classes [tiers] default 2 (Illustrative; deeper where single-source components are known.) | Sub-tier disclosure records.; Dependency graph sub-tier entries.; UNKNOWN Records for declined disclosures. | DOCUMENT_REVIEW; ANALYSIS; INQUIRY; RECONCILIATION | 1) Obtain disclosures. 2) Map into dependency graph. 3) Search for shared sub-tier nodes. 4) Corroborate a sample. 5) Review UNKNOWN treatment. | PREVENTIVE | IMPLEMENTATION | AL3 | PLAN; DESIGN; OPERATE; CHANGE | NORMAL; RECOVERY | Applies to critical asset classes with constrained supply or long lead times. | CG-03 |  | Two UPS brands share one battery-cell maker; All accelerator suppliers depend on one packaging capacity; Transformer suppliers share one bushing source | Dependency; Resource; UnknownRecord | Desk-based analysis; sub-tier disclosures may be commercially sensitive and shall be handled under the classification rules of AIDCF-008. | Declined sub-tier disclosure for a critical class whose failure would defeat recovery or expansion is U2/U10, US4 (CG-03 critical). | NIST SP 800-161r1 (cyber supply chain risk management); ISO 22318 (guidelines for supply chain continuity); ISO 28000 (supply chain security management) | MCF-DEP-014; MCF-SUP-002; MCF-SUP-018; MCF-DEP-002 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-SUP-005 | SUP | Supply Chain, OEM and Ecosystem Assurance | SUP-02 | Contract and service obligations | Service Levels | Contracts for maintenance, support and supply of critical systems contain measurable service levels (response, on-site attendance, restore, parts availability, RMA turnaround) that are consistent with the Service Outcome and recovery tolerances. | The supplier manager shall ensure each critical support or maintenance contract states measurable service levels with units, measurement points, exclusions and escalation, and shall document that each service level is consistent with the time-to-impact and recovery tolerances in DEP-003 and CAP-02. Where contracted levels are inconsistent, the capability owner shall record the gap and its treatment (on-site spares, resident engineers, alternative supplier). | 1) Each critical contract has measurable service levels with units and measurement points. 2) Service levels are compared with tolerances and the comparison is recorded. 3) Inconsistencies have treatments. 4) Escalation contacts and paths are current. | Maximum on-site attendance time for critical electrical/mechanical faults [hours] default 4 (Illustrative; set from DEP-003 time-to-impact and spares held.) | Contracts or schedules with service levels.; Tolerance comparison.; Escalation contact lists. | DOCUMENT_REVIEW; ANALYSIS | 1) List critical contracts. 2) Extract service levels. 3) Compare with tolerances. 4) Review treatments and escalation lists. | DIRECTIVE | IMPLEMENTATION | AL3 | PLAN; BUILD; OPERATE; CHANGE | NORMAL; EMERGENCY; RECOVERY | Applies to critical support and maintenance contracts. |  | CG-10; CG-13 | Next-business-day support for asset with minutes time-to-impact; Exclusions void service level during regional event | Dependency; Interface; Resource | Contract review only; no response-time test shall be performed by raising false faults with suppliers. | Service level absent for a critical contract is US3. | ISO/IEC 20000-1 (service management system requirements); ISO/IEC 19086-1 (cloud SLA framework) | MCF-DEP-022; MCF-DEP-003; MCF-SUP-017 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-SUP-006 | SUP | Supply Chain, OEM and Ecosystem Assurance | SUP-02 | Contract and service obligations | Evidence Rights | The owner has contractual rights to obtain the evidence needed to assess supplier-provided and provider-operated functions: test and commissioning records, maintenance records, firmware SBOMs and release notes, telemetry access, incident RCAs, audit reports and access for witness testing and audit. | The supplier manager shall ensure that each critical supplier and provider contract grants rights to the evidence listed in the AIDCF-008 control evidence profiles relevant to the supplied function, within stated timescales and formats, including rights to witness tests and to audit or receive independent assurance reports, and shall record any evidence the supplier will not provide as an UNKNOWN Record against the affected controls. | 1) Each critical contract has an evidence-rights clause or schedule. 2) The listed evidence covers mandatory items of the affected controls. 3) Rights to witness FAT/SAT and audit exist where needed. 4) Refused evidence is recorded as UNKNOWN against controls. | Evidence delivery time on request [working days] default 10 (Illustrative.) | Contract evidence-rights clauses.; Mapping of rights to control evidence profiles.; Records of evidence requests and responses. | DOCUMENT_REVIEW; SAMPLING | 1) Obtain clauses. 2) Map to control evidence profiles. 3) Sample evidence requests and responses. | DIRECTIVE | IMPLEMENTATION | AL3 | PLAN; BUILD; OPERATE | NORMAL | Applies to critical supplier and provider contracts. |  | CG-03 | Colocation provider refuses generator test records; OEM declines firmware SBOM; No right to witness CDU FAT | EvidenceRequirement; Dependency; UnknownRecord | Contract review only; evidence requests are made through the contract channel, not by direct access to supplier systems. | Absent evidence rights for a provider-operated critical function is US3 for this control; the consequential UNKNOWN on dependent controls takes those controls' severity. | ISO/IEC 27036-2 (supplier relationships: requirements); ISO 19011 (auditing management systems); AICPA SOC 2 reporting framework | MCF-DEP-018; MCF-EVA-002; MCF-SUP-013 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-SUP-007 | SUP | Supply Chain, OEM and Ecosystem Assurance | SUP-02 | Contract and service obligations | Incident Notification | Suppliers and providers notify the owner promptly of incidents, vulnerabilities, field notices, recalls, allocation changes and planned changes that could affect supplied functions, and the notifications reach the people who must act. | The supplier manager shall ensure critical supplier and provider contracts define notification obligations and timescales for incidents, security vulnerabilities, field notices and recalls, planned maintenance and changes, and allocation or end-of-life changes, and shall operate a monitored intake (shared mailbox, portal subscription, ticket integration) that routes notifications to the responsible owner. The supplier manager shall test the intake path at the profile interval. | 1) Notification obligations and timescales exist in critical contracts. 2) Notification intake is monitored and routed to responsible owners. 3) Notifications in the period were received, routed and acted on within timescales. 4) The intake path was tested within the interval. | Notification intake test interval [months] default 6 (Illustrative.) | Contract notification clauses.; Intake configuration and routing rules.; Notification log for period.; Intake test records. | DOCUMENT_REVIEW; RECONCILIATION; TEST; SAMPLING | 1) Obtain clauses and intake design. 2) Compare public advisories to intake log. 3) Trace sample to action. 4) Review intake tests. | DETECTIVE | OPERATION | AL4 | OPERATE; CHANGE | NORMAL; DEGRADED | Applies to critical suppliers and providers that can affect a supplied function through incidents, vulnerabilities, recalls or planned changes. |  | CG-03; CG-15 | Field notice for breaker trip units missed; Carrier planned works not received; Vulnerability advisory for BMC firmware unnoticed | Event; Dependency; Action | Intake tests send synthetic notifications only. | No notification log is U1, US3. | Directive (EU) 2022/2555 (NIS2), supply chain and incident reporting provisions — informative; ISO/IEC 27036-3 (ICT supply chain security); ISO/IEC 29147 (vulnerability disclosure) | MCF-SUP-016; MCF-DEP-023; MCF-SUP-020 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-SUP-008 | SUP | Supply Chain, OEM and Ecosystem Assurance | SUP-02 | Contract and service obligations | Exit and Transition Rights | The owner can exit or replace a critical supplier or provider without losing the ability to operate, maintain or recover critical systems, including access to configuration, control logic, data, documentation, licences, spares and transition assistance. | The supplier manager shall ensure each critical contract provides exit and transition rights proportionate to the dependency, including export of configuration and operational data in usable formats, ownership or escrow of control logic and configuration for programmable controllers, perpetual or transition licences for software required to operate installed equipment, option to purchase spares and tools, documentation hand-over, and transition assistance for a stated period. The capability owner shall maintain an exit plan for each sole-source or high-concentration supplier. | 1) Exit and transition clauses exist in critical contracts. 2) Control logic and configuration ownership or escrow is established for programmable controllers. 3) Licences needed to operate installed equipment survive termination or transition. 4) Exit plans exist for sole-source and high-concentration suppliers. | Minimum transition assistance period [months] default 12 (Illustrative.) | Contract exit clauses.; Escrow agreements or ownership evidence.; Licence terms.; Exit plans. | DOCUMENT_REVIEW; ANALYSIS | 1) Obtain clauses and plans. 2) Check control-logic and licence provisions. 3) Review exit plans for feasibility. | DIRECTIVE | DESIGN | AL2 | PLAN; OPERATE; DECOMMISSION | NORMAL; TRANSITION | Applies to critical suppliers and providers; mandatory exit plans apply to sole-source and high-concentration suppliers identified under MCF-DEP-014. |  | CG-10 | Supplier exit leaves BMS without editable logic; Licence revocation disables installed equipment; Provider holds operational data hostage | Dependency; Resource | Contract and plan review only; escrow release or licence-transfer trials are performed only under agreement with the supplier. | No exit plan for a sole-source supplier is US3. | ISO/IEC 27036-2 (supplier relationships: requirements); ISO/IEC 19086-1 (cloud SLA framework); Regulation (EU) 2022/2554 (DORA), exit strategy provisions — informative | MCF-DEP-015; MCF-DEP-016; MCF-SUP-020 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-SUP-009 | SUP | Supply Chain, OEM and Ecosystem Assurance | SUP-03 | Hardware and component provenance | Approved Sourcing | Critical components (protection devices, circuit breakers and trip units, relays, UPS modules and batteries, accelerators and boards, memory, optics, NICs/DPUs, storage media, controllers and sensors) are purchased only from the OEM or OEM-authorised channels, so that counterfeit, grey-market, refurbished-as-new and tampered parts are excluded at source. | The procurement lead shall maintain an approved source list for each critical component class naming the OEM and authorised distributors, shall configure purchasing controls so that orders for critical classes can be placed only with approved sources, and shall require documented engineering approval and enhanced inspection (MCF-SUP-010) for any exception, such as broker purchase of obsolete parts. | 1) An approved source list exists per critical component class. 2) Purchasing system controls restrict critical-class orders to approved sources. 3) A sample of purchase orders in the period shows only approved sources or approved exceptions. 4) Each exception has engineering approval and enhanced inspection evidence. |  | Approved source list.; Purchasing system configuration.; Sampled purchase orders.; Exception approvals. | DOCUMENT_REVIEW; SAMPLING; RECONCILIATION | 1) Obtain list and system configuration. 2) Sample orders including emergency purchases during incidents. 3) Verify source approval and exceptions. | PREVENTIVE | IMPLEMENTATION | AL3 | BUILD; OPERATE; CHANGE | NORMAL; RECOVERY; EMERGENCY | Applies to critical component classes; emergency purchases during recovery are in scope. |  | CG-08; CG-04 | Counterfeit breaker fails to interrupt fault current; Grey-market optics with altered EEPROM; Refurbished GPUs sold as new | AssetInstance; Threat; Safeguard | Purchasing records review only. | Unverifiable source of installed protection devices is US3; US4 if CG-04 relies on their interrupting performance. | SAE AS5553 (counterfeit electronic parts avoidance); SAE AS6081 (counterfeit parts avoidance for distributors); ISO/IEC 20243 (Open Trusted Technology Provider Standard) | MCF-SUP-010; MCF-SUP-011; MCF-PHY-017 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-SUP-010 | SUP | Supply Chain, OEM and Ecosystem Assurance | SUP-03 | Hardware and component provenance | Counterfeit Prevention | Counterfeit, cloned, remarked or tampered components are detected at receipt, before installation, by inspection and test proportionate to risk, and suspect parts are quarantined and reported. | The receiving and engineering leads shall operate a risk-based incoming inspection for critical component classes, including label, serial and packaging verification against OEM records, physical inspection, and where risk warrants electrical or functional testing (for example protection device trip testing, optics DOM/EEPROM checks, firmware identity checks on boards). Suspect items shall be quarantined, reported to the OEM and, where required, to the relevant authority, and shall not be installed until cleared. | 1) Incoming inspection criteria are defined per critical class and risk level. 2) Inspection records exist for receipts in the period. 3) OEM serial verification is performed for high-value or safety-critical items. 4) Suspect items were quarantined and reported. 5) No installed critical item in a sample lacks an inspection record. | Serial verification coverage for safety-critical protection devices [% of units received] default 100 (Illustrative.) | Inspection criteria.; Receipt inspection records.; OEM serial verification responses.; Quarantine log. | DOCUMENT_REVIEW; SAMPLING; INSPECTION; REPERFORMANCE | 1) Obtain inspection criteria. 2) Sample receipts and installed items. 3) Reperform serial verification for a sample. 4) Review quarantine handling. | DETECTIVE | OPERATION | AL4 | BUILD; OPERATE | NORMAL; RECOVERY | Applies to receipts of critical component classes. |  | CG-04; CG-08 | Counterfeit MCCB installed in PDU; Cloned optics causing fabric errors; Remarked memory modules | AssetInstance; Threat; TestRecord | Electrical testing of protection devices shall be done on a test bench by competent persons; no testing of devices in live switchboards under this control. | Installed safety-critical device without inspection record is US3; US4 where it is a protection device relied on by CG-04. | SAE AS5553 (counterfeit electronic parts avoidance); SAE AS6171 (test methods for suspect counterfeit parts); SAE AS6174 (counterfeit materiel) | MCF-SUP-009; MCF-SUP-011; MCF-SUP-012 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-SUP-011 | SUP | Supply Chain, OEM and Ecosystem Assurance | SUP-03 | Hardware and component provenance | Chain of Custody | High-value and integrity-sensitive equipment (accelerator systems, storage media, network gear, controllers, spare boards) is under recorded custody from the factory or integrator to installation, so that theft, substitution and tampering in transit or staging are prevented or detected. | The logistics lead shall require tamper-evident packaging and seals for critical shipments, recorded hand-offs between factory, freight forwarder, carrier and site, secure staging areas with access control, and receipt verification of seals and serials against the advance shipping notice. Breaks in custody or seal anomalies shall be recorded as security events and the affected items quarantined pending inspection. | 1) Custody requirements are in logistics contracts for critical shipments. 2) Custody records exist for sampled shipments end-to-end. 3) Seal and serial verification at receipt is recorded. 4) Staging areas are access-controlled and logged. 5) Custody anomalies were treated as security events. |  | Logistics contracts.; Custody records and seal logs.; Advance shipping notices.; Staging access logs.; Anomaly reports. | DOCUMENT_REVIEW; SAMPLING; INSPECTION; RECONCILIATION | 1) Sample shipments. 2) Reconcile custody records across parties. 3) Inspect staging area controls. 4) Review anomalies. | PREVENTIVE | OPERATION | AL4 | BUILD; OPERATE; CHANGE | NORMAL | Applies to critical and high-value shipments, including RMA returns and spares. |  | CG-08 | Theft of accelerator trays in transit; Tampered network device inserted; Unlogged staging access | AssetInstance; Threat; Event | Staging-area inspection follows site access control; sealed shipments shall not be opened by the assessor. | Custody gap for an installed integrity-sensitive item is US3. | ISO 28000 (supply chain security management); TAPA Freight Security Requirements; ISO/IEC 20243 (Open Trusted Technology Provider Standard) | MCF-PHY-017; MCF-PHY-018; MCF-SUP-010 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-SUP-012 | SUP | Supply Chain, OEM and Ecosystem Assurance | SUP-03 | Hardware and component provenance | Component Traceability | Critical installed components can be traced by serial number, part number, revision and firmware to their location and the functions they support, quickly enough to act on a field notice, recall or vulnerability before it causes harm. | The asset manager shall record serial, part number, hardware revision and firmware version for critical components (accelerators and boards, NICs/DPUs, optics, switch line cards, storage media, breaker trip units, relays, UPS modules, batteries, CDU pumps and controllers) in the asset register linked to location and Required Function, and shall demonstrate at the profile interval, by exercise, that all units affected by a given notice can be identified within the target time. | 1) Critical component records include serial, part, revision and firmware with location. 2) Records reconcile to installed units for a sample. 3) A traceability exercise in the interval identified all affected units within target time. 4) Real field notices in the period were traced and actioned. | Target time to identify all affected units [hours] default 24 (Illustrative.) Traceability exercise interval [months] default 12 (Illustrative.) | Asset register extract.; Reconciliation sample.; Exercise record with timing.; Field notice action records. | RECONCILIATION; SCENARIO_EXERCISE; SAMPLING; TEST | 1) Obtain register. 2) Reconcile sample to installed units via inspection or telemetry (for example inventory from BMC/Redfish). 3) Run or review traceability exercise with a defined notice. 4) Review real notice handling. | DETECTIVE | EFFECTIVENESS | AL5 | BUILD; COMMISSION; OPERATE; CHANGE | NORMAL | Applies to critical component classes. |  | CG-08; CG-03 | Recall for battery cells cannot be scoped; Optics batch with defect cannot be located; Firmware vulnerability scope unknown | AssetInstance; TestRecord; Event | Exercise is desk-based; reading inventory via management interfaces uses read-only accounts. | Inability to scope a real field notice affecting critical components is US3; US4 where the notice concerns a life-safety or protection device. | ISO/IEC 19770-1 (IT asset management); DMTF Redfish (platform management API) for inventory retrieval; GS1 identification standards | MCF-DEP-001; MCF-CMP-013; MCF-SUP-007 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-SUP-013 | SUP | Supply Chain, OEM and Ecosystem Assurance | SUP-04 | Software, firmware and update supply | Release Provenance | Every firmware, software and configuration package deployed to AI and facility infrastructure (accelerator and board firmware, BMC/BIOS, NIC/DPU firmware, switch OS, storage controller software, drivers and runtime stacks, UPS/PDU/ATS firmware, BMS/EPMS software, CDU and PLC logic) comes from an authenticated source with release notes and component inventory, and is held in a controlled internal repository before deployment. | The platform and control-system owners shall obtain releases only from authenticated OEM channels, record for each release its origin, version, hash, release notes and software bill of materials where available, store it in a controlled repository with access control and integrity protection, and deploy only from that repository. Releases for programmable facility controllers shall be held with the same controls as IT firmware. | 1) A controlled repository exists for firmware and software releases covering IT and facility systems. 2) Each release in the repository has origin, version, hash and release notes recorded; SBOM is held where the supplier provides one. 3) Deployment tooling pulls only from the repository (configuration evidence). 4) A sample of deployed versions reconciles to repository entries. 5) PLC/CDU/BMS logic versions are held with equivalent controls. |  | Repository inventory with metadata.; Repository access control configuration.; Deployment tool configuration.; Reconciliation of deployed versions. | DOCUMENT_REVIEW; RECONCILIATION; SAMPLING; INSPECTION | 1) Obtain repository inventory. 2) Check metadata completeness. 3) Inspect deployment tooling configuration. 4) Reconcile deployed versions from devices to repository. | PREVENTIVE | IMPLEMENTATION | AL3 | BUILD; COMMISSION; OPERATE; CHANGE | NORMAL; MAINTENANCE; RECOVERY | Applies to all programmable devices in the boundary. |  | CG-15; CG-14 | Firmware downloaded from unofficial mirror; PLC logic version unknown; Untracked driver stack on part of cluster | AssetInstance; EvidenceObject; Threat | Device version reads use read-only interfaces; no update is performed under this control. | Unknown provenance of deployed firmware on a control-system or protection device is US3; US4 where CG-07 or CG-15 relies on it. | NIST SP 800-218 (Secure Software Development Framework); ISO/IEC 5962 (SPDX); ECMA-424 (CycloneDX); NTIA minimum elements for an SBOM | MCF-SUP-014; MCF-CMP-013; MCF-SEC-013; MCF-OPS-017 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-SUP-014 | SUP | Supply Chain, OEM and Ecosystem Assurance | SUP-04 | Software, firmware and update supply | Signature Validation | Firmware and software are cryptographically verified before installation and, where the platform supports it, at boot, so that modified or malicious images are rejected. | The platform and control-system owners shall verify OEM signatures (or, where signing is unavailable, OEM-published hashes obtained over an authenticated channel) before staging any release to the repository and before deployment, shall enable platform secure-boot and firmware-signature enforcement where supported (for example on BMCs, accelerators, NICs/DPUs, switches), and shall record device classes that cannot enforce signatures with compensating controls. The owners shall demonstrate rejection of an unsigned or altered image on a non-production device for each enforcing device class. | 1) Signature or hash verification is performed and logged for each release staged in the period. 2) Signature enforcement is enabled on supporting device classes (configuration evidence). 3) Non-enforcing device classes are listed with compensating controls. 4) A rejection test on non-production equipment has been performed for each enforcing class. 5) Where supported, firmware attestation (for example via SPDM measurements) is collected. |  | Verification logs.; Device configuration showing signature enforcement.; Non-enforcing class register.; Rejection test records. | DOCUMENT_REVIEW; INSPECTION; TEST; SAMPLING | 1) Obtain logs and configuration. 2) Sample releases and check verification. 3) Inspect enforcement settings. 4) Review or witness rejection test. | PREVENTIVE | EFFECTIVENESS | AL5 | COMMISSION; OPERATE; CHANGE | NORMAL; MAINTENANCE; RECOVERY | Applies to all programmable devices; enforcement criterion applies where the platform supports it. |  | CG-15; CG-08 | Malicious BMC firmware installed; Tampered switch OS image; Unsigned PLC logic loaded | Safeguard; TestRecord; AssetInstance | Rejection tests shall be performed only on non-production devices isolated from production management networks; flashing production devices to test is prohibited. | Unknown enforcement status on a device class with control-plane authority is US3; US4 where CG-15 relies on it. | NIST SP 800-193 (platform firmware resiliency); NIST SP 800-147 (BIOS protection); DMTF DSP0274 (SPDM); IETF RFC 9334 (remote attestation procedures architecture) | MCF-SUP-013; MCF-SEC-013; MCF-CMP-013 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-SUP-015 | SUP | Supply Chain, OEM and Ecosystem Assurance | SUP-04 | Software, firmware and update supply | Compatibility Assurance | Firmware, driver and software updates are deployed only in combinations that are validated as compatible, and are rolled out in stages aligned to fault domains so that a defective release cannot defeat redundant capacity at once. | The platform owner shall maintain a compatibility matrix for interdependent components (for example accelerator firmware, driver and runtime libraries, NIC/DPU firmware, switch OS, BMC/BIOS, storage client; and for facility systems UPS firmware and EPMS, CDU controller and BMS integration), shall test each new combination on a representative non-production environment, and shall deploy through staged waves where each wave is confined to one fault domain and passes defined health criteria before the next begins. Redundant members of a group shall not be updated in the same wave. | 1) A compatibility matrix exists and is current. 2) Each deployed combination in the period was tested before production. 3) Rollouts followed fault-domain-aligned waves with health gates (deployment records). 4) No rollout updated redundant members of a group in one wave. 5) Health-gate failures halted rollouts and triggered rollback. | Maximum share of a redundant group updated per wave [% of group] default 50 (and never all members) (Illustrative.) Soak time between waves [hours] default 24 (Illustrative.) | Compatibility matrix.; Pre-production test records.; Rollout plans and wave records.; Health-gate results. | DOCUMENT_REVIEW; SAMPLING; ANALYSIS; TEST | 1) Obtain matrix and rollout records. 2) Sample rollouts and verify tests and waves. 3) Check redundant-member separation. 4) Review halted rollouts. | PREVENTIVE | EFFECTIVENESS | AL5 | COMMISSION; OPERATE; CHANGE | MAINTENANCE; TRANSITION; NORMAL | Applies to firmware and software updates on in-scope infrastructure. |  | CG-14; CG-08; CG-09 | Firmware rollout common-mode failure (scenario X08); Driver/firmware mismatch causes accelerator errors; UPS firmware breaks EPMS integration | Safeguard; FaultDomain; TestRecord | Facility controller updates require method statement and change approval (MCF-OPS-006/018). | Unknown rollout history for a redundant group is US3. | ISO/IEC/IEEE 12207 (software life cycle processes); SAE EIA-649C (configuration management) | MCF-CMP-014; MCF-CMP-015; MCF-DEP-006; MCF-OPS-020 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-SUP-016 | SUP | Supply Chain, OEM and Ecosystem Assurance | SUP-04 | Software, firmware and update supply | Vulnerability Response | Vulnerabilities disclosed by suppliers for firmware, OT controllers and AI infrastructure components are triaged, and fixes or compensating controls are applied within timescales proportionate to exposure and consequence. | The security owner shall track supplier advisories for in-scope products, triage each against the asset register and exposure (network reachability, privilege required), assign a remediation target based on severity and consequence, and record either patch deployment through change control or a compensating control with approved exception. The security owner shall report remediation performance to the accountable owner. | 1) Supplier advisories for in-scope products are tracked. 2) Each relevant advisory was triaged against the asset register. 3) Remediation targets are set by severity and consequence and met, or exceptions approved. 4) OT and facility controller advisories are included. | Remediation target for critical, exposed vulnerabilities [days] default 14 (Illustrative; OT may require longer with compensating controls.) | Advisory tracking log.; Triage records.; Remediation and exception records. | DOCUMENT_REVIEW; SAMPLING; RECONCILIATION | 1) Obtain log. 2) Compare with public advisories for in-scope products. 3) Sample remediation timing. | CORRECTIVE | OPERATION | AL4 | OPERATE; CHANGE | NORMAL; MAINTENANCE | Applies to in-scope products with supplier advisories. |  | CG-15 | BMC vulnerability unpatched; PLC advisory ignored; Untracked advisory for CDU controller | Threat; Action; AssetInstance | Patching of facility controllers is performed under change control, never under assessment. | No tracking of OT advisories is US3. | ISO/IEC 30111 (vulnerability handling processes); FIRST CVSS; CISA Known Exploited Vulnerabilities catalogue; IEC 62443-2-3 (patch management in the IACS environment) | MCF-SEC-014; MCF-SEC-015; MCF-SUP-007 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-SUP-017 | SUP | Supply Chain, OEM and Ecosystem Assurance | SUP-05 | Spares, logistics and obsolescence | Critical Spares | Spares for critical assets are held in the quantity, location and condition needed to restore Required Functions within tolerance, based on failure behaviour, installed population, repair time and resupply lead time, rather than on habit or warranty terms. | The maintenance manager shall define a spares strategy for each critical asset class (for example UPS modules and capacitors, battery strings, breakers and trip units, protection relays, generator starter motors and controllers, CDU pumps and controllers, chiller compressors and VFDs, transformer bushings or, where justified, a strategic spare transformer, accelerator trays or boards, NICs, optics, switch line cards, storage drives), stating stock level, location (on site, regional, OEM-held), basis (population, failure rate, MTTR target, lead time) and condition-maintenance requirements for stored spares. The maintenance manager shall reconcile stock to records at the profile interval and replenish below-minimum stock as a tracked action. | 1) Spares strategy exists for each critical asset class with stated basis. 2) Stock levels and locations meet strategy; physical count reconciles to records for a sample. 3) Stored spares are maintained in serviceable condition (for example battery shelf charge, transformer storage conditions, firmware level of spare boards). 4) Below-minimum events in the period were replenished or escalated. 5) OEM-held or regional spares are contractually committed with delivery time. | Spares stock review interval [months] default 6 (Illustrative.) Spare-to-installed ratio for accelerator trays [% of installed] default Site-specific (no default) (Derived from observed failure rates, RMA turnaround and the compute availability outcome.) | Spares strategy.; Stock records and reconciliation counts.; Storage condition records.; Replenishment actions.; OEM spares commitments. | DOCUMENT_REVIEW; INSPECTION; RECONCILIATION; SAMPLING; ANALYSIS | 1) Obtain strategy and stock records. 2) Check basis against population and lead times. 3) Count a sample physically. 4) Inspect storage conditions. 5) Review stock-out and replenishment records. | RECOVERY | OPERATION | AL4 | DESIGN; COMMISSION; OPERATE; CHANGE | NORMAL; DEGRADED; RECOVERY | Applies to critical asset classes on a restoration path; non-critical consumables follow normal stores management. |  | CG-10; CG-05; CG-06 | Long-lead spare after rare failure (scenario X12); Spare battery string unusable through self-discharge; Spare boards at incompatible firmware; Stock recorded but not physically present | Resource; AssetInstance; Safeguard | Handling of heavy spares, batteries and pressurised components follows site manual-handling and hazardous-material procedures. | Unknown stock or condition for a spare on a CG-05/06/10 restoration path is US3; US4 where the restoration-time criterion relies on it. | ISO 55001 (asset management systems); IEC 60300-3-11 (reliability centred maintenance); IEEE 1188 (VRLA battery maintenance) — for stored battery spares | MCF-CMP-022; MCF-SUP-018; MCF-DEP-021; MCF-RES-013 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-SUP-018 | SUP | Supply Chain, OEM and Ecosystem Assurance | SUP-05 | Spares, logistics and obsolescence | Lead Times | Lead times for long-lead equipment (power transformers, MV switchgear, generators, UPS systems, chillers and dry coolers, CDUs, accelerator systems, high-speed optics, switch hardware) are known, tracked and compared with recovery and growth needs, so that both failure replacement and planned expansion are realistic. | The procurement lead shall maintain current quoted and observed lead times for each long-lead equipment class, including manufacturing slot reservations and logistics time, and the capability owner shall compare each with (a) the recovery tolerance for loss of an installed unit and (b) the capacity growth schedule, recording each case where lead time exceeds tolerance or schedule with a treatment (strategic spare, slot reservation, framework order, design change) or acceptance. | 1) Lead times are recorded per long-lead class with date and source. 2) Lead times are compared with recovery tolerances. 3) Lead times are compared with the growth schedule, including manufacturing slot reservations. 4) Exceedances have treatments or acceptance. | Lead-time refresh interval [months] default 6 (Illustrative; lead times for electrical equipment can change materially within a year.) | Lead-time register.; Supplier quotations or slot reservations.; Comparison with tolerances and schedule.; Treatment records. | DOCUMENT_REVIEW; ANALYSIS; RECONCILIATION | 1) Obtain register. 2) Reconcile with recent orders. 3) Check comparisons and treatments. | DIRECTIVE | DESIGN | AL2 | PLAN; DESIGN; OPERATE; CHANGE | NORMAL; RECOVERY | Applies to long-lead classes in the boundary. |  | CG-10; CG-03 | Transformer failure with replacement far beyond tolerance; Expansion stranded by switchgear delay (scenario X17); Accelerator delivery slips beyond commitment | Resource; Dependency; CapacityAssertion | Desk-based analysis. | Unknown lead time for a long-lead class on a restoration path is US3. | ISO 55001 (asset management systems); ISO 22318 (guidelines for supply chain continuity) | MCF-SUP-017; MCF-DEP-014; MCF-CAP-015; MCF-SUP-004 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-SUP-019 | SUP | Supply Chain, OEM and Ecosystem Assurance | SUP-05 | Spares, logistics and obsolescence | Logistics Continuity | The logistics and labour needed for recovery and urgent replacement (heavy-haul transport and route permits for transformers and generators, port and customs clearance, cross-border movement under export controls, emergency fuel delivery, and mobilisation of specialist labour such as HV jointers, commissioning engineers, OEM field engineers and liquid-cooling technicians) can be delivered within recovery tolerance under declared regional disruption. | The recovery owner shall identify the logistics and specialist-labour prerequisites for each recovery scenario involving replacement of long-lead equipment or emergency resupply, shall secure them through contracts or pre-arrangements (heavy-haul contractors, route surveys, customs brokers, export licences, fuel priority, labour call-off agreements), and shall validate them by exercise or documented precedent at the profile interval, including under at least one regional-disruption assumption. | 1) Logistics and labour prerequisites are identified per relevant recovery scenario. 2) Pre-arrangements are in place and current. 3) Heavy-haul access to site (route survey, crane and pad locations) is documented for the largest replaceable units. 4) Validation by exercise or precedent within the interval, including a regional-disruption assumption, shows delivery within tolerance or records the gap. 5) Export-control and customs requirements for cross-border spares are pre-cleared where possible. | Logistics continuity validation interval [months] default 24 (Illustrative.) | Prerequisite register per scenario.; Contracts and pre-arrangements.; Route surveys.; Exercise or precedent records. | DOCUMENT_REVIEW; SCENARIO_EXERCISE; INSPECTION; ANALYSIS | 1) Obtain register and arrangements. 2) Inspect heavy-haul access provisions. 3) Review exercise including regional disruption. 4) Compare times to tolerance. | RECOVERY | RESILIENCE | AL5 | PLAN; DESIGN; OPERATE | EMERGENCY; RECOVERY | Applies where recovery scenarios include equipment replacement or emergency resupply. |  | CG-10; CG-05 | No heavy-haul route for replacement transformer; Specialist labour unavailable regionally; Fuel deliveries deprioritised in regional emergency; Spares held at border | Dependency; Resource; FailureScenario; TestRecord | Exercises are tabletop or walkthrough; any physical mobilisation trial (crane, heavy-haul) requires a lift plan and permit under site rules. | Unvalidated logistics for a CG-10 restoration path is US3 for this RESILIENCE claim; US4 where the CG-10 restoration-time criterion depends on it. | ISO 22301 (business continuity management systems); ISO 22318 (guidelines for supply chain continuity); ISO 28000 (supply chain security management) | MCF-SUP-018; MCF-POW-008; MCF-RES-011; MCF-DEP-016 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-SUP-020 | SUP | Supply Chain, OEM and Ecosystem Assurance | SUP-05 | Spares, logistics and obsolescence | End-of-Life Planning | End-of-sale, end-of-support and obsolescence of critical hardware, firmware and control platforms (PLCs, BMS/EPMS controllers and servers, UPS models, protection relays, accelerator generations, switch OS, storage platforms) are anticipated and managed before support or parts cease. | The asset manager shall maintain a lifecycle register recording vendor end-of-sale and end-of-support dates for critical assets, shall review it at the profile interval, and shall ensure each asset reaching end-of-support within the planning horizon has an approved treatment (refresh, last-time buy, extended support, third-party support with compensating controls) recorded before the date. | 1) Lifecycle register covers critical asset classes with vendor dates. 2) Register reviewed at the interval. 3) Assets within the planning horizon have approved treatments. 4) No critical asset is past end-of-support without an approved treatment. | Obsolescence planning horizon [months] default 24 (Illustrative.) | Lifecycle register.; Vendor end-of-life notices.; Treatment approvals. | DOCUMENT_REVIEW; RECONCILIATION; SAMPLING | 1) Obtain register. 2) Verify dates against notices. 3) Check treatments for horizon assets. 4) Identify assets past end-of-support. | PREVENTIVE | OPERATION | AL4 | PLAN; OPERATE; DECOMMISSION | NORMAL | Applies to critical hardware, firmware and control platforms with vendor lifecycle dates; bespoke or in-house items are covered by their own lifecycle plan. |  | CG-03 | BMS controllers unsupported with no spares; Unsupported PLC firmware with known vulnerabilities; Accelerator generation losing driver support | AssetInstance; Resource; Action | Register review only; no end-of-support device shall be taken out of service for assessment. | Unknown support status of a control-system platform is US3. | IEC 62402 (obsolescence management); ISO 55001 (asset management systems) | MCF-DEP-011; MCF-SUP-008; MCF-CAP-024 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-SUP-021 | SUP | Supply Chain, OEM and Ecosystem Assurance | SUP-06 | Remote support and third-party access | Support Identity | Every person from an OEM, integrator, maintenance contractor or managed-service provider who can access facility or AI infrastructure, remotely or on site, is individually identified and authenticated; shared vendor accounts and default credentials do not exist. | The security owner shall require that all third-party support access to BMS/EPMS, CDU and PLC systems, UPS and switchgear management interfaces, BMCs, cluster managers, fabric and storage controllers uses named individual identities, verified by the supplier and registered by the owner, with multi-factor authentication for remote access. Shared, generic and default vendor accounts shall be disabled or, where technically unavoidable, vaulted with per-use checkout bound to a named person and recorded as an exception. | 1) Third-party identities are registered individually with supplier verification. 2) Account exports from in-scope systems show no active shared or default vendor accounts, or only vaulted exceptions. 3) Remote third-party authentication enforces multi-factor authentication. 4) Exceptions list technical reason, compensating control and approver. |  | Third-party identity register.; Account exports from sampled systems.; MFA configuration.; Exception records. | DOCUMENT_REVIEW; INSPECTION; RECONCILIATION; SAMPLING | 1) Obtain register. 2) Export accounts from a sample of systems including facility controllers. 3) Reconcile accounts to named identities. 4) Check MFA and exceptions. | PREVENTIVE | IMPLEMENTATION | AL3 | BUILD; COMMISSION; OPERATE; CHANGE | NORMAL; MAINTENANCE; EMERGENCY; RECOVERY | Applies to every system in the boundary accessible by third parties. | CG-15 | CG-13 | Shared vendor account used across sites; Default credentials on CDU controller; Former contractor credentials active | Interface; Threat; Safeguard | Account exports use read-only methods; no credentials shall be tested by login attempts against production controllers. | Inability to obtain account data from a control-plane system with third-party access is U2, US4 (CG-15 critical). | IEC 62443-2-4 (security requirements for IACS service providers); NIST SP 800-82r3 (OT security); NIST SP 800-53 Rev. 5 (AC and MA control families); ISO/IEC 27001 (information security management systems) | MCF-SEC-001; MCF-SEC-012; MCF-SUP-022; MCF-SUP-024 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-SUP-022 | SUP | Supply Chain, OEM and Ecosystem Assurance | SUP-06 | Remote support and third-party access | Activation and Approval | Third-party remote access to facility and AI infrastructure is off by default and is enabled only for an approved, time-limited, asset-scoped session linked to a work order or change. | The facility operator shall ensure that third-party remote access paths are disabled by default and are activated only on approval by an authorised owner representative, for a stated duration and set of target assets, referencing an approved ticket or change, through a brokered access gateway. Access shall be deactivated automatically at expiry. Emergency activation shall follow a defined path with retrospective review within the profile time. | 1) Remote access paths are disabled by default (configuration evidence). 2) Each session in the sample had prior approval, a ticket or change reference, a time limit and asset scope. 3) Sessions ended at or before expiry. 4) Emergency activations were reviewed retrospectively within the profile time. | Maximum default session duration [hours] default 4 (Illustrative.) Emergency activation review time [hours] default 24 (Illustrative.) | Gateway configuration.; Session approval records.; Session logs with start/end.; Emergency review records. | INSPECTION; SAMPLING; RECONCILIATION; DOCUMENT_REVIEW | 1) Inspect gateway default state. 2) Sample sessions and reconcile to approvals and tickets. 3) Check expiry enforcement. 4) Review emergency activations. | PREVENTIVE | OPERATION | AL4 | COMMISSION; OPERATE; CHANGE | NORMAL; MAINTENANCE; EMERGENCY; RECOVERY | Applies where any third party has remote access to in-scope systems. | CG-15 | CG-14 | Always-on vendor VPN to BMS; Session left open after work; Remote change without ticket | Interface; Safeguard; Event | Observation and log review only. | Missing session logs for a remote path to a control-plane system is U1, US4 (CG-15 critical). | IEC 62443-2-4 (security requirements for IACS service providers); NIST SP 800-82r3 (OT security); NIST SP 800-53 Rev. 5 (AC and MA control families) | MCF-SEC-012; MCF-SUP-021; MCF-SUP-023; MCF-OPS-018 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-SUP-023 | SUP | Supply Chain, OEM and Ecosystem Assurance | SUP-06 | Remote support and third-party access | Session Monitoring | Third-party sessions on control-plane and OT systems are recorded and, for high-consequence systems, monitored in real time by a competent owner representative able to terminate the session. | The security owner shall record all third-party sessions to in-scope control-plane and OT systems (keystroke or screen recording through the access broker where feasible), shall require live monitoring by a competent owner representative for sessions to systems designated high-consequence (for example EPMS switching, BMS/CDU control, protection relay configuration), and shall retain recordings for the profile period. The owner representative shall have and use the means to terminate a session. | 1) Session recording is enabled for in-scope systems. 2) High-consequence sessions in the sample had a named live monitor. 3) Recordings are retained for the period. 4) Termination capability exists and has been exercised or tested. | Session recording retention [days] default 90 (Illustrative.) | Broker recording configuration.; Session monitor records.; Retained recordings.; Termination test or event. | INSPECTION; SAMPLING; OBSERVATION | 1) Inspect broker configuration. 2) Retrieve sample recordings. 3) Check monitor assignment for high-consequence sessions. 4) Review termination evidence. | DETECTIVE | OPERATION | AL4 | OPERATE; CHANGE | NORMAL; MAINTENANCE; EMERGENCY | Applies to third-party sessions on control-plane and OT systems. |  | CG-15 | Unmonitored vendor changes to CDU setpoints; No evidence after incident; Owner unable to terminate session | Event; Safeguard; EvidenceObject | Termination tests use a test session on non-production systems. | No recordings for high-consequence sessions is US3. | IEC 62443-2-4 (security requirements for IACS service providers); NIST SP 800-82r3 (OT security) | MCF-SUP-022; MCF-SEC-017; MCF-SEC-020 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-SUP-024 | SUP | Supply Chain, OEM and Ecosystem Assurance | SUP-06 | Remote support and third-party access | Revocation and Review | Third-party logical and physical access is revoked promptly when no longer needed and is periodically recertified, so that access does not outlive the person, contract or task. | The security owner shall revoke third-party logical access, credentials, tokens and physical badges within the profile time of contract end, personnel departure notified by the supplier, or task completion, and shall recertify all third-party access with the owning system owner at the profile interval, removing any access not positively confirmed. | 1) Revocations in the period met the profile time. 2) Suppliers notify personnel departures (contract obligation and evidence). 3) Recertification occurred at the interval with removals recorded. 4) Sample of current accounts all map to active contracts and people. | Maximum revocation time after notification [hours] default 24 (Illustrative.) Recertification interval [months] default 3 (Illustrative.) | Revocation records with timestamps.; Supplier departure notifications.; Recertification records.; Account sample. | SAMPLING; RECONCILIATION; DOCUMENT_REVIEW | 1) Obtain revocation and recertification records. 2) Sample accounts and badges. 3) Reconcile to active contracts and personnel. | CORRECTIVE | OPERATION | AL4 | OPERATE; DECOMMISSION | NORMAL | Applies to all third-party access. |  | CG-15; CG-13 | Departed contractor badge active; Expired contract vendor account active | Safeguard; Action; Interface | Account and badge reconciliation only; no access shall be revoked or tested by the assessor. | No recertification evidence is US3. | ISO/IEC 27001 (information security management systems); IEC 62443-2-4 (security requirements for IACS service providers) | MCF-SUP-021; MCF-SEC-001; MCF-PHY-013 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-SEC-001 | SEC | Digital, OT and Control-Plane Security | SEC-01 | Identity and privileged access | Human Identity | Ensure every person who can observe, configure or command facility OT, infrastructure management planes or AI control planes is uniquely identified, strongly authenticated and lifecycle-managed, with no shared or orphaned accounts. | The identity and access manager shall ensure that every human identity with access to BMS, EPMS, CDU and PLC engineering workstations and HMIs, BMC/Redfish interfaces, network devices, hypervisor and Kubernetes control planes, cluster managers and storage controllers is individually attributable, uses phishing-resistant multi-factor authentication where the system supports it (with compensating controls recorded where it does not, for example legacy HMIs), and is joined, moved and removed through an authoritative identity source within defined deadlines. The OT security owner shall maintain an inventory of OT systems that cannot integrate with central identity and the compensating controls applied. | 1) All human accounts on in-scope systems map to a named individual in the authoritative identity source; shared accounts are absent or individually approved with session attribution. 2) Phishing-resistant MFA is enforced for remote and privileged access to in-scope systems, with exceptions listed and compensated. 3) Leaver access is removed within the defined deadline (sampled against HR leaver records). 4) Periodic access recertification of in-scope systems occurred at the defined interval. 5) OT systems lacking central identity integration are inventoried with compensating controls (for example jump-host attribution, local account review). 6) Identity services relied upon for infrastructure access have documented fallback for outage (linked to SEC-004). | Leaver access removal deadline [h] default 24 (illustrative) (Capability-profile parameter.) Access recertification interval [months] default 3 for privileged, 6 for standard (illustrative) (Capability-profile parameter.) | Account extracts from in-scope systems reconciled to the identity source; MFA enforcement configuration and exception list; Leaver sample reconciliation; Recertification records; OT identity exception inventory | RECONCILIATION; SAMPLING; DOCUMENT_REVIEW; INSPECTION | 1) Enumerate in-scope systems including OT HMIs and engineering workstations. 2) Extract local and directory-linked accounts from a sample of each class. 3) Reconcile to the identity source and HR records. 4) Verify MFA enforcement and review exceptions. 5) Review recertification and OT exception inventory. | PREVENTIVE | IMPLEMENTATION | AL3 | BUILD; COMMISSION; OPERATE; CHANGE | NORMAL; MAINTENANCE; EMERGENCY | Applies to all human access to in-scope OT, infrastructure management and AI control-plane systems, including contractors and provider staff (with SUP-021 for provider identities). |  | CG-15; CG-07; CG-13 | Shared HMI login preventing attribution; Leaver retaining BMC access; MFA absent on remote engineering access; Orphaned local admin on switches | Safeguard; InfrastructureSystem; Interface | Account extraction shall use read-only methods; no password testing or credential guessing is permitted without written authorisation from the security owner and, for OT, the facility owner. | Systems whose accounts cannot be enumerated are recorded with U2 and their access treated as uncontrolled in authority-path analysis. | NIST SP 800-63 (Digital identity guidelines); FIDO2 / W3C Web Authentication (phishing-resistant authentication); ISA/IEC 62443-3-3 (System security requirements and security levels); NIST SP 800-82 Rev. 3 (Guide to operational technology security); ISO/IEC 27002 (Information security controls) | MCF-SEC-003; MCF-SEC-004; MCF-SUP-021; MCF-PHY-013 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-SEC-002 | SEC | Digital, OT and Control-Plane Security | SEC-01 | Identity and privileged access | Machine Identity | Ensure machine identities (service accounts, API tokens, certificates, workload identities, node and device identities) used by automation, controllers and agents are inventoried, scoped, rotated and, for hardware, anchored in a root of trust with attestation. | The platform security lead shall maintain an inventory of machine identities with access to in-scope infrastructure, including owner, purpose, scope, credential type, rotation interval and expiry, and shall prohibit long-lived static credentials for consequential authority where short-lived or certificate-based credentials are supported. The platform security lead shall require hardware-rooted identity (for example TPM or device identity certificates) and boot or firmware attestation (for example via SPDM or TPM quotes) for accelerator nodes, BMCs and fabric devices that support it, and shall gate cluster admission on successful attestation. | 1) A machine-identity inventory covers service accounts, tokens, certificates and workload identities with owner and scope. 2) Long-lived static credentials with write or command authority are absent or individually approved with rotation. 3) Certificates and tokens are rotated within defined intervals and expiry is monitored. 4) Nodes and devices supporting hardware root of trust present device identity and attestation, and cluster admission rejects failed attestation. 5) Machine identities are scoped to least privilege (sampled). | Maximum static credential lifetime (consequential authority) [days] default 90 (illustrative) (Capability-profile parameter.) Certificate expiry warning window [days] default 30 (illustrative) (Capability-profile parameter.) | Machine-identity inventory; Credential type and rotation evidence; Certificate expiry monitoring; Attestation configuration and admission logs; Scope samples | RECONCILIATION; INSPECTION; SAMPLING; ANALYSIS | 1) Review the inventory and reconcile with secrets stores and target systems. 2) Identify static credentials with consequential authority. 3) Review rotation and expiry monitoring. 4) Review attestation configuration and sample admission logs including rejections. 5) Sample scopes for least privilege. | PREVENTIVE | IMPLEMENTATION | AL3 | DESIGN; BUILD; COMMISSION; OPERATE | NORMAL; MAINTENANCE; RECOVERY | Applies to machine identities with access to in-scope infrastructure. Hardware attestation criteria apply only where devices support it; unsupported classes are listed. |  | CG-15; CG-08 | Hard-coded API token in automation with BMS write access; Expired certificate halting control plane; Tampered node joining cluster without attestation; Over-scoped service account | Safeguard; AssetInstance; Interface | Attestation rejection tests shall use a designated test node; do not alter firmware on production nodes to test rejection. | Credentials discovered on target systems but absent from inventory are Findings; if discovery is not possible, record U5. | Trusted Computing Group TPM 2.0 Library Specification; DMTF DSP0274 (Security Protocol and Data Model, SPDM); IETF RFC 9334 (Remote ATtestation procedureS architecture); NIST SP 800-193 (Platform firmware resiliency guidelines); NIST SP 800-207 (Zero trust architecture) | MCF-SEC-021; MCF-SEC-013; MCF-CMP-021; MCF-SUP-014 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-SEC-003 | SEC | Digital, OT and Control-Plane Security | SEC-01 | Identity and privileged access | Privileged Access | Ensure privileged and consequential authority over facility OT, BMC/Redfish, network, hypervisor/Kubernetes, cluster manager and storage control planes is least-privilege, brokered, time-bound and monitored, so no single compromised identity can command cross-domain infrastructure. | The infrastructure security owner shall define privileged roles by authority action (observe, configure, command, bypass, update, revoke, recover, per AIDCF-005) and by domain, shall prohibit standing cross-domain privileged roles (for example a single role with write access to both BMS/EPMS and cluster control planes) except as approved break-glass, and shall broker privileged sessions through a privileged access management (PAM) system or jump hosts providing just-in-time elevation, session recording and approval for command and bypass actions. The infrastructure security owner shall test at a defined interval that privilege boundaries hold, including that elevation requires approval and that sessions are recorded. | 1) Privileged roles are defined by authority action and domain, with an effective-permission analysis for each. 2) No standing identity holds command or bypass authority across more than one infrastructure domain without approved break-glass status. 3) Privileged access to in-scope systems is brokered with just-in-time elevation and session recording. 4) Command and bypass actions on OT systems require approval or are restricted to authorised operators on site. 5) Tests in the interval confirmed that direct (non-brokered) privileged access is blocked and elevation requires approval. 6) Privileged session logs are reviewed at a defined frequency. | Maximum JIT elevation duration [h] default 4 (illustrative) (Capability-profile parameter.) Privilege boundary test interval [months] default 6 (illustrative) (Capability-profile parameter.) | Privileged role catalogue by authority action and domain; Effective-permission analysis; PAM configuration and session recordings sample; Bypass-path test results; Session review records | ANALYSIS; TEST; SAMPLING; DOCUMENT_REVIEW | 1) Review role catalogue and effective permissions, including group and federation inheritance. 2) Identify identities with cross-domain command or bypass authority. 3) Review PAM configuration and sample session recordings. 4) Review or perform tests of non-brokered access paths. 5) Review session review records. | PREVENTIVE | EFFECTIVENESS | AL5 | DESIGN; COMMISSION; OPERATE; CHANGE | NORMAL; MAINTENANCE; EMERGENCY; RECOVERY | Applies to all privileged access to in-scope OT, infrastructure management and AI control-plane systems. | CG-15 | CG-07 | Domain admin inheriting BMS write rights (control-plane inheritance); Direct SSH to BMCs bypassing PAM; Standing cluster-admin token; Shared management identity across power and cooling | Safeguard; Interface; InfrastructureSystem; TestRecord | Bypass-path tests shall be non-destructive (attempt authentication or connection only, no commands) and require written authorisation from the security owner; tests touching OT systems also require facility owner authorisation and must not issue any write or command. | If effective permissions cannot be computed because of opaque federation or local roles, record U9 at US4 against CG-15. | AIDCF-005 (AIDCF–AI Trust Graph Integration Standard); NIST SP 800-207 (Zero trust architecture); ISA/IEC 62443-3-3 (System security requirements and security levels); NIST SP 800-53 Rev. 5 (Security and privacy controls); NIST SP 800-82 Rev. 3 (Guide to operational technology security) | MCF-SEC-001; MCF-SEC-004; MCF-SEC-010; MCF-SEC-021; MCF-SUP-022 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-SEC-004 | SEC | Digital, OT and Control-Plane Security | SEC-01 | Identity and privileged access | Break-Glass Governance | Ensure emergency accounts and procedures across OT, infrastructure and control planes work when central identity fails, are protected against misuse, and every use is reviewed. | The infrastructure security owner shall govern break-glass arrangements for all in-scope domains: inventory of emergency accounts, storage under dual control with an offline copy outside the failure domains they recover, use triggers, notification on use, maximum duration, mandatory post-use review and credential rotation. The infrastructure security owner shall verify at a defined interval that break-glass retrieval and login work with the primary identity provider and vault unavailable, and shall review all uses. | 1) Break-glass inventory covers OT, BMC, network, hypervisor/Kubernetes, cluster manager and storage domains. 2) Credentials are under dual control with an offline copy located outside recovered failure domains. 3) Use triggers alerts to the security function in real time. 4) Every use in the period was reviewed and followed by rotation within the deadline. 5) Retrieval and login tests with primary identity and vault unavailable succeeded in the interval. | Break-glass rotation after use [h] default 24 (illustrative) (Capability-profile parameter.) | Break-glass inventory and storage arrangements; Alerting configuration; Use, review and rotation records; Retrieval/login test records | DOCUMENT_REVIEW; SAMPLING; TEST; ANALYSIS | 1) Review inventory coverage across domains. 2) Inspect storage and offline copy location against fault domains. 3) Verify alerting on use. 4) Sample uses for review and rotation. 5) Review retrieval test. | CORRECTIVE | OPERATION | AL4 | COMMISSION; OPERATE | EMERGENCY; FAILED; RECOVERY | Applies to all in-scope domains. Network-specific break-glass implementation is NET-016. |  | CG-15; CG-10 | Offline copy stored in the data centre it recovers; Silent break-glass use; Emergency account used as routine admin | Safeguard; Event; Dependency | Retrieval tests shall not disable production identity; simulate unavailability for the test client only, and rotate credentials afterwards. | Domains without a tested break-glass path are recorded with U1 for recovery claims. | NIST SP 800-53 Rev. 5 (Security and privacy controls); ISA/IEC 62443-3-3 (System security requirements and security levels); NIST SP 800-82 Rev. 3 (Guide to operational technology security) | MCF-NET-016; MCF-SEC-003; MCF-RES-013; MCF-SEC-001 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-SEC-005 | SEC | Digital, OT and Control-Plane Security | SEC-02 | Control-plane protection | BMS and EPMS Security | Ensure building management, electrical power monitoring, CDU and PLC/SCADA systems that monitor and command power and cooling are secured to a target security level appropriate to their consequence, so compromise or misuse cannot defeat electrical or thermal continuity. | The OT security owner shall perform a security risk assessment for BMS, EPMS, CDU controllers, PLCs, SCADA servers, historians and engineering workstations using a zone-and-conduit approach consistent with ISA/IEC 62443, assign a target security level (SL-T) to each zone, and implement countermeasures across the foundational requirement areas (identification and authentication, use control, system integrity, data confidentiality, restricted data flow, timely response to events, resource availability). The facility owner shall ensure that safety-instrumented and protection functions (electrical protection relays, emergency shutdown, hardwired interlocks) are independent of BMS/EPMS networks, and the OT security owner shall verify by test that unauthorised write or command attempts against controllers are blocked or detected and that controllers fail to a defined safe state on loss of supervisory communication. | 1) A security risk assessment exists for BMS/EPMS/CDU/PLC assets with zones, conduits and assigned SL-T. 2) Achieved countermeasures are assessed against SL-T for each foundational requirement area, with gaps recorded. 3) Protection relays, emergency shutdown and hardwired interlocks do not depend on BMS/EPMS network availability or integrity. 4) Default credentials are absent and engineering protocols (for example BACnet, Modbus/TCP) are restricted to defined conduits. 5) Tests confirmed that unauthorised write/command attempts from outside permitted conduits are blocked or alarmed. 6) Controllers fail to the defined safe state (for example last good setpoint, mechanical fail-safe position) on loss of supervisory communication, verified by test or vendor-witnessed evidence. 7) Controller logic and firmware changes are detected (checksum or version monitoring). | Target security level for power and cooling control zones [SL (ISA/IEC 62443)] default SL-T 2 minimum; SL-T 3 for zones whose compromise defeats CG-05/CG-06 (illustrative) (Assigned by risk assessment per ISA/IEC 62443-3-2.) Controller logic integrity check interval [days] default 7 (illustrative) (Capability-profile parameter.) | OT security risk assessment with zone/conduit model and SL-T; SL gap assessment against foundational requirements; Independence analysis for protection and safety functions; Credential and protocol configuration evidence; Write/command blocking test results; Fail-safe behaviour test or witnessed vendor evidence; Logic/firmware integrity monitoring records | DOCUMENT_REVIEW; INSPECTION; ANALYSIS; TEST; RECONCILIATION | 1) Review the risk assessment, zone/conduit model and SL-T assignments. 2) Review SL gap assessment by foundational requirement area. 3) Trace protection and safety functions to confirm independence from BMS/EPMS networks. 4) Inspect credential and protocol restrictions on a sample of controllers. 5) Review or witness write/command blocking tests from non-permitted zones. 6) Review fail-safe evidence and logic integrity monitoring. | PREVENTIVE | EFFECTIVENESS | AL5 | DESIGN; COMMISSION; OPERATE; CHANGE | NORMAL; MAINTENANCE; DEGRADED; EMERGENCY | Applies to all BMS, EPMS, CDU, PLC, SCADA, historian and OT engineering systems supporting in-scope power and cooling. Where operated by a colocation provider, evidence rights are required (DEP-018, SUP-006). | CG-07 | CG-15; CG-05; CG-06 | Malicious setpoint change causing cooling loss at load; EPMS compromise masking electrical alarms; Protection logic dependent on BMS network; Default credentials on CDU controller; Controller failing to unsafe state on comms loss | InfrastructureSystem; Safeguard; Threat; FaultDomain; TestRecord | No active scanning, fuzzing, write or command test shall be performed against production BMS/EPMS/CDU/PLC systems without written authorisation from the facility owner and OT security owner, plant in a safe state, operator presence, and vendor consultation; passive monitoring and test-bench testing are preferred. Fail-safe tests that remove supervisory communication require engineering authorisation and a defined restoration plan. | If controller logic integrity or fail-safe state cannot be established, record U8 at US4 against CG-07; do not infer from vendor marketing material. | ISA/IEC 62443-3-2 (Security risk assessment, zones and conduits); ISA/IEC 62443-3-3 (System security requirements and security levels); ISA/IEC 62443-4-2 (Technical security requirements for IACS components); NIST SP 800-82 Rev. 3 (Guide to operational technology security); MITRE ATT&CK for ICS (knowledge base) | MCF-SEC-009; MCF-SEC-023; MCF-POW-021; MCF-THM-021; MCF-THM-022 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-SEC-006 | SEC | Digital, OT and Control-Plane Security | SEC-02 | Control-plane protection | Cluster Manager Security | Ensure the AI control plane (Kubernetes or HPC scheduler, cluster manager, provisioning and image services, hypervisor managers) cannot be used to gain unbounded authority over compute, data and connected infrastructure. | The platform security lead shall harden each cluster manager and control plane to a documented benchmark (for example CIS Kubernetes Benchmark where applicable), restrict API server and scheduler administrative access to brokered privileged paths, enforce admission control that blocks privileged containers, host-namespace access and unapproved images on accelerator nodes, protect control-plane state stores (for example etcd) with encryption and access restriction, and separate tenant-facing from infrastructure-administrative interfaces. The platform security lead shall test at a defined interval that a tenant or workload identity cannot escalate to node, cluster-admin or BMC authority. | 1) Control-plane hardening against a documented benchmark is assessed with deviations recorded. 2) Administrative API access is restricted to brokered privileged paths. 3) Admission control blocks privileged pods, host mounts and unapproved images on accelerator nodes (verified by test). 4) Control-plane state stores are encrypted and access-restricted. 5) Tenant-facing and administrative interfaces are separated. 6) Escalation tests in the interval found no path from tenant workload to node, cluster-admin or BMC authority, or Findings were raised. | Escalation test interval [months] default 12 (illustrative) (Capability-profile parameter.) | Hardening benchmark assessment; API access configuration; Admission policy and rejection logs; State store protection evidence; Escalation test reports | INSPECTION; TEST; DOCUMENT_REVIEW; ANALYSIS | 1) Review hardening assessment and deviations. 2) Inspect administrative access paths. 3) Test admission control with prohibited workload specifications in a test namespace. 4) Review state store protection. 5) Review escalation test reports. | PREVENTIVE | EFFECTIVENESS | AL5 | DESIGN; COMMISSION; OPERATE; CHANGE | NORMAL; MAINTENANCE; RECOVERY | Applies to all cluster managers, schedulers and hypervisor managers controlling in-scope compute. | CG-15 | CG-08 | Privileged container giving node root and BMC reach; Exposed etcd; Cluster-admin token leaked; Unapproved image with tampered drivers | InfrastructureSystem; Safeguard; Threat; TestRecord | Escalation tests shall run in designated test namespaces or clusters under written authorisation; no tests shall modify production workloads or node firmware. | Where the control plane is provider-managed and escalation testing is not permitted, record U2 and require provider assurance (E5). | CIS Kubernetes Benchmark; NIST SP 800-190 (Application container security guide); NIST SP 800-207 (Zero trust architecture) | MCF-SEC-003; MCF-CMP-010; MCF-SEC-002; MCF-SEC-010 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-SEC-007 | SEC | Digital, OT and Control-Plane Security | SEC-02 | Control-plane protection | Fabric Controller Security | Ensure fabric controllers, subnet managers, SDN controllers and network automation platforms are protected so that their compromise cannot reconfigure, partition or blackhole fabrics. | The infrastructure security owner shall ensure fabric controllers, subnet managers and network automation platforms are reachable only from the management zone, use individually attributable and brokered administrative access, authenticate southbound connections to devices (for example certificate-based gNMI/NETCONF), protect fabric security keys (for example InfiniBand management and partition keys), and log all configuration actions to the security telemetry platform. The fabric operations lead shall reconcile controller access configuration to this requirement at a defined interval. | 1) Controllers and automation platforms are reachable only from the management zone (verified). 2) Administrative access is individually attributable and brokered. 3) Southbound device connections are authenticated and encrypted where supported. 4) Fabric security keys are managed and not left at defaults. 5) All configuration actions are logged to security telemetry. |  | Controller network access configuration; Administrative access configuration; Southbound authentication configuration; Key management evidence; Configuration action logs | INSPECTION; RECONCILIATION; DOCUMENT_REVIEW | 1) Inspect network reachability of controllers. 2) Review administrative access and logging. 3) Review southbound authentication and keys. | PREVENTIVE | IMPLEMENTATION | AL3 | COMMISSION; OPERATE; CHANGE | NORMAL; MAINTENANCE | Applies to fabric controllers, subnet managers and network automation affecting in-scope fabrics. Resilience of controllers is NET-021. |  | CG-15; CG-08 | Default management key enabling rogue subnet manager; Automation platform compromised to push malicious config; Unauthenticated southbound sessions | InfrastructureSystem; Safeguard; Interface | Non-intrusive configuration review; do not attempt rogue subnet-manager tests on production fabrics. | If default fabric keys cannot be ruled out, record U7 against fabric integrity. | InfiniBand Trade Association, InfiniBand Architecture Specification (Volumes 1 and 2); OpenConfig gNMI specification and OpenConfig data models; ISA/IEC 62443-3-3 (System security requirements and security levels) | MCF-NET-021; MCF-NET-022; MCF-SEC-010; MCF-SEC-023 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-SEC-008 | SEC | Digital, OT and Control-Plane Security | SEC-02 | Control-plane protection | Storage Controller Security | Ensure storage management planes cannot be used to destroy, encrypt or exfiltrate training data, checkpoints and model artefacts, and that destructive operations require additional protection. | The storage platform owner shall restrict storage controller and management interfaces to the management zone with brokered privileged access, shall require multi-person approval or delayed execution for destructive operations (volume or bucket deletion, snapshot or retention policy reduction, replication break), shall protect immutable recovery copies with retention locks that administrators cannot shorten, and shall log management actions to security telemetry. | 1) Storage management interfaces are reachable only from the management zone. 2) Privileged storage access is brokered and attributable. 3) Destructive operations require multi-person approval or delayed execution. 4) Immutable recovery copies have retention locks not reducible by administrators (verified configuration). 5) Management actions are logged to security telemetry. | Destructive-operation delay [h] default 24 (illustrative) (Capability-profile parameter.) | Storage management access configuration; Destructive-operation approval configuration; Retention lock configuration; Management action logs | INSPECTION; RECONCILIATION; DOCUMENT_REVIEW | 1) Inspect management reachability. 2) Review privileged access. 3) Verify destructive-operation protection. 4) Verify retention locks. 5) Review logging. | PREVENTIVE | IMPLEMENTATION | AL3 | COMMISSION; OPERATE; CHANGE | NORMAL; MAINTENANCE; RECOVERY | Applies to storage platforms holding in-scope training data, checkpoints and model artefacts. |  | CG-15; CG-10; CG-08 | Compromised admin deleting all snapshots; Ransomware encrypting checkpoint tier; Retention lock shortened by admin | InfrastructureSystem; Safeguard; Resource | Do not execute destructive operations to test protections; use a test volume in a non-production namespace. | If immutability cannot be verified, treat recovery copies as mutable (U7) in recovery analysis. | NIST SP 800-53 Rev. 5 (Security and privacy controls); ISO/IEC 27002 (Information security controls) | MCF-STO-016; MCF-STO-013; MCF-RES-016; MCF-SEC-003 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-SEC-009 | SEC | Digital, OT and Control-Plane Security | SEC-03 | Network security and segmentation | Security Zoning | Ensure the facility OT, infrastructure management, AI control-plane, tenant and corporate environments are partitioned into security zones with defined conduits, so that compromise in one zone cannot reach consequential authority in another. | The infrastructure security owner shall maintain a zone-and-conduit model covering facility OT (BMS, EPMS, CDU, PLC, fire and physical security integrations), infrastructure management (BMC, PDU, switch management, OOB), AI control planes, storage management, tenant and corporate networks and external connections, with each conduit's permitted flows, protocols and direction, and the security level target per zone. The OT security owner shall reconcile the as-built network (firewall rules, VLAN/VRF configuration, physical links, wireless and cellular devices) to the model at a defined interval and after change, and shall record every undocumented path (including dual-homed hosts and vendor-installed modems) as a Finding. | 1) A zone-and-conduit model covers all listed environments with permitted flows and SL-T. 2) Firewall, VLAN/VRF and routing configuration reconcile to the model. 3) Dual-homed hosts, unmanaged switches, wireless and cellular devices bridging zones are discovered and dispositioned. 4) Conduits between OT and IT pass through defined boundary devices (for example an industrial DMZ) with no direct routed path. 5) Reconciliation was performed in the interval and after material change. | Zone reconciliation interval [months] default 6 (illustrative) (Capability-profile parameter.) | Zone-and-conduit model; Configuration reconciliation report; Passive discovery results (for example network traffic analysis) for undocumented paths; Disposition of discovered bridging devices | DOCUMENT_REVIEW; RECONCILIATION; ANALYSIS; INSPECTION; OBSERVATION | 1) Review the zone-and-conduit model against the environment inventory. 2) Reconcile firewall, VLAN/VRF and routing configuration to permitted conduits. 3) Review passive discovery for undocumented flows and bridging devices. 4) Inspect a sample of OT cabinets for unmanaged switches and modems. 5) Confirm dispositions of discovered paths. | PREVENTIVE | IMPLEMENTATION | AL3 | DESIGN; BUILD; COMMISSION; OPERATE; CHANGE | NORMAL; MAINTENANCE; EMERGENCY | Applies to all in-scope sites and environments. Physical zoning is PHY-009; this control covers network and logical zones. | CG-07 | CG-15; CG-09 | Vendor cellular modem bridging BMS to internet; Dual-homed historian linking corporate IT and OT; Flat management network spanning BMC and BMS; Unreviewed any-any rule in conduit | FaultDomain; Interface; Safeguard; ArchitectureSnapshot | Discovery in OT zones shall be passive (traffic mirroring) unless active scanning is authorised in writing by the facility owner and OT security owner after vendor consultation; active scans of controllers can disrupt them. | Zones without discovery coverage are recorded with U5 and treated as potentially bridged in authority-path analysis. | ISA/IEC 62443-3-2 (Security risk assessment, zones and conduits); ISA/IEC 62443-3-3 (System security requirements and security levels); NIST SP 800-82 Rev. 3 (Guide to operational technology security); NIST SP 800-207 (Zero trust architecture) | MCF-SEC-010; MCF-SEC-011; MCF-SEC-005; MCF-PHY-009; MCF-NET-013 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-SEC-010 | SEC | Digital, OT and Control-Plane Security | SEC-03 | Network security and segmentation | Management-Plane Segmentation | Ensure management planes (BMC/IPMI/Redfish, switch management, PDU, hypervisor and Kubernetes administrative APIs, storage management) are segmented so that tenant, workload and corporate networks cannot reach them, and so that one management plane cannot be used to pivot to another. | The infrastructure security owner shall segment each management plane into its own zone, shall disable insecure management protocols (for example IPMI over LAN where Redfish is available, unauthenticated SNMP versions, Telnet), shall restrict BMC access to brokered administrative paths, and shall prevent host operating systems from reaching their own or other BMCs over the network except where required and approved. The infrastructure security owner shall test at a defined interval from representative tenant, workload and corporate vantage points that management interfaces are unreachable and that pivoting between management planes is blocked. | 1) Each management plane is a distinct zone with permitted conduits only. 2) Insecure management protocols are disabled on BMCs, switches and PDUs (sampled configuration). 3) Host-to-BMC network access and in-band BMC interfaces are disabled or approved. 4) Reachability tests from tenant, workload and corporate vantage points found no management interface reachable. 5) Pivot tests between management planes (for example BMC zone to OT zone) found paths blocked. | Management segmentation test interval [months] default 6 (illustrative) (Capability-profile parameter.) | Management zone design; Protocol configuration samples; Reachability and pivot test reports | TEST; INSPECTION; ANALYSIS | 1) Review management zone design. 2) Sample protocol configuration on BMCs, switches and PDUs. 3) Run or review reachability tests from tenant, workload and corporate vantage points. 4) Run or review pivot tests between management planes. | PREVENTIVE | EFFECTIVENESS | AL5 | DESIGN; COMMISSION; OPERATE; CHANGE | NORMAL; MAINTENANCE; RECOVERY | Applies to all management planes of in-scope infrastructure. | CG-15 | CG-07 | Tenant workload reaching BMCs and reflashing firmware; IPMI cipher weaknesses exploited; Pivot from BMC zone to BMS; PDU web interface reachable from corporate network | FaultDomain; Interface; Safeguard; TestRecord | Reachability and pivot tests shall attempt connection only and shall not authenticate or issue commands; they require written authorisation from the security owner, and from the facility owner for any test touching OT zones. | Vantage points not tested are recorded with U5; untested pairs of management planes are treated as connected. | DMTF DSP0266 (Redfish specification); ISA/IEC 62443-3-3 (System security requirements and security levels); NIST SP 800-53 Rev. 5 (Security and privacy controls); NIST SP 800-207 (Zero trust architecture) | MCF-NET-013; MCF-SEC-009; MCF-SEC-003; MCF-SEC-011 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-SEC-011 | SEC | Digital, OT and Control-Plane Security | SEC-03 | Network security and segmentation | Filtering and Gateways | Ensure conduits between zones are enforced by managed boundary devices whose rule sets are minimal, reviewed and monitored, including industrial DMZs, unidirectional gateways and API gateways for automation. | The security operations manager shall operate boundary devices on every conduit in the zone model with deny-by-default rule sets, documented business justification and owner for each rule, review of rules at a defined interval, removal of unused rules, and logging of denied and permitted consequential flows to security telemetry. The OT security owner shall use unidirectional or protocol-break gateways where the zone model requires one-way data export from power and cooling control zones. | 1) Every conduit is enforced by a managed boundary device with deny-by-default. 2) Each rule has justification and owner; any-any or overly broad rules are absent or approved. 3) Rule reviews occurred in the interval with unused rules removed. 4) Required unidirectional or protocol-break gateways are deployed for OT data export. 5) Boundary logs are forwarded to security telemetry. | Rule review interval [months] default 6 (illustrative) (Capability-profile parameter.) | Boundary device inventory mapped to conduits; Rule sets with justification; Rule review records; Gateway deployment evidence; Log forwarding configuration | ANALYSIS; DOCUMENT_REVIEW; SAMPLING | 1) Map boundary devices to conduits. 2) Analyse rule sets for breadth and justification. 3) Review rule review records. 4) Verify gateways for OT export. 5) Check log forwarding. | PREVENTIVE | OPERATION | AL4 | COMMISSION; OPERATE; CHANGE | NORMAL; MAINTENANCE | Applies to every conduit in the SEC-009 model. |  | CG-07; CG-15 | Temporary vendor rule left open; Bidirectional path where one-way export intended; Rule sprawl hiding consequential paths | Safeguard; Interface; AssetInstance | Rule analysis is offline; any active validation follows SEC-010 testing restrictions. | Conduits without an identified enforcing device are treated as open (U1). | ISA/IEC 62443-3-3 (System security requirements and security levels); NIST SP 800-82 Rev. 3 (Guide to operational technology security); NIST SP 800-53 Rev. 5 (Security and privacy controls) | MCF-SEC-009; MCF-SEC-010; MCF-NET-011; MCF-SEC-017 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-SEC-012 | SEC | Digital, OT and Control-Plane Security | SEC-03 | Network security and segmentation | Remote Access | Ensure all remote access to OT, infrastructure management and AI control planes, especially by vendors and OEMs, is brokered, approved per session, time-bound, monitored and revocable. | The infrastructure security owner shall permit remote access to in-scope systems only through a managed remote-access gateway that enforces individual identity, MFA, per-session approval by the system owner for vendor and OEM access, time limits, session recording and the ability to terminate sessions in real time, and shall prohibit persistent vendor connections, vendor-installed remote-access tools and modems. The OT security owner shall require that remote sessions to power and cooling control systems with write or command capability are supervised by an on-site or on-shift authorised operator. | 1) All remote access paths to in-scope systems traverse the managed gateway (no alternative paths found in discovery). 2) Vendor/OEM sessions require per-session approval and are time-limited. 3) Sessions are recorded and can be terminated in real time (demonstrated). 4) Persistent vendor connections and unmanaged remote tools are absent. 5) Remote write/command sessions to OT systems were supervised (sampled). 6) Revocation of a vendor's access takes effect within the defined time (tested). | Maximum vendor session duration [h] default 8 (illustrative) (Capability-profile parameter.) Revocation effect time [min] default 15 (illustrative) (Capability-profile parameter.) | Remote access architecture; Gateway configuration; Session approval and recording samples; Discovery results for alternative paths; Revocation test record | TEST; SAMPLING; INSPECTION; ANALYSIS | 1) Review remote access architecture. 2) Review discovery results for alternative paths and vendor tools. 3) Sample sessions for approval, recording and supervision. 4) Witness real-time termination and revocation test. | PREVENTIVE | EFFECTIVENESS | AL5 | COMMISSION; OPERATE; CHANGE | NORMAL; MAINTENANCE; EMERGENCY | Applies to all remote access to in-scope OT, management and control-plane systems. Supplier-side identity and contractual obligations are SUP-021 to SUP-024. | CG-15 | CG-07 | Always-on OEM VPN to BMS; Vendor remote tool installed on HMI; Compromised vendor account issuing commands; Session not terminable | Interface; Safeguard; Dependency; TestRecord | Revocation tests shall use a designated test vendor account; do not terminate live vendor sessions supporting active work without coordinating with the system owner. | If discovery has not covered all OT zones, record U5 at US4 against CG-15. | ISA/IEC 62443-2-4 (Security programme requirements for IACS service providers); ISA/IEC 62443-3-3 (System security requirements and security levels); NIST SP 800-82 Rev. 3 (Guide to operational technology security); NIST SP 800-207 (Zero trust architecture) | MCF-SUP-021; MCF-SUP-022; MCF-SUP-023; MCF-SUP-024; MCF-SEC-003 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-SEC-013 | SEC | Digital, OT and Control-Plane Security | SEC-04 | Configuration, vulnerability and patching | Secure Baseline | Ensure OT controllers, BMCs, accelerator nodes, NICs, switches and control-plane hosts run hardened configurations and integrity-verified firmware with secure boot, so that tampered or insecure states are prevented or detected. | The infrastructure security owner shall define secure configuration baselines for each in-scope device class, including disabled unused services, credential policy, logging, and for firmware-bearing devices the approved signed firmware versions, secure boot enablement, firmware rollback protection and measured boot where supported. The platform security lead shall verify compliance with the baseline at a defined interval using automated assessment or attestation and shall record non-compliant devices as Findings. | 1) Secure baselines exist for each device class including firmware and boot-integrity settings. 2) Secure boot is enabled on devices that support it (sampled or attested). 3) Firmware versions match approved signed versions; unsigned or unknown firmware is absent. 4) Firmware rollback protection is enabled where supported. 5) Compliance assessment ran in the interval with non-compliance tracked. | Baseline compliance assessment interval [days] default 30 (illustrative) (Capability-profile parameter.) Baseline compliance target [% devices compliant] default 98 (illustrative) (Capability-profile parameter.) | Secure baselines per device class; Compliance assessment reports; Firmware inventory with signature status; Secure boot and attestation evidence | INSPECTION; REPERFORMANCE; SAMPLING; DOCUMENT_REVIEW | 1) Review baselines per device class. 2) Review compliance reports and reperform on sample. 3) Check firmware signature status and secure boot. 4) Review non-compliance tracking. | PREVENTIVE | IMPLEMENTATION | AL3 | DESIGN; BUILD; COMMISSION; OPERATE | NORMAL; MAINTENANCE; RECOVERY | Applies to all in-scope device classes. |  | CG-07; CG-15; CG-08 | Secure boot disabled on accelerator nodes; Unsigned BMC firmware; Firmware downgrade to vulnerable version; Insecure services enabled on controllers | ArchitectureSnapshot; Safeguard; AssetInstance | Compliance checks shall be read-only; firmware updates are not part of this control. | Devices whose firmware cannot be read are treated as non-compliant (U1). | NIST SP 800-193 (Platform firmware resiliency guidelines); Trusted Computing Group TPM 2.0 Library Specification; DMTF DSP0274 (Security Protocol and Data Model, SPDM); ISA/IEC 62443-4-2 (Technical security requirements for IACS components); NIST SP 800-53 Rev. 5 (Security and privacy controls) | MCF-CMP-013; MCF-SUP-014; MCF-NET-022; MCF-SEC-002 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-SEC-014 | SEC | Digital, OT and Control-Plane Security | SEC-04 | Configuration, vulnerability and patching | Vulnerability Management | Ensure vulnerabilities in OT, infrastructure management, firmware and AI control-plane components are identified, prioritised by exploitability and infrastructure consequence, and remediated or mitigated within defined times. | The security operations manager shall maintain vulnerability visibility for all in-scope asset classes (including passive or vendor-advisory-based identification for OT assets that cannot be actively scanned), shall prioritise using exploitation evidence (for example known-exploited catalogues) and infrastructure consequence (reachability to CG-05/CG-06/CG-07/CG-15 authority), and shall meet remediation or mitigation times defined per priority. The security operations manager shall report overdue items to governance. | 1) Vulnerability identification covers all in-scope asset classes with method stated (scan, agent, passive, advisory). 2) Prioritisation considers exploitation evidence and infrastructure consequence. 3) Remediation or mitigation times are met per priority (sampled). 4) Overdue items are reported and have exceptions (SEC-016). 5) OT vendor advisories are monitored and assessed. | Remediation time for known-exploited vulnerabilities on reachable management planes [days] default 14 (illustrative) (Capability-profile parameter.) | Coverage report by asset class; Prioritisation method; Remediation SLA reports; Overdue reports; Advisory monitoring records | ANALYSIS; SAMPLING; DOCUMENT_REVIEW | 1) Compare coverage with asset inventory. 2) Review prioritisation method. 3) Sample vulnerabilities for SLA adherence. 4) Review advisory monitoring. | DETECTIVE | OPERATION | AL4 | OPERATE | NORMAL; MAINTENANCE | Applies to all in-scope assets. |  | CG-07; CG-15 | Exploitable BMC vulnerability unpatched; OT asset blind spot; Prioritisation ignoring consequence | Threat; AssetInstance; Finding | Active scanning of OT assets is prohibited unless authorised in writing by the facility owner after vendor consultation; prefer passive identification. | Assets without any identification method are recorded with U5. | NIST SP 800-40 Rev. 4 (Guide to enterprise patch management planning); CISA Known Exploited Vulnerabilities catalogue; IEC TR 62443-2-3 (Patch management in the IACS environment); NIST SP 800-82 Rev. 3 (Guide to operational technology security) | MCF-SEC-015; MCF-SEC-016; MCF-SUP-016 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-SEC-015 | SEC | Digital, OT and Control-Plane Security | SEC-04 | Configuration, vulnerability and patching | Patch Governance | Ensure security patches and firmware updates to OT and infrastructure are tested for compatibility and operational impact, staged to avoid common-mode failure, and applied within defined times. | The change authority shall require that patches and firmware updates to OT controllers, BMCs, NICs, switches, accelerator nodes and control planes are tested on representative test systems, approved by the system owner and, for OT, the vendor where required, applied in stages that never update all redundant members or all fault domains simultaneously, and verified after application with rollback available. The security operations manager shall measure patch latency against defined targets. | 1) Patches are tested on representative test systems before production. 2) OT patches have vendor compatibility confirmation where required. 3) Staging prevents simultaneous update of all redundant members or fault domains. 4) Post-patch verification and rollback availability are recorded. 5) Patch latency meets targets or exceptions exist. | Maximum fraction of a redundancy group patched in one stage [%] default 50 (illustrative) (Avoids common-mode failure (X08).) | Patch test records; Vendor compatibility confirmations; Staged change records; Post-patch verification; Patch latency reports | SAMPLING; DOCUMENT_REVIEW; RECONCILIATION | 1) Identify version changes from inventories. 2) Trace to test, approval and staging records. 3) Check redundancy-group staging. 4) Review latency. | PREVENTIVE | OPERATION | AL4 | OPERATE; CHANGE | MAINTENANCE; TRANSITION; NORMAL | Applies to all patching of in-scope assets. |  | CG-14; CG-07 | Firmware update bricking all CDU controllers; Patch applied to both PLC redundant pair; Untested BMC update breaking node boot | Action; AssetInstance; TestRecord | Patch testing shall be on test systems; production pilots follow change control. | Version changes without matching records are Findings. | IEC TR 62443-2-3 (Patch management in the IACS environment); NIST SP 800-40 Rev. 4 (Guide to enterprise patch management planning); NIST SP 800-82 Rev. 3 (Guide to operational technology security) | MCF-SEC-014; MCF-CMP-015; MCF-NET-022; MCF-OPS-018 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-SEC-016 | SEC | Digital, OT and Control-Plane Security | SEC-04 | Configuration, vulnerability and patching | Exception and Compensating Control | Ensure security exceptions (unpatchable OT, legacy protocols, missing MFA) are approved by appropriate authority, time-bound and backed by verified compensating controls. | The infrastructure security owner shall maintain a security exception register for in-scope systems recording the deviation, risk assessment including infrastructure consequence, compensating controls, approver at the authority level required by consequence, and expiry. The infrastructure security owner shall verify compensating controls are in place before approval and at renewal. | 1) All known deviations are in the register. 2) Approvals match the required authority for the consequence. 3) Compensating controls were verified before approval and at renewal. 4) No exceptions are expired without renewal. | Maximum exception duration [months] default 12 (illustrative) (Capability-profile parameter.) | Exception register; Approval records; Compensating-control verification records | DOCUMENT_REVIEW; RECONCILIATION; INSPECTION | 1) Reconcile deviations to the register. 2) Check approval authority. 3) Inspect compensating controls for a sample. 4) Check expiries. | DIRECTIVE | OPERATION | AL4 | OPERATE; CHANGE | NORMAL; MAINTENANCE | Applies to all in-scope security deviations. |  | CG-07; CG-15 | Indefinite exception for legacy HMI; Compensating control never implemented; Approver lacking authority | Finding; Safeguard; Control | Inspection only. | Deviations not in the register are Findings; compensating controls not verified are recorded as U1. | ISO/IEC 27001 (Information security management systems); ISA/IEC 62443-2-1 (Security programme requirements for IACS asset owners) | MCF-GOV-011; MCF-SEC-013; MCF-SEC-014 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-SEC-017 | SEC | Digital, OT and Control-Plane Security | SEC-05 | Detection and response | Security Telemetry | Ensure security-relevant logs and events from OT, management planes, control planes, remote access and identity systems are collected centrally with integrity, time synchronisation and retention sufficient for detection and investigation. | The security operations manager shall collect security telemetry from identity providers, PAM, remote-access gateways, boundary devices, BMCs, network devices, fabric controllers, cluster managers, storage controllers and OT passive monitoring (including controller write and program-change events), with time synchronised to NET-024 sources, integrity protection, and retention per the evidence retention class, and shall monitor source health and alert on silent sources. | 1) Telemetry sources cover all listed classes with gaps recorded. 2) OT passive monitoring captures controller write and program-change events. 3) Timestamps are synchronised and offsets monitored. 4) Logs are integrity-protected and retained per class. 5) Silent-source alerts operate and gaps are investigated. | Silent-source alert threshold [min] default 60 (illustrative) (Capability-profile parameter.) | Source coverage report; OT monitoring coverage; Time synchronisation evidence; Integrity and retention configuration; Source health alerts | ANALYSIS; SAMPLING; INSPECTION | 1) Compare sources to inventory. 2) Query sample events from each class. 3) Check time offset and integrity. 4) Review silent-source alerts. | DETECTIVE | OPERATION | AL4 | COMMISSION; OPERATE | NORMAL; MAINTENANCE; EMERGENCY; RECOVERY | Applies to all in-scope security-relevant systems. |  | CG-15; CG-07 | BMC logs not collected; OT program change invisible; Logs alterable by attacker; Silent source unnoticed | EvidenceObject; Safeguard; Event | Passive OT monitoring via traffic mirroring only. | Source classes without collection are recorded with U5. | NIST SP 800-92 (Guide to computer security log management); NIST SP 800-82 Rev. 3 (Guide to operational technology security); ISA/IEC 62443-3-3 (System security requirements and security levels) | MCF-SEC-018; MCF-NET-023; MCF-NET-024; MCF-EVA-006 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-SEC-018 | SEC | Digital, OT and Control-Plane Security | SEC-05 | Detection and response | Behaviour Detection | Ensure detection of anomalous or malicious behaviour against infrastructure authority, including unexpected OT writes, BMC firmware operations, mass configuration changes, privilege escalation and anomalous automation actions. | The security operations manager shall maintain detection use cases mapped to infrastructure threat scenarios (for example ATT&CK for ICS techniques and AIDCF-004 scenarios X05, X08, X15), covering unexpected controller writes or program changes, BMC firmware update or power commands outside change windows, mass configuration pushes, privilege escalation, anomalous remote sessions and automation acting outside its scope, and shall validate detection effectiveness by safe simulation at a defined interval. | 1) Detection use cases map to listed infrastructure scenarios. 2) Use cases cover OT writes, BMC operations, mass config, privilege escalation, remote sessions and automation scope violations. 3) Simulations in the interval demonstrated detection and alert triage within target time. 4) Missed detections were remediated. | Detection-to-triage target [min] default 15 (illustrative) (Capability-profile parameter.) Detection validation interval [months] default 6 (illustrative) (Capability-profile parameter.) | Use case catalogue with mapping; Simulation records and results; Remediation records | TEST; DOCUMENT_REVIEW; ANALYSIS | 1) Review use case mapping. 2) Review or witness simulations. 3) Measure detection-to-triage times. 4) Review remediation of misses. | DETECTIVE | EFFECTIVENESS | AL5 | OPERATE | NORMAL; MAINTENANCE; EMERGENCY | Applies to all in-scope infrastructure authority. |  | CG-15; CG-07 | Unexpected setpoint write undetected; Mass firmware push unnoticed; Agent acting outside scope undetected | Safeguard; Threat; TestRecord | Simulations on OT shall replay benign traffic or use test benches; never issue real writes to production controllers. Simulations require written authorisation from the security owner and facility owner. | Use cases never validated are recorded with U8. | MITRE ATT&CK for ICS (knowledge base); NIST SP 800-61 Rev. 3 (Incident response recommendations); NIST SP 800-82 Rev. 3 (Guide to operational technology security) | MCF-SEC-017; MCF-SEC-019; MCF-SEC-021 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-SEC-019 | SEC | Digital, OT and Control-Plane Security | SEC-05 | Detection and response | Incident Containment | Ensure cyber and cyber-physical incidents affecting infrastructure can be contained without causing unsafe states or unnecessary loss of AI service, with pre-approved containment actions and safety-coordinated decision-making. | The security operations manager shall maintain incident playbooks for infrastructure scenarios (BMS/EPMS compromise, BMC compromise, control-plane compromise, malicious automation, vendor account compromise) that define pre-approved containment actions (credential revocation, conduit closure, session termination, controller isolation to local or manual control), the safety checks required before each action, and the decision authority. The facility owner shall ensure that OT containment actions are coordinated with facility operations so that isolating supervisory control does not remove cooling or power continuity, and the security operations manager shall exercise the playbooks at a defined interval. | 1) Playbooks exist for each listed scenario with containment actions, safety checks and authority. 2) OT containment actions specify the safe fallback (local/manual control, last-good setpoints) and facility operations role. 3) Containment actions are technically available (for example conduit closure capability verified). 4) Exercises in the interval executed containment decisions and actions (or simulations) within target time. 5) Containment does not depend on systems likely to be compromised in the scenario. | Containment decision time target [min] default 30 (illustrative) (Capability-profile parameter.) Playbook exercise interval [months] default 12 (illustrative) (Capability-profile parameter.) | Infrastructure incident playbooks; Safe fallback definitions; Containment capability verification; Exercise records | DOCUMENT_REVIEW; SCENARIO_EXERCISE; TEST; INQUIRY | 1) Review playbooks for scenarios, actions, safety checks and authority. 2) Review safe fallback definitions with facility operations. 3) Verify containment capability. 4) Review exercise records. 5) Check dependencies of containment actions. | CORRECTIVE | RESILIENCE | AL5 | PLAN; OPERATE | EMERGENCY; DEGRADED; RECOVERY | Applies to all in-scope infrastructure. |  | CG-09; CG-15; CG-07; CG-10 | Isolating BMS causes cooling loss; Containment relies on compromised identity provider; No authority to sever vendor access; Delayed decision allows spread | Safeguard; Action; FailureScenario | Containment exercises on OT shall be simulations or tabletop unless live isolation to local control is authorised by the facility owner with operators in attendance and plant in a stable state. | Scenarios without an exercised playbook are recorded with U1. | NIST SP 800-61 Rev. 3 (Incident response recommendations); NIST SP 800-82 Rev. 3 (Guide to operational technology security); ISA/IEC 62443-2-1 (Security programme requirements for IACS asset owners) | MCF-RES-019; MCF-RES-021; MCF-SEC-018; MCF-SEC-020; MCF-OPS-014 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-SEC-020 | SEC | Digital, OT and Control-Plane Security | SEC-05 | Detection and response | Forensic Readiness | Ensure that evidence needed to investigate infrastructure incidents (logs, controller programs, firmware images, session recordings) is preserved with chain of custody and that collection does not endanger operations. | The security operations manager shall define forensic collection procedures for each in-scope system class, including OT controllers and BMCs, specifying what to collect, how to collect safely, and chain-of-custody requirements, and shall ensure retention and legal hold capability for telemetry and session recordings. The OT security owner shall ensure baseline copies of controller programs and firmware hashes are available for comparison. | 1) Collection procedures exist per system class including OT and BMC. 2) Procedures specify safe collection methods. 3) Chain-of-custody and legal hold capability exist. 4) Baseline controller programs and firmware hashes are available. |  | Forensic procedures; Chain-of-custody templates and tooling; Legal hold capability evidence; Baseline program and hash repository | DOCUMENT_REVIEW; INSPECTION | 1) Review procedures per class. 2) Inspect chain-of-custody tooling and legal hold. 3) Verify baseline repository contents for a sample. | DETECTIVE | IMPLEMENTATION | AL3 | PLAN; OPERATE | EMERGENCY; RECOVERY | Applies to all in-scope system classes. |  | CG-15 | Evidence destroyed during recovery; Unsafe collection disrupting controller; No baseline to detect logic tampering | EvidenceObject; Safeguard | Forensic collection from OT controllers shall use vendor-supported read methods only. | Classes without collection procedures are recorded with U1. | NIST SP 800-86 (Guide to integrating forensic techniques into incident response); NIST SP 800-61 Rev. 3 (Incident response recommendations); NIST SP 800-82 Rev. 3 (Guide to operational technology security) | MCF-SEC-017; MCF-EVA-006; MCF-SEC-019 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-SEC-021 | SEC | Digital, OT and Control-Plane Security | SEC-06 | AI-enabled and automated action | Agent or Automation Authority | Ensure every AI agent, automation pipeline and closed-loop controller that can act on infrastructure has an explicit, bounded and inventoried authority scope, so that tool-mediated actions cannot exceed what the owner approved. | The automation owner shall register every agent, automation and closed-loop control that can observe, configure, command, bypass, update or recover infrastructure (including AIOps remediation, cooling optimisation loops, power capping, network automation and AI agents with tool access), stating its effective identity, tools and APIs, target systems, permitted actions, rate and magnitude limits, operating states in which it may act, and its human owner. The infrastructure security owner shall reconcile registered scope with effective permissions at a defined interval and shall prohibit any automation from holding cross-domain command or bypass authority without approval under SEC-003. | 1) All automations and agents with infrastructure authority are registered with identity, tools, targets, actions, limits, states and owner. 2) Effective permissions reconcile to registered scope (no excess). 3) Rate and magnitude limits (for example maximum setpoint change, maximum nodes acted on) are enforced technically. 4) Automation is restricted to declared operating states (for example disabled in EMERGENCY unless approved). 5) No automation holds unapproved cross-domain command or bypass authority. 6) Telemetry-to-command coupling is analysed for sensor-trust dependency (AIDCF-005 pattern). | Maximum automated setpoint change per interval [units per min] default System-specific (illustrative: 1 °C per 5 min for supply temperature) (Capability-profile parameter set by engineering authority.) Maximum nodes acted on per automated action [count] default Fault-domain size (illustrative) (Limits blast radius.) | Automation and agent authority register; Effective permission reconciliation; Limit enforcement configuration; State restriction configuration; Telemetry-to-command analysis | RECONCILIATION; ANALYSIS; INSPECTION; DOCUMENT_REVIEW | 1) Discover automations and agents from identity, API gateway and controller logs. 2) Compare with the register. 3) Compute effective permissions and reconcile to scope. 4) Inspect technical limit and state enforcement. 5) Review telemetry-to-command analysis. | DIRECTIVE | IMPLEMENTATION | AL3 | DESIGN; COMMISSION; OPERATE; CHANGE | NORMAL; DEGRADED; MAINTENANCE; EMERGENCY | Applies to every automated or AI-enabled actor with any authority beyond OBSERVE over in-scope infrastructure. | CG-15 | CG-07 | AIOps agent with power-cycle rights over all nodes; Cooling optimiser driven by spoofed sensors; Agent inheriting operator's full privileges; Automation acting during EMERGENCY | Safeguard; Interface; Dependency; InfrastructureSystem | Reconciliation is read-only; do not invoke agent tools against production systems to test scope. | Automations discovered in logs but not registered are recorded as US4 UNKNOWN (U1) against CG-15 until registered and reconciled. | AIDCF-005 (AIDCF–AI Trust Graph Integration Standard); NIST AI 100-1 (AI Risk Management Framework); OWASP Top 10 for Large Language Model Applications; NIST SP 800-207 (Zero trust architecture) | MCF-SEC-022; MCF-SEC-023; MCF-SEC-024; MCF-SEC-002; MCF-THM-021 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-SEC-022 | SEC | Digital, OT and Control-Plane Security | SEC-06 | AI-enabled and automated action | Approval Controls | Ensure consequential automated or agent-initiated infrastructure actions require human approval proportionate to consequence, and that approvals cannot be bypassed. | The automation owner shall classify each automated action by consequence and reversibility and shall require human approval (single or dual) for actions above the defined threshold, such as OT setpoint or mode changes beyond limits, power-cycling beyond one fault domain, firmware updates, fabric-wide configuration pushes and destructive storage operations. The infrastructure security owner shall verify by test that approval cannot be bypassed by the automation's own identity. | 1) Actions are classified by consequence and reversibility. 2) Approval requirements are defined per class. 3) Approval enforcement is technical, outside the automation's control. 4) Tests confirmed approval cannot be bypassed. 5) Approval records exist for sampled consequential actions. |  | Action classification; Approval configuration; Bypass test results; Approval records | TEST; SAMPLING; DOCUMENT_REVIEW | 1) Review classification. 2) Inspect approval enforcement architecture. 3) Review or witness bypass tests in a test environment. 4) Sample approval records. | PREVENTIVE | EFFECTIVENESS | AL5 | DESIGN; OPERATE; CHANGE | NORMAL; MAINTENANCE; EMERGENCY | Applies to automation and agents registered under SEC-021 whose actions are classified above the lowest consequence class. |  | CG-15; CG-14 | Agent self-approves; Approval fatigue rubber-stamping; Approval enforced only in prompt instructions | Safeguard; Action; TestRecord | Bypass tests in test environment only. | Approvals enforced only by agent instructions or prompts are treated as absent (U8). | AIDCF-005 (AIDCF–AI Trust Graph Integration Standard); NIST AI 100-1 (AI Risk Management Framework); OWASP Top 10 for Large Language Model Applications | MCF-SEC-021; MCF-SEC-023; MCF-RES-023 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-SEC-023 | SEC | Digital, OT and Control-Plane Security | SEC-06 | AI-enabled and automated action | Command Allowlisting | Ensure that only explicitly allowlisted commands, write operations and parameter ranges can be issued to power, cooling and critical infrastructure controllers by any automated or remote actor, enforced at a point the actor cannot modify. | The OT security owner shall enforce, at a boundary or broker the actor cannot modify (for example an OT protocol-aware gateway, a command broker or controller-level write protection), an allowlist of permitted commands, registers or objects, and parameter ranges for writes to BMS, EPMS, CDU and PLC systems from automation, agents and remote sessions, and shall block or require approval for anything outside the list. The OT security owner shall test at a defined interval that out-of-list writes and out-of-range values are blocked and alarmed. | 1) Allowlists exist for each automation/remote actor writing to OT systems, covering commands, objects and ranges. 2) Enforcement is at a point outside the actor's control. 3) Out-of-list and out-of-range attempts are blocked and alarmed (test results). 4) Allowlists are reviewed with engineering authority after control-logic changes. 5) Controller-level write protection (for example key switch or run mode) is used where supported. | Allowlist test interval [months] default 6 (illustrative) (Capability-profile parameter.) | Allowlist definitions; Enforcement architecture; Test results; Review records | TEST; INSPECTION; DOCUMENT_REVIEW | 1) Review allowlists per actor. 2) Inspect enforcement point. 3) Review or witness block tests on test bench or under authorisation. 4) Review allowlist reviews after logic changes. | PREVENTIVE | EFFECTIVENESS | AL5 | DESIGN; COMMISSION; OPERATE; CHANGE | NORMAL; MAINTENANCE; EMERGENCY | Applies wherever automation, agents or remote sessions can write to in-scope OT controllers. | CG-07 | CG-15 | Agent writing unsafe CDU flow setpoint; Remote session changing protection mode; Malicious write to chiller sequencing | Safeguard; Interface; TestRecord | Block tests against production controllers shall use benign out-of-list requests that the gateway intercepts, with operator presence and facility owner authorisation; test benches are preferred. | If enforcement sits within the actor's own software, record U8 and treat writes as unrestricted. | ISA/IEC 62443-3-3 (System security requirements and security levels); NIST SP 800-82 Rev. 3 (Guide to operational technology security); AIDCF-005 (AIDCF–AI Trust Graph Integration Standard) | MCF-SEC-005; MCF-SEC-021; MCF-SEC-022; MCF-THM-021 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-SEC-024 | SEC | Digital, OT and Control-Plane Security | SEC-06 | AI-enabled and automated action | Safe Rollback | Ensure automated or agent-initiated infrastructure changes can be detected, halted and reversed to a known-safe state quickly, including when the automation itself has failed or been compromised. | The automation owner shall provide, for every registered automation and agent, a kill switch that halts its actions without depending on the automation itself, a record of actions taken sufficient to reverse them, and a defined safe state (for example last approved setpoints, previous configuration) for each target. The automation owner shall test at a defined interval that the kill switch halts actions within target time and that rollback restores the safe state, coordinating OT rollback with facility operations. | 1) Every registered automation has an independent kill switch. 2) Action logs are sufficient for reversal. 3) Safe states are defined per target. 4) Tests in the interval demonstrated halt within target time and rollback to safe state. 5) OT rollback procedures are coordinated with facility operations. | Kill-switch halt time [s] default 60 (illustrative) (Capability-profile parameter.) | Kill switch design; Action logs; Safe state definitions; Halt and rollback test records | TEST; DOCUMENT_REVIEW; SCENARIO_EXERCISE | 1) Review kill switch independence. 2) Review action log completeness. 3) Review safe state definitions. 4) Review or witness halt and rollback tests. | RECOVERY | RESILIENCE | AL5 | DESIGN; COMMISSION; OPERATE | NORMAL; EMERGENCY; RECOVERY; DEGRADED | Applies to every automation and agent registered under SEC-021, including vendor-supplied optimisation loops embedded in BMS or CDU controllers. |  | CG-15; CG-10; CG-07 | Runaway automation power-cycling nodes; Kill switch dependent on compromised platform; Rollback restores corrupt state | Safeguard; Action; TestRecord | Halt and rollback tests on OT targets require facility owner authorisation and operator presence; prefer test benches. | Automations without tested halt are recorded with U1. | AIDCF-005 (AIDCF–AI Trust Graph Integration Standard); NIST AI 100-1 (AI Risk Management Framework); NIST SP 800-82 Rev. 3 (Guide to operational technology security) | MCF-SEC-021; MCF-RES-015; MCF-NET-022; MCF-CMP-016 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-EVA-001 | EVA | Evidence, Assessment and Assurance Management | EVA-01 | Evidence architecture | Evidence Taxonomy | Ensure that every in-scope control has an Evidence Requirement profile expressed in the AIDCF-008 vocabulary (classes E1-E7, quality floor, sufficiency floor, state and period coverage, independence), and that any local evidence subtypes map unambiguously to those classes. | The evidence lead shall maintain, for every in-scope control, an Evidence Requirement profile using the AIDCF-008 classes, quality dimensions (P, F, C, R, T, I), sufficiency levels and control profile tiers, strengthened where the capability profile or criticality requires and never weakened below the registry profile. The evidence lead shall maintain a mapping of every local evidence subtype (for example 'EPMS waveform capture', 'CDU trend export', 'fabric link error report') to exactly one AIDCF-008 class. | 1) Every in-scope control has an Evidence Requirement profile with claim type, profile tier, required classes, quality floor, sufficiency floor, state and period coverage and independence. 2) No profile is weaker than the AIDCF-007A registry profile for the same control and claim type. 3) Every local evidence subtype in use maps to exactly one AIDCF-008 class. 4) Profiles for gate-CRITICAL controls meet or exceed the evidence floor of each gate they map to. 5) The taxonomy uses the canonical vocabularies only (E1-E7 classes, Q0-Q5 bands, S0-S5 sufficiency, EC0-EC5 conformance levels) with no legacy grade codes. |  | Evidence Requirement profiles for in-scope controls; Local subtype-to-class mapping; Comparison of local profiles to registry profiles; Gate floor comparison for CRITICAL controls | DOCUMENT_REVIEW; RECONCILIATION; ANALYSIS | 1) Obtain profiles and check field completeness for every in-scope control. 2) Compare each profile with the registry profile and list weakenings. 3) Check the subtype-to-class mapping for unmapped or multiply mapped subtypes. 4) Compare profiles of gate-CRITICAL controls with gate evidence floors. 5) Screen for legacy vocabulary. | DIRECTIVE | DESIGN | AL2 | PLAN; DESIGN; OPERATE | NORMAL | Applies to every programme that produces Control Assessments. |  |  | Evidence requested ad hoc with no stated requirement; Local profile weaker than the registry; Subtype counted as E4 test evidence when it is E3 observation; Legacy grade codes cause inconsistent sufficiency judgements | EvidenceRequirement; Control; EvidenceObject | Desk review of profiles and mappings; no evidence collection is involved. | If a control has no profile, its result is UNKNOWN (U8 method uncertain) until a profile is approved; the assessor shall not improvise a floor. | AIDCF-008 Evidence Model; ISO/IEC/IEEE 15026-2 (assurance case) - evidence; W3C PROV-DM (provenance data model) | MCF-EVA-003; MCF-EVA-007; MCF-EVA-018; MCF-GOV-004 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-EVA-002 | EVA | Evidence, Assessment and Assurance Management | EVA-01 | Evidence architecture | Evidence Ownership | Ensure that for every Evidence Requirement there is a named source owner responsible for producing the evidence, so that requests reach someone with access and authority, and missing evidence is attributable. | The evidence lead shall assign, for each Evidence Requirement in an assessment, a source owner (person or role in the owner, operator or provider organisation) responsible for producing the evidence by the requested date, and shall record each request, response, delay and refusal in the evidence request record. Unfulfilled requests at the response deadline shall be escalated to the capability owner and recorded as UNKNOWN where unresolved. | 1) Every Evidence Requirement in the sample has an assigned source owner. 2) Every request has an evidence request record with request date, due date, response and status. 3) Overdue requests were escalated to the capability owner. 4) Unfulfilled requests at assessment close are recorded as UNKNOWN Records with type U1 or U2. 5) Provider-held evidence has a source owner in the provider organisation and an internal owner who manages the request. | Evidence request response time [working days] default 10 (Engagement parameter; illustrative) | Evidence request records for the assessment; Source owner assignments; Escalation records; UNKNOWN Records for unfulfilled requests | DOCUMENT_REVIEW; RECONCILIATION; SAMPLING | 1) Obtain evidence request records and check source owner assignment. 2) Test timeliness and escalation for overdue requests. 3) Reconcile unfulfilled requests to UNKNOWN Records. 4) Check provider-held evidence ownership on both sides. | DIRECTIVE | IMPLEMENTATION | AL3 | PLAN; OPERATE | NORMAL | Applies to every assessment that requests evidence from others. |  | CG-13 | Evidence request sent to a general mailbox and never answered; Missing evidence silently dropped from scope; Provider refuses access and no UNKNOWN is raised; Nobody knows who holds commissioning records | EvidenceRequirement; EvidenceObject; UnknownRecord; Action | Review of evidence request records only; the assessor does not contact provider source owners directly without the internal owner's agreement. | Every request unfulfilled at assessment close becomes an UNKNOWN Record; it shall never be closed as 'not provided' without an UNKNOWN Record. | AIDCF-008 Evidence Model; ISO 19011 (guidelines for auditing management systems) | MCF-GOV-008; MCF-EVA-014; MCF-EVA-001 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-EVA-003 | EVA | Evidence, Assessment and Assurance Management | EVA-01 | Evidence architecture | Evidence Repository | Ensure that accepted evidence is held in a repository that assigns immutable identifiers, records the mandatory AIDCF-008 metadata, produces an EvidenceManifest with hashes for each Evidence Package, and supports retrieval of exactly the evidence a decision relied on. | The evidence lead shall operate an evidence repository in which every Evidence Object has an immutable identifier, the mandatory metadata defined in AIDCF-008 (including source, collector, custodian, observation time, collection time, scope, state, classification, integrity value and lifecycle state), and conditional metadata for test, telemetry, configuration, human, external and derived evidence. The tool owner shall configure the repository to generate an EvidenceManifest with content hashes for each Evidence Package and to freeze the manifest referenced by each Assurance Decision. | 1) Every Evidence Object in a sample has an immutable identifier and complete mandatory metadata. 2) Conditional metadata are present for test, telemetry, configuration, human, external and derived evidence in the sample. 3) Each Evidence Package supporting a decision has an EvidenceManifest with content hashes. 4) The manifest referenced by each decision is frozen and retrievable, and its hashes verify against stored objects. 5) Repository configuration prevents in-place overwrite of accepted Evidence Objects. |  | Repository configuration export; Sample of Evidence Object metadata records; EvidenceManifests for decisions in the period; Hash verification output | INSPECTION; SAMPLING; TEST; RECONCILIATION | 1) Export repository configuration and verify identifier immutability and overwrite protection. 2) Sample Evidence Objects and check mandatory and conditional metadata. 3) Retrieve manifests for decisions in the period. 4) Recompute hashes with an independent tool and compare. | PREVENTIVE | IMPLEMENTATION | AL3 | PLAN; OPERATE | NORMAL | Applies to every programme issuing Assurance Decisions. |  |  | Evidence overwritten with a newer version under the same ID; Decision cannot be reproduced because its evidence set is unknown; Telemetry evidence without source clock or query; Missing collector identity | EvidenceObject; EvidencePackage; ReleaseManifest; AssuranceDecision | Hash recomputation uses read-only access to stored objects; no object is modified. | If a decision's manifest cannot be retrieved, record a U1 UNKNOWN against that decision's evidence basis and refer it to MCF-EVA-024 for suspension review. | AIDCF-008 Evidence Model; AIDCF-014 End-to-End Traceability and Machine-Executable Data Standard; ISO 14721 (open archival information system reference model) | MCF-EVA-004; MCF-EVA-006; MCF-GOV-008 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-EVA-004 | EVA | Evidence, Assessment and Assurance Management | EVA-01 | Evidence architecture | Retention and Protection | Ensure that assurance evidence is retained according to its retention class, protected according to its classification, preserved under legal hold, and recoverable after loss of the repository, so that decisions remain reviewable and challengeable throughout their validity. | The evidence lead shall assign each Evidence Object a retention class (R0-R5) and a classification level, define retention periods by legal, contractual and decision-validity requirements, apply legal holds when instructed, and record authorised destruction. The tool owner shall back up the repository, including manifests and custody logs, to a separate fault domain and shall test restoration at the restoration test interval, verifying hashes and custody logs after restore. | 1) Every Evidence Object in the sample has a retention class and classification. 2) Retention periods are defined and no Evidence Object supporting a decision still within its validity or challenge period was destroyed. 3) Legal holds in the period were applied to all relevant objects and destruction was blocked. 4) Backups of objects, manifests and custody logs are held in a fault domain separate from the primary repository. 5) A restoration test within the interval restored a representative sample and hashes and custody logs verified after restore. 6) Access controls enforce classification, and restricted evidence access is logged. | Evidence repository restoration test interval [months] default 12 (Programme parameter; illustrative) | Retention schedule and classification policy; Sample of object retention and classification attributes; Legal hold records; Backup configuration showing separate fault domain; Restoration test record with hash verification; Destruction records | DOCUMENT_REVIEW; INSPECTION; TEST; SAMPLING | 1) Review retention schedule and classification policy. 2) Sample objects and verify attributes and that none supporting a valid decision was destroyed. 3) Review legal hold application. 4) Inspect backup configuration for fault-domain separation. 5) Examine or observe a restoration test and recompute hashes on restored objects. | RECOVERY | RESILIENCE | AL5 | OPERATE; DECOMMISSION | NORMAL; RECOVERY | Applies to every programme retaining evidence beyond a single engagement. |  |  | Evidence destroyed before challenge period ends; Backups in the same storage system as the primary; Restored evidence fails hash verification unnoticed; Classified evidence accessible to all assessors | EvidenceObject; EvidencePackage; DistributionControl | Restoration tests use an isolated restore target; production repository content is never overwritten by a restore test. | If restoration has never been tested, the RESILIENCE claim is UNKNOWN (U1); backup existence alone supports only IMPLEMENTATION. | ISO 15489-1 (records management); ISO/IEC 27001 (information security management systems); ISO/IEC 27040 (storage security); ISO/IEC 27050 series (electronic discovery) | MCF-EVA-003; MCF-GOV-008; MCF-EVA-006 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-EVA-005 | EVA | Evidence, Assessment and Assurance Management | EVA-02 | Evidence provenance and quality | Source Provenance | Ensure that every accepted Evidence Object has an established origin, authority and collection lineage, including derived and AI-assisted evidence whose sources, transformation and human review are recorded, so that no conclusion rests on evidence of unknown origin. | The lead assessor shall ensure that, before an Evidence Object is accepted, its source, collector, collection activity and authority are recorded and verified; that derived evidence records source Evidence IDs, query or script and version, assumptions and reviewer; and that AI-assisted extraction, summarisation or classification is recorded with model and version, process record and the accountable human review, and is treated as candidate evidence that does not corroborate its own sources. | 1) Every accepted Evidence Object in the sample has recorded source, collector, collection activity and authority. 2) Provenance was verified (for example extraction witnessed, issuer confirmed) for evidence supporting gate-CRITICAL controls. 3) Derived evidence records source IDs, transformation method and version, assumptions and reviewer. 4) AI-assisted evidence records model and version, process record and human reviewer, and is not used as independent corroboration of its sources. 5) No Evidence Object with P rating below the profile floor supports a CONFORMING result. |  | Sample of accepted Evidence Object provenance records; Collection activity records for gate-supporting evidence; Derived evidence lineage records; AI-assisted processing records with review | SAMPLING; REPERFORMANCE; DOCUMENT_REVIEW; ANALYSIS | 1) Sample accepted Evidence Objects, weighted to those supporting CRITICAL controls. 2) Check provenance fields and verification records. 3) Trace derived evidence to sources and re-run one transformation. 4) Inspect AI-assisted processing records and confirm human review and non-use as corroboration. 5) Reperform provenance verification at source for a sub-sample. | PREVENTIVE | OPERATION | AL4 | OPERATE | NORMAL | Applies to every programme accepting evidence; AI-assisted criteria apply only where AI-assisted processing is used. |  |  | Screenshot of a configuration accepted with no record of who captured it or from where; Derived capacity analysis whose source telemetry cannot be identified; AI summary of commissioning reports treated as corroboration; Provider attestation with unverified issuer | EvidenceObject; EvidenceRequirement; ValidationResult | Reperformance of extraction at source is read-only and performed by the system owner under observation. | Evidence whose origin cannot be established is recorded as U6 and is excluded from support of any CONFORMING result. | W3C PROV-DM (provenance data model); ISO/IEC 27037 (identification, collection, acquisition and preservation of digital evidence); AIDCF-008 Evidence Model | MCF-EVA-006; MCF-EVA-007; MCF-EVA-003 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-EVA-006 | EVA | Evidence, Assessment and Assurance Management | EVA-02 | Evidence provenance and quality | Integrity and Custody | Ensure that alteration of evidence or loss of custody is detected, so that evidence supporting gates and decisions can be shown to be the evidence originally collected. | The evidence lead shall ensure that every Evidence Object supporting a gate result or Assurance Decision has an integrity value computed at collection, an integrity level (I0-I5) assigned, and a custody log; that integrity values are re-verified before decision issue and on retrieval for challenge or reassessment; and that integrity failures are recorded, investigated and the affected evidence withdrawn from support. The evidence lead shall test detection at least once per integrity test interval by a controlled tamper exercise on test objects. | 1) Every gate-supporting Evidence Object in the sample has an integrity value from collection, an integrity level and a custody log. 2) Integrity values were re-verified before each decision issue in the period. 3) Integrity failures in the period were recorded, investigated and the affected evidence withdrawn from support. 4) A controlled tamper exercise within the interval was detected by the integrity mechanism. 5) Redactions preserved a controlled unredacted source and recorded basis and method. | Integrity detection test interval [months] default 12 (Programme parameter; illustrative) | Integrity values and custody logs for sampled evidence; Pre-decision integrity verification records; Integrity failure records; Tamper exercise record; Redaction records | TEST; SAMPLING; INSPECTION; REPERFORMANCE | 1) Sample gate-supporting evidence and check integrity values, levels and custody logs. 2) Verify pre-decision re-verification records. 3) Review integrity failure handling. 4) Examine the tamper exercise design and result; reperform verification on a sub-sample. 5) Review redaction records. | DETECTIVE | EFFECTIVENESS | AL5 | OPERATE | NORMAL | Applies to all evidence supporting gate results or Assurance Decisions. |  |  | Test report edited after collection to remove an anomaly; Custody gap during provider transfer; Integrity values computed only after editing; Redaction removes content without a controlled original | EvidenceObject; EvidencePackage; ValidationResult | Tamper exercises use dedicated test objects in a non-production area of the repository, with the evidence lead's written approval; real evidence is never altered. | Any Evidence Object whose integrity cannot be re-verified is recorded as U7 and withdrawn from support until re-collected or independently corroborated. | ISO/IEC 27037 (identification, collection, acquisition and preservation of digital evidence); ISO/IEC 27042 (analysis and interpretation of digital evidence); AIDCF-008 Evidence Model | MCF-GOV-008; MCF-EVA-005; MCF-EVA-004 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-EVA-007 | EVA | Evidence, Assessment and Assurance Management | EVA-02 | Evidence provenance and quality | Relevance and Reliability | Ensure that each Evidence Object is rated for fitness to the precise assertion and for reliability of its method and source, with rationale, so that reliable but irrelevant evidence (for example a design document cited for an operation claim) does not support a result. | The lead assessor shall ensure that every Evidence Object used to support a Control Assessment is rated on all six AIDCF-008 quality dimensions with rationale, that the fitness (F) rating considers subject, criterion, claim type, configuration and operating state, that the reliability (R) rating considers method repeatability and corroboration, and that a second assessor independently re-rates a sample with differences resolved and recorded. | 1) Every supporting Evidence Object in the sample has P, F, C, R, T and I ratings with rationale. 2) F ratings reflect claim type and operating state; no E1 design evidence alone supports an OPERATION, EFFECTIVENESS or RESILIENCE claim. 3) Independent re-rating of a sample agrees within one point on each dimension, or differences were resolved and recorded. 4) No Evidence Object below the profile quality floor supports a CONFORMING result. 5) Quality vectors are retained and not collapsed to a single averaged number. | Independent re-rating sample [% of supporting Evidence Objects] default 10 (Programme parameter; illustrative, minimum of 10 objects) | Quality ratings with rationale for sampled evidence; Independent re-rating records; Control Assessments with supporting evidence lists | SAMPLING; REPERFORMANCE; ANALYSIS | 1) Sample Control Assessments and their supporting evidence. 2) Check quality ratings and rationale. 3) Test claim-type fitness, especially E1-only support for higher claims. 4) Reperform ratings for a sub-sample and compare. 5) Compare ratings with profile floors for CONFORMING results. | PREVENTIVE | OPERATION | AL4 | OPERATE | NORMAL | Applies to every Control Assessment that relies on evidence, which is every Control Assessment other than NOT_APPLICABLE dispositions. |  |  | Design drawing accepted as proof of operation; Vendor datasheet accepted as proof of installed configuration; Ratings inflated to meet floors; Single averaged quality score hides a weak integrity rating | EvidenceObject; ControlAssessment; EvidenceRequirement | Desk re-rating of evidence records only; source systems are not accessed for this control. | Where reviewers cannot agree on a rating after discussion, record a U9 UNKNOWN on the evidence and apply the lower rating until resolved. | AIDCF-008 Evidence Model; ISO 19011 (guidelines for auditing management systems) - audit evidence; ISAE 3000 (assurance engagements other than audits or reviews of historical financial information) | MCF-EVA-005; MCF-EVA-008; MCF-EVA-018 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-EVA-008 | EVA | Evidence, Assessment and Assurance Management | EVA-02 | Evidence provenance and quality | Currency and Coverage | Ensure that evidence is current for the state asserted and covers the required population, locations, period, operating states and scenarios, so that a result is not extrapolated beyond what the evidence represents. | The lead assessor shall ensure that each Evidence Object used to support a result is checked against the AIDCF-008 freshness basis for its category and against any material change since collection, and that each Control Assessment records coverage across entity, population, location, time, operating state, scenario, tenant or workload, and dependency dimensions, with gaps recorded as U3 or U5 UNKNOWN Records. | 1) Every supporting Evidence Object in the sample was checked for currency against its category basis and for intervening material change. 2) Each sampled Control Assessment records coverage across the AIDCF-008 coverage dimensions relevant to its claim type. 3) Evidence predating a material change to its subject is not used without re-validation. 4) Coverage gaps (for example no evidence from DEGRADED or MAINTENANCE states) are recorded as U5 UNKNOWN Records. 5) No result is stated for a population, state or period broader than the evidence covers. |  | Currency checks for sampled evidence; Coverage records in sampled Control Assessments; Change log for subjects of sampled evidence; UNKNOWN Records for currency and coverage gaps | SAMPLING; RECONCILIATION; ANALYSIS | 1) Sample Control Assessments and their evidence. 2) Compare evidence dates with the freshness basis and change log. 3) Check coverage records against the relevant dimensions. 4) Confirm coverage gaps are recorded as UNKNOWN Records. 5) Compare stated result scope with evidence coverage. | PREVENTIVE | OPERATION | AL4 | OPERATE | NORMAL | Applies to every Control Assessment at OPERATION claim type or above, and to DESIGN and IMPLEMENTATION assessments where evidence predates a material change. |  |  | Commissioning test from before a cooling conversion used for current effectiveness; UPS test on one of four modules extrapolated to all; No maintenance-state evidence yet maintenance-state claim made; Telemetry from one hall used for a multi-hall instance | EvidenceObject; ControlAssessment; UnknownRecord; Sample | Desk analysis only. | Evidence that predates a material change is recorded as U3 for the changed subject; coverage gaps are recorded as U5 with the missing dimension named. | AIDCF-008 Evidence Model; ISO 2859-1 (sampling procedures for inspection by attributes); ISO 19011 (guidelines for auditing management systems) | MCF-EVA-007; MCF-EVA-011; MCF-EVA-021 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-EVA-009 | EVA | Evidence, Assessment and Assurance Management | EVA-03 | Assessment planning and execution | Decision Question | Ensure that each assessment answers a precisely stated decision question (for example 'Can Capability Instance X sustain training goodput within tolerance through loss of one CDU per pod, as of date D?') that names the Capability Instance, Service Outcomes, tolerances, operating states, intended users and prohibited interpretations. | The decision authority shall approve, before fieldwork begins, a decision question for each assessment that states the Capability Instance, the Service Outcomes and tolerances in question, the operating states, the as-of date or period, the intended users and use, and the interpretations the conclusion shall not support. The lead assessor shall frame the assurance case top claim from the approved decision question and shall obtain re-approval if the question changes during the assessment. | 1) An approved decision question exists for each assessment, dated before fieldwork. 2) The question names Capability Instance, Service Outcomes, tolerances, operating states, as-of date or period, intended users and use, and prohibited interpretations. 3) The assurance case top claim is derived from the decision question without broadening it. 4) Changes to the question during the assessment were re-approved by the decision authority. 5) The report and Assurance Statement restate the same decision question. |  | Approved decision question record; Assurance case top claim; Change records for the question; Report and Assurance Statement extracts | DOCUMENT_REVIEW; RECONCILIATION; INQUIRY | 1) Obtain the approved decision question and check required elements and approval date. 2) Compare the top claim with the question. 3) Review change records for the question. 4) Compare the question restated in the report and statement. | DIRECTIVE | DESIGN | AL2 | PLAN | NORMAL | Applies to every assessment that produces an Assurance Decision. | CG-01 |  | Assessment asks 'is the data centre resilient?' with no instance, outcome or state; Conclusion used for a purchase decision it was not designed for; Top claim broader than the approved question; Question changed mid-assessment without approval | AssuranceProgram; Assessment; CapabilityInstance; ServiceOutcome | Desk review of engagement records only; draft decision questions are treated as confidential to the commissioning party. | If no approved decision question exists, record a US5 UNKNOWN Record; no Assurance Decision above INCONCLUSIVE may be issued. | ISO/IEC/IEEE 15026-2 (assurance case); ISAE 3000 (assurance engagements other than audits or reviews of historical financial information) - engagement acceptance; AIDCF-009 Assessment Methodology Practitioner Handbook | MCF-EVA-010; MCF-GOV-001; MCF-CAP-001; MCF-CAP-010 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-EVA-010 | EVA | Evidence, Assessment and Assurance Management | EVA-03 | Assessment planning and execution | Scope and Criteria | Ensure that each assessment has an approved boundary (physical, logical, organisational, provider and temporal), applicable criteria (AIDCF artifact and capability-profile versions, applicable controls, claim types, gates), and visible exclusions with their residual effect. | The lead assessor shall prepare, and the decision authority shall approve before fieldwork, a scope record for each assessment stating the boundary across physical, logical, organisational, provider and temporal dimensions; the operating states assessed; the applicable AIDCF artifact and capability-profile versions; the applicable controls with claim types; the applicable gates; and every exclusion with rationale and residual effect on the decision. The lead assessor shall reconcile the boundary to the ArchitectureSnapshot (MCF-CAP-004) and record any element of the snapshot that is neither in scope nor excluded. | 1) An approved scope record exists, dated before fieldwork, covering all five boundary dimensions and the operating states. 2) Applicable criteria are identified by version, including the control set with claim types and the gate set. 3) Every exclusion has rationale and residual effect on the decision. 4) Reconciliation to the ArchitectureSnapshot leaves no element neither in scope nor excluded. 5) Shared and external dependencies crossing the boundary are listed with how they are assessed (directly, by provider evidence, or as UNKNOWN). |  | Approved scope record; Applicable control and gate list with claim types; Exclusion register with residual effect; Boundary-to-ArchitectureSnapshot reconciliation | DOCUMENT_REVIEW; RECONCILIATION; ANALYSIS | 1) Obtain the approved scope record and check dimensions, states and approval date. 2) Check criteria versions, control set and gate set. 3) Review exclusions for rationale and residual effect. 4) Reperform boundary reconciliation for a sample of snapshot elements. 5) Check treatment of cross-boundary dependencies. | DIRECTIVE | DESIGN | AL2 | PLAN | NORMAL | Applies to every assessment, including delta assessments after material change, which require their own scope record. | CG-02 |  | Utility supply excluded with no residual effect stated; Provider-operated cooling plant neither in scope nor excluded; Criteria version not stated, so results are unreproducible; Maintenance state silently omitted from scope | Assessment; ArchitectureSnapshot; Dependency; CriticalGate | Desk review and graph reconciliation using read-only queries; no site access is required. | Any ArchitectureSnapshot element that is neither in scope nor excluded is recorded as a US5 UNKNOWN Record against the boundary. | ISO/IEC/IEEE 15026-2 (assurance case) - context and assumptions; ISO 19011 (guidelines for auditing management systems) - audit scope and criteria; AIDCF-011 Assurance Program Framework | MCF-EVA-009; MCF-CAP-004; MCF-EVA-017; MCF-EVA-016 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-EVA-011 | EVA | Evidence, Assessment and Assurance Management | EVA-03 | Assessment planning and execution | Sampling and Testing | Ensure that sampling is risk-based, reproducible and not over-extrapolated, and that tests are authorised, safe, defined in advance (initial state, method, expected result, abort criteria, restoration) and recorded with anomalies. | The lead assessor shall document, for each sample, the population and its frame, strata, selection method, sample size rationale, exclusions and expansion rule, and shall record failed samples and their effect. For each test, the lead assessor shall obtain written authorisation from the system owner and, for hazardous or service-affecting tests, the safety authority, and shall record the initial state, method, expected result, abort criteria, instrumentation, restoration steps, result and anomalies. Tests shall be performed by authorised operators; assessors shall observe. | 1) Each sample in the assessment has documented population frame, strata, method, size rationale, exclusions and expansion rule. 2) Judgemental samples are not represented as statistical coverage, and sampled results are not extrapolated beyond the represented population and conditions. 3) Failed samples triggered expansion or were reflected in the result. 4) Every test has prior written authorisation from the system owner and, where hazardous or service-affecting, the safety authority. 5) Every test record contains initial state, method, expected result, abort criteria, instrumentation, restoration, result and anomalies. 6) Tests were performed by authorised operators, with assessors observing. |  | Sampling plans and records; Test authorisations; Test records with required conditional metadata; Expansion records for failed samples | DOCUMENT_REVIEW; REPERFORMANCE; SAMPLING | 1) Review sampling plans for required elements. 2) Reperform selection for one sample from the population frame. 3) Check expansion after failed samples and absence of over-extrapolation. 4) Check test authorisations and safety authority sign-off for hazardous tests. 5) Check test records for required metadata and operator/observer roles. | PREVENTIVE | IMPLEMENTATION | AL3 | PLAN; OPERATE; COMMISSION | NORMAL; MAINTENANCE; DEGRADED | Applies to every assessment that samples or tests. |  | CG-04 | Assessor operates switchgear during a test; Test performed without abort criteria and fails to restore; Three good samples extrapolated to an entire fleet; Failed sample discarded | Sample; TestRecord; AssessmentProcedure | This control governs safety of all assessment testing: hazardous-energy, pressurised-fluid, refrigerant, battery and service-affecting tests require written authorisation from the system owner and the safety authority, a method statement, initial-state verification, abort criteria, permits under the site safe system of work and restoration steps. The safety authority may stop any test at any time; a stopped test is recorded with its partial result and does not count as passed. | If a test lacks authorisation records, its result is excluded from support and recorded as U8 (method uncertain); it is not re-run without authorisation. | ISO 2859-1 (sampling procedures for inspection by attributes); ISO 19011 (guidelines for auditing management systems) - audit sampling; AIDCF-009 Assessment Methodology Practitioner Handbook | MCF-EVA-008; MCF-EVA-012; MCF-CAP-019; MCF-CAP-022 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-EVA-012 | EVA | Evidence, Assessment and Assurance Management | EVA-03 | Assessment planning and execution | Specialist Involvement | Ensure that domain specialists (electrical, mechanical, compute, storage and network, OT security, resilience, evidence and data) approve the technical methods and conclusions in their domains, and that reliance on specialists is recorded with scope, competence and responsibility. | The lead assessor shall identify, for each assessment, the domains requiring specialist judgement, appoint a competent specialist for each (MCF-GOV-023), and record the specialist's scope, competence evidence and responsibility. Each specialist shall approve the methods and the Control Assessment results in their domain. Where a specialist is external, the lead assessor shall evaluate their independence and the transferability of their conclusions. | 1) Domains requiring specialist judgement are identified for the assessment. 2) Each identified domain has an appointed specialist with recorded scope, competence evidence and responsibility. 3) Methods and Control Assessment results in each specialist domain carry the specialist's approval. 4) External specialists' independence and transferability of conclusions were evaluated. 5) No technical conclusion in a specialist domain was issued without specialist approval. |  | Specialist domain identification; Specialist appointment and reliance records; Specialist approvals on methods and results; External specialist evaluation records | DOCUMENT_REVIEW; RECONCILIATION; INQUIRY | 1) Review domain identification against scope. 2) Check appointments and reliance records. 3) Reconcile results in each domain to specialist approvals. 4) Review external specialist evaluations. 5) Interview one specialist on scope and approval. | PREVENTIVE | IMPLEMENTATION | AL3 | PLAN; OPERATE | NORMAL | Applies to every assessment that includes technical infrastructure domains. |  |  | Generalist assessor concludes on protection coordination; OEM engineer acts as independent specialist for their own product; Specialist reviews methods but not results; Liquid-cooling domain not identified as needing a specialist | Assessment; ReviewRecord; ControlAssessment | Record review and interview only. | If specialist approval is missing for a domain result, that result is UNKNOWN (U9 interpretation unresolved) until approved. | ISO 19011 (guidelines for auditing management systems) - technical experts; ISAE 3000 (assurance engagements other than audits or reviews of historical financial information) - use of experts; AIDCF-011 Assurance Program Framework | MCF-GOV-023; MCF-EVA-011; MCF-EVA-015 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-EVA-013 | EVA | Evidence, Assessment and Assurance Management | EVA-04 | Findings, UNKNOWN and limitations | Finding Traceability | Ensure that every Finding is traceable to the criterion, the evidenced condition, the supporting and challenging evidence, the affected Service Outcomes, controls and gates, and to its action and closure evidence. | The lead assessor shall record every Finding with a stable identifier, criterion (control and assessment criterion), condition, supporting and challenging Evidence Object references, cause where evidenced or labelled as analysis, consequence for Service Outcomes, dependencies and states, classification, and gate and score effect. The action owner shall record closure evidence, and the lead assessor shall close a Finding only after re-assessing that evidence. | 1) Every Finding in the sample has identifier, criterion, condition, evidence references, consequence, classification and gate/score effect. 2) Cause is either evidenced or explicitly labelled as analysis. 3) Each Finding is linked in the graph to its control, Service Outcomes and gates. 4) Closed Findings have closure evidence re-assessed by an assessor, not closed on management assertion. 5) Findings are not deleted; superseded Findings retain history. |  | Findings register extract; Sampled Finding records with evidence links; Graph links from Findings to controls, outcomes and gates; Closure evidence and re-assessment records | SAMPLING; RECONCILIATION; DOCUMENT_REVIEW | 1) Extract the full Findings register including closed and superseded items. 2) Sample Findings and check required fields and evidence references. 3) Check graph links to controls, outcomes and gates. 4) Verify closure evidence and re-assessment for closed Findings. 5) Compare register history for deletions. | DETECTIVE | OPERATION | AL4 | OPERATE | NORMAL | Applies to every assessment that raises Findings. |  |  | Finding closed on an email saying 'fixed'; Finding with no link to the gate it affects; Cause speculated without evidence; Embarrassing Finding deleted | Finding; EvidenceObject; Action; ControlAssessment | Review of Findings records only; closure evidence involving site changes is verified under the relevant domain control. | If a Finding's evidence references cannot be resolved to Evidence Objects, record a U1 UNKNOWN on the Finding and keep it open. | AIDCF-012 Reporting and Assurance Statement Standard; ISO 19011 (guidelines for auditing management systems) - audit findings | MCF-EVA-014; MCF-EVA-016; MCF-GOV-024 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-EVA-014 | EVA | Evidence, Assessment and Assurance Management | EVA-04 | Findings, UNKNOWN and limitations | UNKNOWN Preservation | Ensure that missing, inaccessible, stale, conflicting or unverifiable knowledge is recorded as an UNKNOWN Record with type, severity and decision effect, carried unchanged into gates, scores, decisions and reports, and never silently resolved favourably. | The lead assessor shall record every UNKNOWN as an UNKNOWN Record with subject, missing attribute, type (U1-U10), severity (US1-US5) with the test that determined it, reason, potential consequence, evidence needed, owner, status and gate and decision effect. The decision authority shall ensure that every US3, US4 and US5 UNKNOWN Record is reflected in the Gate Results, decision ceiling and report, and that UNKNOWN Records are closed only by new evidence or approved re-scoping, never by assumption. | 1) Every UNKNOWN Record in the sample has all required fields including type and severity with the test applied. 2) Severity was assigned top-down by the US5-to-US1 tests; reperformance yields the same severity. 3) Every US4 UNKNOWN Record is reflected as a gate UNKNOWN and every US5 caps the decision at INCONCLUSIVE. 4) Every US3 and above UNKNOWN Record appears in the report with decision effect. 5) A seeded or traced set of UNKNOWNs survived unchanged from workpaper to report. 6) Closed UNKNOWN Records cite new evidence or approved re-scoping. | UNKNOWN traceability test set size [UNKNOWN Records] default 10 (Programme parameter; illustrative) | UNKNOWN register extract; Sampled UNKNOWN Records; Gate Results and decision record; Report extracts; Traceability or seeded-UNKNOWN test record; Closure records | REPERFORMANCE; TEST; SAMPLING; RECONCILIATION | 1) Extract the UNKNOWN register and sample records. 2) Check required fields and reperform severity assignment. 3) Reconcile US4 and US5 records to Gate Results and decision ceiling. 4) Trace US3+ records into the report. 5) Examine or perform the traceability test from workpaper to report. 6) Review closure basis for closed records. | DETECTIVE | EFFECTIVENESS | AL5 | OPERATE | NORMAL | Applies to every assessment; an assessment with no UNKNOWN Records shall record that the UNKNOWN search was performed. |  |  | UNKNOWN downgraded to an 'improvement opportunity' in the executive report; Missing evidence treated as conforming; US4 UNKNOWN not reflected in its gate; UNKNOWN closed because the deadline passed | UnknownRecord; GateResult; AssuranceDecision; AssuranceReport | Seeded-UNKNOWN tests use copies of completed assessments labelled as test material; they are never introduced into live workpapers. | If the register cannot be shown to be complete (for example UNKNOWNs held in personal notes), record a US4 UNKNOWN Record against UNKNOWN completeness for the assessment. | AIDCF-008 Evidence Model; ISO/IEC/IEEE 15026-2 (assurance case) - defeaters; AIDCF-012 Reporting and Assurance Statement Standard | MCF-EVA-015; MCF-EVA-016; MCF-EVA-018; MCF-GOV-003 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-EVA-015 | EVA | Evidence, Assessment and Assurance Management | EVA-04 | Findings, UNKNOWN and limitations | Conflict Handling | Ensure that when material evidence supports incompatible propositions (for example design shows 2N power, EPMS shows a shared upstream breaker), both lineages are preserved, the conflict is analysed and resolved, bounded or escalated, and the result reflects it. | The lead assessor shall register each material evidence conflict as an EvidenceConflict with both assertions and their evidence lineages, analyse scope, time and state differences, seek corroboration, obtain competent review and record whether the conflict is resolved, bounded or escalated. Unresolved conflicts shall be recorded as U4 UNKNOWN Records; observed or tested evidence shall take precedence over design intent unless shown to be unrepresentative. | 1) Every material conflict identified in the sample is registered with both assertions and lineages. 2) Each conflict record shows analysis of scope, time and state differences and corroboration sought. 3) Resolution, bounding or escalation is recorded with competent reviewer. 4) Unresolved conflicts are U4 UNKNOWN Records with severity assigned. 5) Where design intent conflicts with observed or tested evidence, the observed or tested evidence prevailed or the reason it was unrepresentative is recorded. 6) Neither lineage was deleted. |  | Evidence conflict register; Conflict analysis and review records; UNKNOWN Records for unresolved conflicts | DOCUMENT_REVIEW; ANALYSIS; SAMPLING | 1) Obtain the conflict register. 2) Search workpapers for unregistered contradictions. 3) Review analysis, corroboration and review for each sampled conflict. 4) Confirm unresolved conflicts are U4 UNKNOWN Records. 5) Check precedence of observed evidence over design intent. | CORRECTIVE | OPERATION | AL4 | OPERATE | NORMAL | Applies to every assessment in which two or more evidence sources address the same assertion. |  |  | Inconvenient telemetry ignored in favour of design documents; Conflicting provider attestation discarded; Conflict resolved by majority of documents rather than by evidence quality; Conflict unresolved but result CONFORMING | EvidenceObject; UnknownRecord; ControlAssessment | Desk analysis only; corroborating extraction, if needed, is read-only. | Unresolved material conflicts are U4 UNKNOWN Records and the affected result is UNKNOWN until resolved or bounded. | AIDCF-008 Evidence Model; ISO/IEC/IEEE 15026-2 (assurance case) | MCF-EVA-014; MCF-EVA-007; MCF-EVA-012 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-EVA-016 | EVA | Evidence, Assessment and Assurance Management | EVA-04 | Findings, UNKNOWN and limitations | Limitation Disclosure | Ensure that every limitation on the conclusion (exclusions, restricted or inaccessible evidence, untested states, assumptions, sampling limits, provider reliance) is disclosed in every report and statement at a prominence matching its effect. | The lead assessor shall compile a limitations register for each assessment covering exclusions, restricted or inaccessible evidence, unassessed operating states, assumptions, sampling and test limits and reliance on providers or specialists, each with its effect on the decision. The reporting owner shall ensure every report and Assurance Statement for the assessment discloses each limitation with an effect on the decision, and that redaction for security does not remove a limitation. | 1) A limitations register exists covering the six limitation categories, each with decision effect. 2) Every limitation with a decision effect appears in each report and statement for the assessment. 3) Limitations affecting gates appear in the executive report alongside the Gate Results. 4) Redacted reports still state each limitation, even where its technical detail is withheld. 5) No report broadens scope beyond what the limitations allow. |  | Limitations register; All reports and statements for the assessment; Redaction records | RECONCILIATION; DOCUMENT_REVIEW | 1) Obtain the limitations register. 2) Reconcile each limitation to every report and statement. 3) Check executive-report prominence for gate-affecting limitations. 4) Compare redacted and unredacted versions for limitation removal. 5) Check report scope against limitations. | DETECTIVE | OPERATION | AL4 | OPERATE | NORMAL | Applies to every assessment that issues a report or statement. |  |  | Public summary omits that utility dependency was excluded; Redaction removes the statement that cooling failover was untested; Provider reliance not disclosed; Executive summary implies all states were assessed | AssuranceReport; AssuranceStatement; DistributionControl | Desk review; restricted report versions viewed under distribution controls. | If a report version cannot be obtained for reconciliation, record a U2 UNKNOWN for that report and treat its disclosure as unverified. | AIDCF-012 Reporting and Assurance Statement Standard; ISAE 3000 (assurance engagements other than audits or reviews of historical financial information) - inherent limitations | MCF-EVA-020; MCF-GOV-020; MCF-EVA-010; MCF-EVA-014 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-EVA-017 | EVA | Evidence, Assessment and Assurance Management | EVA-05 | Critical gates and decisions | Gate Applicability | Ensure that, for each assessment, every critical gate CG-01 to CG-15 is determined as applicable or APPROVED_NA with boundary rationale, and that the CRITICAL and SUPPORTING control set for each applicable gate is identified from the registry for the scope. | The lead assessor shall determine, for each assessment, the applicability of each gate CG-01 to CG-15 to the decision question and boundary, shall identify for each applicable gate the in-scope CRITICAL and SUPPORTING controls from the AIDCF-007A registry gate mappings and the gate criteria from AIDCF-010, and shall submit any proposed APPROVED_NA with boundary rationale to the decision authority. Meta-gates CG-11 and CG-12 shall always be applicable. | 1) Each of the fifteen gates has an applicability determination for the assessment. 2) Every APPROVED_NA has boundary rationale and decision-authority approval. 3) CG-11 and CG-12 are applicable in every assessment. 4) For each applicable gate, the in-scope CRITICAL and SUPPORTING controls match the registry gate mappings filtered by scope. 5) Gate criteria and evidence floors applied are those of the declared AIDCF-010 version. |  | Gate applicability record; APPROVED_NA approvals; Gate-to-control lists per applicable gate; Registry gate mapping extract for the declared version | DOCUMENT_REVIEW; RECONCILIATION | 1) Obtain the applicability record and check all fifteen gates. 2) Review APPROVED_NA rationale and approvals. 3) Reconcile gate-control lists to registry mappings filtered by scope. 4) Confirm gate criteria and floors match the declared AIDCF-010 version. | DIRECTIVE | DESIGN | AL2 | PLAN | NORMAL | Applies to every assessment that issues Gate Results, including delta and incident-triggered assessments. |  |  | CG-04 marked not applicable for a site with battery rooms; CRITICAL control omitted from a gate's control list; Superseded gate criteria applied; APPROVED_NA granted by the lead assessor | CriticalGate; Control; Assessment | Desk review against the published registry release; no system access is required. | If the registry version used for gate mappings cannot be identified, record a U8 UNKNOWN against every Gate Result of the assessment. | AIDCF-010 Scoring and Decision Framework; AIDCF-007A Canonical Master Control Registry | MCF-EVA-018; MCF-GOV-015; MCF-EVA-010 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-EVA-018 | EVA | Evidence, Assessment and Assurance Management | EVA-05 | Critical gates and decisions | Gate Evidence | Ensure that evidence for each applicable gate meets the gate's mandatory evidence classes and sufficiency floor from AIDCF-008, without substitution below the floor to complete a scorecard, and that Gate Results are computed by the AIDCF-010 roll-up rule. | The lead assessor shall assemble, for each applicable gate, a gate Evidence Package containing the mandatory evidence classes for that gate, shall assess its sufficiency against the gate floor, and shall compute the Gate Result by the AIDCF-010 roll-up rule from CRITICAL control results, gate criteria and evidence sufficiency. The independent reviewer shall confirm, for each gate, that no evidence below the mandatory type or quality floor was substituted. | 1) Each applicable gate has an Evidence Package containing its mandatory evidence classes. 2) Sufficiency of each gate package is assessed and recorded against the gate floor. 3) No gate PASS is supported by a package below its floor; such gates are UNKNOWN. 4) Each Gate Result reproduces when the roll-up rule is reapplied. 5) The independent reviewer confirmed absence of below-floor substitution for each gate. |  | Gate Evidence Packages; Gate sufficiency assessments; Gate Result computation records; Independent reviewer gate confirmation | REPERFORMANCE; DOCUMENT_REVIEW; ANALYSIS | 1) Obtain gate packages and check mandatory classes per gate. 2) Review sufficiency assessments against floors. 3) Reapply the roll-up rule to recorded results. 4) Check independent reviewer confirmations. | PREVENTIVE | OPERATION | AL4 | OPERATE | NORMAL | Applies to every assessment that issues Gate Results. |  |  | CG-05 passed on design documents and an old UPS test; Interview substituted for missing E4 recovery test under CG-10; Gate PASS with a CRITICAL control PARTIAL; Gate result computed by averaging | CriticalGate; GateResult; EvidencePackage | Desk reperformance of gate roll-up from recorded results; no evidence is re-collected under this control. | Any gate whose package is below floor is UNKNOWN; this shall be recorded as a US4 UNKNOWN Record against the gate. | AIDCF-008 Evidence Model; AIDCF-010 Scoring and Decision Framework | MCF-EVA-017; MCF-EVA-019; MCF-GOV-015; MCF-EVA-007 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-EVA-019 | EVA | Evidence, Assessment and Assurance Management | EVA-05 | Critical gates and decisions | Independent Decision | Ensure that the Assurance Decision is issued by the accountable decision authority, separate from those who prepared and performed the assessment, on the basis of a recorded Decision Recommendation and review, and that automation only proposes. | The decision authority shall issue each Assurance Decision personally or through documented delegation, on the basis of a Decision Recommendation from the lead assessor and the independent review record, and shall record the decision state, controlling reasons (including Gate Results and UNKNOWN ceilings), conditions with owners and dates, and validity. The tool owner shall ensure that no tool can transition a decision to APPROVED without the decision authority's authenticated action. | 1) Every Assurance Decision in the period was issued by the decision authority or a documented delegate. 2) The decision authority was not the preparer or performer of the assessment. 3) Each decision references a Decision Recommendation and independent review record. 4) Each decision records state, controlling reasons, conditions with owners and dates, and validity. 5) Tool configuration requires an authenticated decision-authority action for APPROVED status; no automated approval occurred. |  | Decision records; Delegation instruments; Decision Recommendations and review records; Decision workflow configuration and audit log | DOCUMENT_REVIEW; INSPECTION; RECONCILIATION | 1) List decisions in the period and verify issuer authority. 2) Compare issuer with preparer and performer records. 3) Check references to recommendation and review. 4) Check required decision content. 5) Inspect workflow configuration and audit log for automated approvals. | PREVENTIVE | IMPLEMENTATION | AL3 | OPERATE | NORMAL | Applies to every Assurance Decision. |  | CG-13 | Lead assessor issues the decision; Tool auto-approves when score exceeds a threshold; Decision issued without review; Conditions without owners or dates | AssuranceDecision; DecisionRecommendation; ReviewRecord | Read-only inspection of workflow configuration and logs. | If the workflow audit log cannot show who approved a decision, record a U7 UNKNOWN against that decision's authority. | ISO/IEC 17020 (requirements for bodies performing inspection) - impartiality; AIDCF-010 Scoring and Decision Framework; AIDCF-006 Assurance Principles Standard | MCF-GOV-002; MCF-GOV-016; MCF-GOV-022; MCF-EVA-018 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-EVA-020 | EVA | Evidence, Assessment and Assurance Management | EVA-05 | Critical gates and decisions | Claim Language | Ensure that reports and statements use only the controlled decision, gate and result vocabulary, bound every conclusion by Capability Instance, Service Outcomes, scope, states and date, and contain no prohibited claims. | The reporting owner shall ensure that every report and Assurance Statement uses the controlled decision states (REASONABLY_ASSURED, CONDITIONALLY_ASSURED, LIMITED, NOT_ASSURED, INCONCLUSIVE), Gate Results (PASS, FAIL, UNKNOWN, APPROVED_NA, NOT_ASSESSED) and control results of AIDCF-010 with the controlled wording of AIDCF-012; bounds each conclusion by Capability Instance, Service Outcomes, boundary, operating states and as-of date; and contains no prohibited claim (certified, accredited, universally safe, secure or resilient, compliant with all laws). The independent reviewer shall check claim language before issue. | 1) Every report and statement in the sample uses only the controlled decision, gate and result vocabulary. 2) Each conclusion is bounded by Capability Instance, Service Outcomes, boundary, operating states and as-of date. 3) No prohibited claim appears. 4) No visual device (colour, badge, score) presents a stronger conclusion than the decision state. 5) Independent review of claim language is recorded before issue. |  | Sampled reports and statements; Independent review records for claim language | DOCUMENT_REVIEW; SAMPLING; ANALYSIS | 1) Collect all issued reports and statements in the period. 2) Screen vocabulary and bounding elements. 3) Screen for prohibited claims and misleading visual devices. 4) Check independent review records. | PREVENTIVE | OPERATION | AL4 | OPERATE | NORMAL | Applies to every report or statement conveying an AIDCF conclusion. |  |  | Statement says 'fully resilient AI data centre'; Legacy term 'Adverse' or 'Conditional' used; Green badge shown for a LIMITED decision; Conclusion stated without as-of date | AssuranceReport; AssuranceStatement; AssuranceDecision | Desk review of issued documents only. | If an issued document cannot be retrieved, record a U2 UNKNOWN for that document's claim language. | AIDCF-012 Reporting and Assurance Statement Standard; ISO/IEC 17000 (conformity assessment vocabulary and general principles) | MCF-GOV-020; MCF-EVA-016; MCF-EVA-019 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-EVA-021 | EVA | Evidence, Assessment and Assurance Management | EVA-06 | Reassessment and continuing assurance | Evidence Expiry | Ensure that each Evidence Object relied on by a current decision has a currency basis and review date, that expiry is detected, and that expired mandatory evidence triggers review of the claims it supports. | The evidence lead shall record, for each Evidence Object supporting a current Assurance Decision, its currency basis and review date per AIDCF-008, shall monitor for expiry, and on expiry of mandatory evidence shall notify the lead assessor and capability owner, mark the evidence STALE and initiate review of the dependent claims and Gate Results within the expiry response time. | 1) Every Evidence Object supporting a current decision has a currency basis and review date. 2) Expiry monitoring operated throughout the period (for example scheduled reports or alerts). 3) Every expiry of mandatory evidence in the period was notified and the evidence marked STALE. 4) Dependent claims and Gate Results were reviewed within the expiry response time. 5) No current decision relies on expired mandatory evidence without a recorded review outcome. | Expiry response time [working days] default 20 (Programme parameter; illustrative) | Evidence currency records for current decisions; Expiry monitoring outputs; Expiry notifications and STALE markings; Dependent claim review records | ANALYSIS; RECONCILIATION; SAMPLING | 1) Obtain currency records for evidence supporting current decisions. 2) Run an independent expiry query and compare with monitoring outputs. 3) Trace expiries to notifications, STALE markings and reviews. 4) Check current decisions for reliance on expired mandatory evidence. | DETECTIVE | OPERATION | AL4 | OPERATE | NORMAL | Applies to every programme with decisions that remain valid over time. |  |  | Annual UPS test expired but CG-05 PASS still reported; Provider certificate lapsed unnoticed; Evidence with no review date; Expiry alerts sent to a departed staff member | EvidenceObject; ReassessmentTrigger; AssuranceDecision | Read-only queries against currency records. | Evidence with no currency basis is treated as STALE (U3) for any OPERATION, EFFECTIVENESS or RESILIENCE claim. | AIDCF-008 Evidence Model; ISO 15489-1 (records management) | MCF-EVA-008; MCF-EVA-022; MCF-EVA-024 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-EVA-022 | EVA | Evidence, Assessment and Assurance Management | EVA-06 | Reassessment and continuing assurance | Change Triggers | Ensure that material change, incidents, gate changes and evidence invalidation automatically or reliably trigger reassessment of the affected claims, gates and decisions, and that the trigger mechanism is shown to work. | The assurance programme lead shall define reassessment triggers for each current Assurance Decision (material architecture, capacity, configuration, provider or ownership change; incidents affecting Service Outcomes; gate FAIL or critical UNKNOWN; evidence invalidation), shall connect the change, incident and evidence systems so that trigger events are routed to the lead assessor and capability owner, and shall verify at least once per trigger test interval, by injecting a test event, that triggers reach the responsible roles and initiate reassessment. | 1) Each current decision has defined reassessment triggers covering change, incident, gate and evidence events. 2) Change, incident and evidence systems route trigger events to the lead assessor and capability owner. 3) Every material change and Service Outcome incident in the period was matched to a trigger response. 4) An injected test event within the interval reached the responsible roles and initiated the reassessment workflow. 5) Trigger responses record the affected claims, gates and decisions and the outcome. | Trigger test interval [months] default 6 (Programme parameter; illustrative) | Trigger definitions per decision; Integration configuration between change, incident and evidence systems and the assurance workflow; Trigger response records; Injected test event record | TEST; RECONCILIATION; INSPECTION; DOCUMENT_REVIEW | 1) Review trigger definitions per current decision. 2) Inspect integration configuration. 3) Reconcile material changes and incidents to trigger responses. 4) Examine or perform an injected test event with the tool owner. | DETECTIVE | EFFECTIVENESS | AL5 | OPERATE; CHANGE | NORMAL; TRANSITION | Applies to every programme with decisions remaining valid after issue. |  | CG-14 | Cooling conversion completed but prior CG-06 PASS still relied upon; Incident ticket never reaches the assurance team; Trigger fires to a mailbox nobody monitors; Provider change outside the owner's change system | ReassessmentTrigger; Event; AssuranceDecision; IntegrationHandoff | Injected test events are clearly marked as tests in non-production change or incident queues, or use a test category agreed with the tool owner; they shall not page operational on-call staff or alter real change records. | If provider-originated changes are not routed, record a U10 UNKNOWN for provider-dependent claims. | ISO/IEC 20000-1 (service management system) - change and incident management; AIDCF-014 End-to-End Traceability and Machine-Executable Data Standard; AIDCF-011 Assurance Program Framework | MCF-CAP-023; MCF-EVA-021; MCF-EVA-024; MCF-EVA-023 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-EVA-023 | EVA | Evidence, Assessment and Assurance Management | EVA-06 | Reassessment and continuing assurance | Monitoring Coverage | Ensure that where continuing assurance is claimed, the specific claims monitored, the telemetry and evidence feeds used, their coverage and their blind spots are defined, and that feed health is itself monitored. | The assurance programme lead shall, for each claim under continuing assurance, define the monitored indicators, their source feeds, coverage across assets, locations and operating states, thresholds that trigger review, and known blind spots. The tool owner shall monitor feed health (gaps, latency, clock integrity, dropped data) and alert the evidence lead on degradation; the programme lead shall state blind spots in each continuing-assurance report. | 1) Each claim under continuing assurance has defined indicators, feeds, coverage, thresholds and blind spots. 2) Feed coverage reconciles to the in-scope asset and location population. 3) Feed health is monitored, and degradations in the period were alerted and actioned. 4) Threshold breaches in the period triggered review. 5) Continuing-assurance reports state blind spots and feed-health limitations. | Maximum tolerated feed gap [% of period] default 5 (Programme parameter; illustrative) | Continuing assurance claim definitions; Feed coverage reconciliation; Feed-health monitoring records; Threshold breach review records; Continuing-assurance reports | RECONCILIATION; ANALYSIS; INSPECTION; DOCUMENT_REVIEW | 1) Review continuing-assurance claim definitions. 2) Reconcile feed coverage to asset and location registers. 3) Analyse feed-health records for gaps and actions. 4) Trace threshold breaches to reviews. 5) Check blind-spot disclosure in reports. | DETECTIVE | OPERATION | AL4 | OPERATE | NORMAL; DEGRADED; MAINTENANCE | Applies only where continuing assurance (AL6) is claimed; otherwise NOT_APPLICABLE. |  |  | Continuous assurance claimed while half the CDUs report no telemetry; Clock drift corrupts event ordering; New hall never onboarded to monitoring; Blind spots omitted from report | ReassessmentTrigger; EvidenceObject; AssuranceReport | Read-only access to observability and monitoring systems. | If feed coverage cannot be reconciled, record a U5 UNKNOWN and do not describe the claim as continuously assured. | AIDCF-011 Assurance Program Framework; NIST SP 800-137 (information security continuous monitoring); NIST SP 800-92 (guide to computer security log management) | MCF-EVA-022; MCF-EVA-021; MCF-CAP-013 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002
MCF-EVA-024 | EVA | Evidence, Assessment and Assurance Management | EVA-06 | Reassessment and continuing assurance | Decision Suspension and Supersession | Ensure that when a decision can no longer be relied upon (material change, incident, gate FAIL, evidence invalidation, expiry), it is suspended, withdrawn or superseded promptly, intended users are notified, and history is preserved, so that failure of a prior conclusion is contained. | The decision authority shall define criteria for suspension, withdrawal and supersession of Assurance Decisions, shall act on each trigger response that meets the criteria within the suspension time, shall notify all intended users and recipients of external communications, and shall preserve the prior decision, its evidence manifest and the reason for change. The programme lead shall rehearse the suspension and notification process at least once per rehearsal interval. | 1) Suspension, withdrawal and supersession criteria are defined. 2) Each trigger response meeting the criteria in the period resulted in suspension, withdrawal or supersession within the suspension time. 3) All intended users and external recipients were notified. 4) Prior decisions, manifests and reasons are preserved and linked by SUPERSEDES relationships. 5) A rehearsal within the interval exercised suspension and notification end to end, or a real suspension did so. | Suspension time after qualifying trigger [working days] default 5 (Programme parameter; illustrative) Suspension rehearsal interval [months] default 12 (Programme parameter; illustrative) | Suspension, withdrawal and supersession criteria; Trigger response and decision lifecycle records; Notification records; Decision history with SUPERSEDES links; Rehearsal or real-event record | SCENARIO_EXERCISE; DOCUMENT_REVIEW; RECONCILIATION; SAMPLING | 1) Review criteria. 2) Reconcile qualifying trigger responses to lifecycle actions and timing. 3) Check notifications to intended users and external recipients. 4) Inspect history preservation and SUPERSEDES links. 5) Examine or observe a rehearsal. | RECOVERY | RESILIENCE | AL5 | OPERATE; CHANGE | NORMAL; RECOVERY | Applies to every programme with decisions relied upon after issue. |  |  | Customer still relying on a decision invalidated by a cooling incident; Superseded decision deleted; Suspension notice not sent to external recipients; Gate FAIL after incident not acted on | AssuranceDecision; ReassessmentTrigger; AssuranceStatement; DistributionControl | Rehearsals use test decision records and test distribution lists; no notice is sent to real external recipients during a rehearsal. | If decision history cannot be shown to be preserved, record a U7 UNKNOWN against prior decisions' traceability. | AIDCF-012 Reporting and Assurance Statement Standard; AIDCF-011 Assurance Program Framework; ISO 22301 (business continuity management systems) - exercising | MCF-EVA-022; MCF-EVA-021; MCF-GOV-020; MCF-EVA-019 | CANDIDATE | 1.1 | AIDCF-007A-AMD-002

## Evidence Profiles
Control ID | claimType | profileTier | requiredClasses | optionalClasses | qualityFloor | sufficiencyFloor | stateCoverage | periodCoverage | independence | mandatoryItems | acceptableAlternatives | unknownEffect | reassessmentTriggers
MCF-GOV-001 | DESIGN | CP-1 | E1; E6 | E5 | P3 F3 C3 R3 T3 I2 | S3 | NORMAL | Charter version in force at the assessment date and the preceding review cycle | Approval evidence shall originate from the governing-body secretariat or equivalent, not from the charter author | Approved governance charter with version identifier and effective date; Governing-body resolution or minute recording approval of that charter version | Terms of reference of a board-delegated committee containing equivalent content, supported by the delegation instrument | US3 Material: control result UNKNOWN; CG-13 gate-level evaluation records the gap; decision capped at CONDITIONALLY_ASSURED with a named condition to evidence charter approval | Change of accountable executive or decision authority; Organisational restructuring affecting assurance reporting lines; Change of programme model or assurance provider; Addition of a Capability Instance to scope
MCF-GOV-002 | IMPLEMENTATION | CP-2 | E1; E2; E3 | E6 | P3 F3 C3 R3 T3 I3 | S3 | NORMAL; EMERGENCY; RECOVERY | Current matrix plus decisions taken in the twelve months preceding the assessment, or since the last assessment if shorter | Workflow configuration shall be extracted by the assessor or under assessor observation, not supplied as a screenshot by the approver population | Approved decision-rights matrix with version and approval record; Export of approver role configuration from change, exception, risk and decision workflow tools; Sampled decision records with approver identity, role and date | Where approvals are paper-based, a complete approval log reconciled to signed records replaces the workflow configuration export | US4 Critical: CG-13 Gate Result UNKNOWN; decision capped at LIMITED until the decision-rights evidence is produced | Reorganisation or change in delegation limits; Introduction or replacement of an approval workflow tool; A decision found to have been taken outside its decision right; Change of emergency response arrangements
MCF-GOV-003 | OPERATION | CP-3 | E1; E3 | E6 | P3 F3 C4 R3 T3 I3 | S4 | NORMAL | At least four consecutive meeting cycles, or all meetings in the last twelve months | Minutes shall be the approved record held by the committee secretary; drafts or summaries prepared by management are not sufficient | Approved committee terms of reference; Approved minutes and committee action log; Sampled meeting packs with register extracts | Recorded and transcribed meetings with approved action logs may replace minutes where the organisation's records policy permits | US3 Material: control result UNKNOWN; decision capped at CONDITIONALLY_ASSURED with a condition that oversight operation is evidenced | Change of chair or loss of the independent member; Two consecutive missed or inquorate meetings; A gate FAIL not presented to the committee; Change to terms of reference
MCF-GOV-004 | IMPLEMENTATION | CP-2 | E1; E2 | E7 | P3 F3 C3 R3 T3 I3 | S3 | NORMAL | Methodology baseline in force and reports issued in the last twelve months | Tool configuration comparison shall be performed by the assessor against published release manifests, not by the tool owner alone | Methodology baseline record with versions, tailorings, rationale and approvals; Tool configuration export showing registry, vocabulary and scoring versions | Where no tool is used, controlled template versions with checksums replace the tool configuration export | US3 Material: affected control and gate results UNKNOWN where the methodology version cannot be established; decision capped at CONDITIONALLY_ASSURED | New AIDCF artifact release adopted; Approval of a new local tailoring; Assessment tool upgrade or replacement; Report found to declare an incorrect baseline
MCF-GOV-005 | IMPLEMENTATION | CP-2 | E1; E6 | E2; E7 | P3 F3 C4 R3 T3 I2 | S3 | NORMAL; MAINTENANCE; EMERGENCY | RACI in force and appointments current at the assessment date | Interview evidence shall be obtained by the assessor directly from role holders, separately from the RACI author | Approved RACI with version; Responsibility clauses of operator, provider and tenant contracts; RACI reconciliation record | A responsibility matrix embedded in a service management system, exported with version metadata | US4 Critical: CG-13 Gate Result UNKNOWN; decision capped at LIMITED | Organisational change; New, changed or terminated provider or tenant contract; Departure of an Accountable role holder; Incident in which responsibility was disputed
MCF-GOV-006 | IMPLEMENTATION | CP-2 | E1; E2; E7 | E6 | P3 F4 C4 R3 T3 I3 | S3 | NORMAL; DEGRADED; EMERGENCY | Graph state at the assessment date and changes during the preceding twelve months | The graph extract shall be produced by query executed or witnessed by the assessor | Assurance graph extract of Required Functions and Dependencies with owner attributes; RACI and decision-rights matrix extracts | Where no graph exists, a function and dependency register maintained under document control, with an explicit limitation recorded against traceability | US4 Critical: CG-13 Gate Result UNKNOWN for each unowned critical function; decision capped at LIMITED | New Required Function or material Dependency identified; Change of provider for an external dependency; Owner departure; Incident revealing an unowned function
MCF-GOV-007 | OPERATION | CP-3 | E1; E3 | E6 | P3 F4 C4 R3 T3 I3 | S4 | NORMAL; DEGRADED; MAINTENANCE | All acceptances active at any point in the twelve months preceding the assessment | Assessor selects the sample from a full register extract; management selection of examples is not accepted | Risk-acceptance authority schedule; Risk register extract of acceptances in the period; Sampled acceptance records with acceptor role and date | Where risk acceptances are recorded in decision minutes rather than a register, a complete extraction from minutes reconciled to the action log | US4 Critical: CG-13 Gate Result UNKNOWN; decision capped at LIMITED | Change of risk appetite or authority levels; Acceptance found to exceed authority; Expiry of acceptances touching gate-critical controls; Change of impact tolerance
MCF-GOV-008 | OPERATION | CP-3 | E1; E2; E3 | E7 | P4 F3 C4 R4 T3 I4 | S4 | NORMAL | Custody events for Evidence Objects supporting decisions issued in the last twelve months | Custody logs shall be extracted from the repository system of record by the assessor, not compiled by the custodian | Repository access policy and role configuration export; Custody logs for sampled Evidence Objects; Pre-decision custody review records | For paper or physical evidence, a sealed-bag custody register with signatures and seal numbers | US3 Material: affected gate evidence treated as integrity-uncertain (U7); dependent gate results may become UNKNOWN under CG-11 | Repository migration or platform change; Custodian change; Detected unauthorised access or alteration; New provider evidence exchange
MCF-GOV-009 | DESIGN | CP-1 | E1 | E6; E7 | P3 F3 C3 R3 T3 I2 | S3 | NORMAL | Documents in force at the assessment date | Contradiction comparison on a sample of document pairs shall be performed by the assessor | Policy hierarchy register; Approved policy-level documents | Document management system metadata export with parent-child links in place of a separate register | US3 Material: control result UNKNOWN; reliance on procedures for affected controls is limited and recorded as a condition | New or withdrawn policy; New site, hall or cluster added to scope; Contradiction contributing to an incident
MCF-GOV-010 | IMPLEMENTATION | CP-2 | E1; E2 | E5; E6 | P3 F3 C3 R3 T3 I2 | S3 | NORMAL | Baseline in force and records produced since the last major design or commissioning event | Domain specialists for each infrastructure domain shall confirm applicability of the listed standard families | Technical standards baseline with editions and scope; Deviation register entries with approvals | Design basis documents per domain that each list applied standards, consolidated by the assessor | US3 Material: affected DESIGN claims in infrastructure domains may become UNKNOWN; decision condition recorded | New edition of an applied standard adopted; OEM specification revision for accelerators, CDUs or power equipment; New infrastructure domain or technology introduced (for example immersion cooling); Deviation approved
MCF-GOV-011 | OPERATION | CP-3 | E1; E3 | E2; E7 | P3 F4 C4 R3 T3 I3 | S4 | NORMAL; MAINTENANCE; DEGRADED | All exceptions active during the twelve months preceding the assessment | Assessor compares observed configuration deviations with the register independently of the exception owner | Exception register extract for the period; Sampled exception records with approvals | Exception records held in a GRC tool, exported with full field history | US3 Material: affected control results UNKNOWN where undeclared deviation cannot be excluded; decision condition recorded | Exception approved for a gate-critical control; Exceptions past expiry; Deviation discovered without an exception; Change in exception approval authority
MCF-GOV-012 | IMPLEMENTATION | CP-2 | E1; E2; E3 | E6 | P3 F3 C3 R3 T4 I3 | S3 | NORMAL; EMERGENCY | Document versions current at the assessment date | Point-of-use inspection shall be performed by the assessor | Document management system version and status export; Point-of-use inspection record | Controlled print register with issue and withdrawal signatures where points of use rely on printed documents | US3 Material: affected OPERATION claims in operational domains may be qualified; decision condition recorded | Document management system replacement; Incident where an outdated document was used; Major change requiring runbook revision
MCF-GOV-013 | DESIGN | CP-1 | E1; E7 | E6 | P3 F4 C3 R3 T3 I2 | S3 | NORMAL | Current planning period | Approval by the oversight committee, separate from the programme lead who prepared the plan | Approved assurance plan; Criticality classification extract | Engagement-level plan for a single assessment, approved by the decision authority | US3 Material: decision capped at CONDITIONALLY_ASSURED; condition requires an approved plan before reliance is extended | New Capability Instance; Change in criticality classification; Major change programme approved; Gate FAIL requiring unplanned assessment
MCF-GOV-014 | DESIGN | CP-1 | E1 | E6; E7 | P3 F3 C3 R3 T3 I2 | S3 | NORMAL | Appetite statement and tolerances in force at the assessment date | Reconciliation performed by the assessor | Approved risk appetite statement; Reconciliation of impact tolerances to appetite limits | Enterprise risk appetite with capability-specific annex | US3 Material: impact tolerances cannot be confirmed as governed; decision condition recorded | Revision of risk appetite; Change of impact tolerance; New Service Outcome class
MCF-GOV-015 | OPERATION | CP-3 | E1; E3; E7 | E5 | P4 F4 C4 R4 T3 I4 | S4 | NORMAL | All Assurance Decisions issued in the twelve months preceding the assessment | Roll-up reperformance by the assessor or independent reviewer, separate from the team that produced the Gate Results | Gate register with history; Decision records and executive reports for sampled assessments | Machine-readable gate results exported from the assessment tool with full audit history | US3 Material: decisions in the period may not be relied on above CONDITIONALLY_ASSURED until gate governance is evidenced | Change to AIDCF-010 roll-up rule or gate criteria; Gate Result altered outside reassessment; Decision issued above gate ceiling
MCF-GOV-016 | EFFECTIVENESS | CP-4 | E1; E3; E4 | E5; E6 | P4 F4 C3 R4 T3 I3 | S4 | NORMAL | All material decisions in the last twelve months and at least one effectiveness test | Effectiveness test designed and scored by a party other than the reviewers tested | Independent review records for each material decision; Review effectiveness test record with seeded defects and detection outcome | External quality assessment of the review function by a second-party or independent provider, if it includes reperformance | US3 Material: decisions are treated as self-reviewed; decision capped at CONDITIONALLY_ASSURED for intended users beyond management | Change of reviewer pool; Decision issued without review; Missed defect discovered after issue; New domain requiring reviewer competence
MCF-GOV-017 | DESIGN | CP-1 | E1 | E6; E7 | P3 F4 C3 R3 T3 I2 | S3 | NORMAL | Obligations in force at the assessment date | Sample of source documents selected by the assessor | Stakeholder obligation register; Traceability from obligations to Service Outcomes and constraints | Contract management system extract with obligation tagging | US3 Material: affected Service Outcome definitions qualified; decision condition recorded | New or amended customer contract; New grid connection or permit condition; Insurance renewal with new warranties
MCF-GOV-018 | OPERATION | CP-3 | E1; E3 | E5; E6 | P3 F3 C4 R3 T3 I2 | S4 | NORMAL | Twelve months preceding the assessment | Assessor or legal specialist checks a sample of known changes against the log | Regulatory monitoring scope by jurisdiction and topic; Change log with impact assessments for the period | Subscription legal-update service records combined with internal impact assessments | US3 Material: obligation completeness qualified; decision condition recorded | Entry into a new jurisdiction; Major regulatory change affecting energy, water or critical infrastructure; Regulatory enforcement event
MCF-GOV-019 | IMPLEMENTATION | CP-2 | E1; E7 | E3 | P3 F4 C4 R3 T3 I3 | S3 | NORMAL | Commitments in force at the assessment date | Assessor selects contracts and reperforms reconciliation | Commitment register with metric definitions; Reconciliation records to Service Outcomes | Standard product terms plus a register of negotiated deviations | US3 Material: decision condition recorded; Service Outcome adequacy for customer reliance qualified | New customer contract or renewal; Change in Service Outcome tolerance; SLA breach
MCF-GOV-020 | OPERATION | CP-3 | E1; E3 | E7 | P3 F4 C4 R3 T3 I3 | S4 | NORMAL | Twelve months preceding the assessment | Assessor compares each communication with the underlying decision record | Register of external communications conveying conclusions; Copies of the communications; Approval records | Communications archive search by assessor where no register exists, with a coverage limitation recorded | US3 Material: decision condition recorded; continued external reliance is qualified | Decision suspended, withdrawn or superseded; New external audience; Change in AIDCF-012 controlled language
MCF-GOV-021 | OPERATION | CP-3 | E1; E3 | E6 | P3 F3 C4 R3 T3 I3 | S4 | NORMAL | Engagements active in the twelve months preceding the assessment | Assessor cross-checks declarations against design, change and advisory records independently of the declarant | Declarations of interest for engagement personnel; Threat evaluations and safeguard records; Engagement assignment records | Provider's own conflict register, if the provider grants access to records for the engagement personnel | US3 Material: affected results treated as not independently assessed; decision capped at CONDITIONALLY_ASSURED for external reliance | New provider engaged; Assessor previously involved in design or operation; Fee structure change; Undeclared conflict discovered
MCF-GOV-022 | IMPLEMENTATION | CP-2 | E1; E3 | E6 | P3 F3 C3 R3 T3 I3 | S3 | NORMAL | Engagements completed in the twelve months preceding the assessment | Assessment of this control shall not be performed by the assessment function it concerns | Independence policy with levels per reliance class; Engagement records with team composition, provider model and reporting line | Engagement letters stating provider model and intended users | US3 Material: intended use of affected decisions restricted to management; condition recorded | Change of provider model; Change of assessment function reporting line; New intended-user class
MCF-GOV-023 | OPERATION | CP-3 | E1; E3; E6 | E5 | P3 F4 C4 R3 T3 I2 | S4 | NORMAL | Assignments in the twelve months preceding the assessment | Assessor verifies a sample of competence evidence at source (certificates, prior work records) | Competence framework; Competence register with evidence; Engagement assignment records | Provider-held competence records made available for engagement personnel | US3 Material: affected domain results carry a confidence ceiling of CONF-2 and a decision condition | New technology in scope; New assessor or provider; Finding attributed to competence gap
MCF-GOV-024 | OPERATION | CP-3 | E1; E3 | E6 | P3 F3 C4 R3 T3 I4 | S4 | NORMAL | Challenges raised in the twelve months preceding the assessment | Record history extracted by the assessor from the system of record | Appeal and challenge procedure; Challenge log for the period; Record history for challenged results | Where no challenges occurred, a walkthrough of the procedure with the decision authority, recorded as limited operating evidence | US2 Moderate: confidence in contested results limited to CONF-2 | Challenge upheld; Change of decision authority; Repeated challenges on the same gate
MCF-CAP-001 | IMPLEMENTATION | CP-2 | E1; E2; E7 | E6 | P3 F4 C4 R3 T4 I3 | S3 | NORMAL | Register state at the assessment date and reconciliations over the preceding two intervals | Scheduler and asset exports shall be produced by query executed or witnessed by the assessor | Capability register extract with all attributes; Scheduler or orchestration inventory export (cluster, pod, node counts) dated within the reconciliation interval; Reconciliation record listing unmatched items and dispositions | Configuration management database extract with capability tagging, where the CMDB is itself reconciled to the scheduler | US5 Systemic: the Capability Instance definition is unresolved; CG-01 Gate Result UNKNOWN and decision capped at INCONCLUSIVE | New cluster, pod or service pool brought into service; Re-allocation of accelerators between instances; Change of tenancy model; Hall or site added to or removed from an instance
MCF-CAP-002 | IMPLEMENTATION | CP-2 | E1; E6 | E2 | P3 F3 C4 R3 T3 I2 | S3 | NORMAL; EMERGENCY; RECOVERY | Appointments in force at the assessment date | Assessor interviews the owner and deputy separately from the appointing executive | Capability owner appointment records; Capability register, RACI and decision-rights extracts | Organisational role description with explicit capability ownership, plus appointment of the current holder | US4 Critical: CG-13 Gate Result UNKNOWN for the instance; decision capped at LIMITED | Owner or deputy change; Reorganisation; Change of facility operator or platform provider
MCF-CAP-003 | OPERATION | CP-3 | E1; E3 | E2; E7 | P3 F4 C4 R3 T4 I3 | S4 | NORMAL; TRANSITION | Status transitions over the twelve months preceding the assessment | Assessor obtains scheduler or tenancy evidence independently of the status log owner | Status transition log for the period; Commissioning acceptance records; Scheduler evidence of production workload on each instance | Change records for go-live with linked acceptance evidence | US3 Material: claim-type selection for the instance may be wrong; decision condition recorded | Status transition; Production workload observed on a non-in-service instance; Partial retirement
MCF-CAP-004 | IMPLEMENTATION | CP-2 | E1; E2; E7 | E6; E3 | P3 F4 C4 R4 T4 I3 | S3 | NORMAL | Snapshot current at the assessment date | Technical exports taken from source systems by or in front of the assessor; drawings verified by site inspection for a sample | Assurance graph extract of Outcome-Function-System links; As-built drawings, single-line diagrams and P&IDs for sampled links; Network topology and cluster manifest exports | Where no graph exists, a controlled architecture register with function-to-system tables, with a traceability limitation recorded | US4 Critical: CG-02 Gate Result UNKNOWN; decision capped at LIMITED | Material architecture change; Expansion or re-cabling of a fabric; Change in cooling topology; As-built discrepancy found
MCF-CAP-005 | DESIGN | CP-1 | E1; E7 | E3; E6 | P3 F4 C3 R3 T3 I2 | S3 | NORMAL; MAINTENANCE; DEGRADED | Outcome definitions in force at the assessment date | Approval by the capability owner, separate from the author; assessor reperforms metric derivation from source for one window | Approved Service Outcome records for availability; Metric definition and measurement data source description | Service level objective specification in the platform's SLO system, approved by the capability owner | US5 Systemic: Service Outcome definition unresolved; CG-01 Gate Result UNKNOWN and decision capped at INCONCLUSIVE | Change of availability target or exclusions; Change of measurement data source; New customer commitment; Change of impact tolerance
MCF-CAP-006 | DESIGN | CP-1 | E1; E7 | E3; E4 | P3 F4 C3 R3 T3 I2 | S3 | NORMAL; DEGRADED | Outcome definitions in force at the assessment date | Assessor or compute specialist reviews metric adequacy independently of the platform team | Approved performance Service Outcome records; Metric and method specifications with workload reference | SLO specifications in the platform observability system, approved by the capability owner | US5 Systemic: Service Outcome definition unresolved; CG-01 Gate Result UNKNOWN and decision capped at INCONCLUSIVE | New accelerator generation or workload type; Change of benchmark or measurement method; Change of design power per accelerator; Fabric re-architecture
MCF-CAP-007 | DESIGN | CP-1 | E1; E2 | E7; E6 | P3 F4 C3 R3 T3 I3 | S3 | NORMAL; RECOVERY | Outcome definitions in force at the assessment date | Storage or compute specialist reviews adequacy of detection mechanisms | Approved integrity Service Outcome records; Detection mechanism description per protected data class | Data protection design specification approved by the capability owner and containing equivalent statements | US5 Systemic: Service Outcome definition unresolved; CG-01 Gate Result UNKNOWN and decision capped at INCONCLUSIVE | Change of checkpoint format or storage system; New accelerator generation; Incident of detected or suspected silent data corruption; Change of dataset pipeline
MCF-CAP-008 | DESIGN | CP-1 | E1; E2 | E7; E4 | P3 F4 C3 R3 T3 I2 | S3 | RECOVERY; FAILED; EMERGENCY | Outcome definitions in force at the assessment date | Resilience specialist reviews consistency of RTO/RPO with architecture | Approved recovery Service Outcome records; Restoration order definition | Business continuity plan section for the instance, approved by the capability owner, containing equivalent content | US5 Systemic: Service Outcome definition unresolved; CG-01 Gate Result UNKNOWN and decision capped at INCONCLUSIVE | Change of RTO/RPO; Change of checkpoint strategy or storage; New dependency in the restoration path; Failed recovery exercise
MCF-CAP-009 | DESIGN | CP-1 | E1; E7 | E6 | P3 F3 C4 R3 T3 I2 | S3 | NORMAL | Classifications in force at the assessment date | Assessor reperforms classification for a sample | Approved criticality criteria; Classification register with rationale | Business impact analysis outputs applying approved criteria | US3 Material: assurance depth may be mis-set; decision condition recorded | New Capability Instance or Service Outcome; Change of consequence thresholds; Material change to an instance
MCF-CAP-010 | DESIGN | CP-1 | E1; E7 | E6 | P3 F4 C4 R3 T3 I2 | S3 | NORMAL; DEGRADED; EMERGENCY; RECOVERY | Tolerances in force at the assessment date | Approval by the accountable executive, separate from the capability owner who set them | Approved impact tolerance records per Service Outcome; Approval record by the accountable executive | Business impact analysis with approved maximum tolerable periods of disruption | US5 Systemic: tolerance T in the top claim is undefined; CG-01 Gate Result UNKNOWN and decision capped at INCONCLUSIVE | Change of risk appetite; New or changed customer commitment; Incident exceeding a tolerance
MCF-CAP-011 | DESIGN | CP-1 | E1; E6 | E7 | P3 F3 C3 R3 T3 I2 | S3 | NORMAL; DEGRADED; FAILED | Analysis current within the planning period | Assessor interviews at least one affected stakeholder representative directly | Stakeholder consequence analysis per Service Outcome; Stakeholder review records | Business impact analysis containing stakeholder consequence content | US3 Material: criticality and tolerance rationale qualified; decision condition recorded | New tenant or dependent service; Incident revealing unanticipated consequence; Change of Service Outcome
MCF-CAP-012 | IMPLEMENTATION | CP-2 | E1; E2 | E3; E4 | P3 F4 C4 R4 T4 I3 | S3 | NORMAL; DEGRADED; EMERGENCY | Configuration current at the assessment date | Configuration exports taken from source systems under assessor observation | Priority class definitions; Scheduler pre-emption and quota configuration export; Load-shedding and power-capping sequence configuration | Where load shedding is manual, the switching procedure with shed order and evidence of operator training | US3 Material: degraded-state protection of critical outcomes unverified; decision condition recorded | New tenant or workload class; Change of shed sequence or EPMS logic; Scheduler policy change
MCF-CAP-013 | OPERATION | CP-3 | E2; E3; E7 | E1 | P4 F4 C4 R4 T4 I3 | S4 | NORMAL; MAINTENANCE | At least the baseline period ending within the refresh interval | Assessor reperforms aggregation for one hall or pod from raw telemetry | Demand baseline report with methods and sources; Telemetry extracts for the baseline period; Independent reconciliation sample | Commissioning load measurements for an instance in service for less than the baseline period, with limitation recorded | US3 Material: capacity headroom claims in POW and THM rest on unverified demand; decision condition recorded | New accelerator generation or cluster expansion; Change of workload mix; Meter replacement or recalibration; Telemetry outage longer than 10% of the baseline period
MCF-CAP-014 | OPERATION | CP-3 | E2; E3; E7 | E4; E1 | P4 F4 C3 R4 T4 I3 | S4 | NORMAL; TRANSITION; RECOVERY | Captures covering each representative workload type, taken since the last change in accelerator generation or power-management configuration | Electrical specialist independent of the capacity manager reviews capture method and resolution | Peak and transient characterisation report; High-resolution power-quality or meter captures for representative workloads | OEM-provided transient profiles for the accelerator platform, only for DESIGN-stage use and with the limitation recorded | US3 Material: POW and THM capacity and control-stability claims lack a demand basis; affected CG-05 and CG-06 evaluation records the gap | New accelerator generation; Change in power-capping or power-smoothing configuration; New workload type (for example very large synchronous training); Protection trip or UPS alarm correlated with workload steps
MCF-CAP-015 | DESIGN | CP-1 | E1; E7 | E3; E6 | P3 F3 C3 R3 T3 I2 | S3 | NORMAL | Forecast current at the assessment date and the last review against actuals | Assessor reperforms one commitment-date derivation | Approved growth forecast with assumptions and uncertainty; Lead-time register for utility and long-lead equipment | Capital plan with capacity assumptions, approved by the capability owner | US2 Moderate: confidence in forward-looking capacity claims limited to CONF-2 | Change of accelerator roadmap; Change of utility connection timeline; Forecast error beyond the uncertainty range
MCF-CAP-016 | RESILIENCE | CP-5 | E1; E3; E4; E7 | E2; E5 | P4 F4 C3 R4 T3 I3 | S5 | RECOVERY; TRANSITION; DEGRADED | Model current at the assessment date; exercise within the exercise interval | Exercise observed by a party independent of the team that built the model | Scenario demand model; Recovery staging plan; Exercise record with measured demand | Measured demand from a genuine recovery event, analysed against the model, in place of an exercise | US3 Material: recovery staging unvalidated; CG-10 evaluation records the gap; decision condition recorded | Change of recovery architecture or checkpoint strategy; Expansion of instance; Recovery event with demand exceeding model
MCF-CAP-017 | IMPLEMENTATION | CP-2 | E1; E2 | E3; E7 | P3 F4 C4 R4 T4 I3 | S3 | NORMAL; DEGRADED; MAINTENANCE | Configuration current at the assessment date and exceedances in the preceding twelve months | Configuration exports taken from source systems under assessor observation | Load envelope definition with derivations; Power-capping and admission-control configuration export; BMS/EPMS alarm threshold configuration | Where enforcement is procedural, deployment approval records showing envelope checks before each rack installation | US3 Material: overload protection of power and cooling paths unverified; decision condition recorded | New accelerator generation; Change in redundancy state; Rating change of any path element; Exceedance event
MCF-CAP-018 | IMPLEMENTATION | CP-2 | E1; E2 | E3 | P3 F4 C4 R4 T4 I3 | S3 | NORMAL; DEGRADED | Configuration current at the assessment date | Mechanical specialist verifies envelope derivation; configuration exported under assessor observation | Environmental envelope definition with sources; BMS and CDU setpoint and alarm configuration export | Commissioning records of setpoints, where no change has occurred since commissioning and change records confirm this | US3 Material: thermal protection of equipment unverified; CG-06 evaluation records the gap | OEM specification revision; New equipment sharing a loop; Change of BMS or CDU setpoints; Thermal throttling or over-temperature event
MCF-CAP-019 | EFFECTIVENESS | CP-4 | E2; E3; E4 | E1; E5; E7 | P4 F4 C3 R4 T3 I3 | S4 | DEGRADED; EMERGENCY; MAINTENANCE | Validations within the duration validation interval at current load | Test witnessed by a party independent of the facility operator or by an electrical/mechanical specialist assessor | Duration limit statement; UPS autonomy test or discharge record at measured load; Thermal ride-through test, event record or validated model | Validated computational model calibrated against a measured event, for thermal ride-through where a test is not safe | US3 Material: response timing unsupported; CG-05, CG-06 and CG-10 evaluations record the gap; decision condition recorded | Load increase beyond the validated level; Battery replacement or ageing alarms; Cooling topology change; Event where a limit was approached or exceeded
MCF-CAP-020 | OPERATION | CP-3 | E1; E2; E3 | E6 | P3 F4 C4 R4 T4 I3 | S4 | MAINTENANCE; DEGRADED; EMERGENCY; RECOVERY; TRANSITION | Non-normal state periods in the twelve months preceding the assessment | Assessor samples state periods from the log and obtains telemetry independently | State-specific limit definitions; State entry/exit log; Telemetry and change records for sampled state periods | Maintenance window records with associated telemetry where no formal state log exists, with limitation recorded | US3 Material: containment in non-normal states unverified; CG-09 evaluation records the gap | New maintenance regime; Incident during a non-normal state; Redundancy topology change
MCF-CAP-021 | IMPLEMENTATION | CP-2 | E1; E2; E4 | E7 | P3 F4 C3 R4 T3 I3 | S3 | NORMAL | Current configuration and the most recent design and commissioning baseline | Assessor selects trace samples and obtains configuration independently | Traceability matrix or graph extract; Current configuration exports; Deviation register | Per-system design basis and commissioning dossiers linked by system identifier | US3 Material: IMPLEMENTATION claims in infrastructure domains qualified; CG-02 evaluation records the gap | Material change; Discovery of undisclosed deviation; New design baseline
MCF-CAP-022 | EFFECTIVENESS | CP-4 | E1; E2; E3; E4 | E5 | P4 F4 C4 R4 T3 I4 | S4 | NORMAL; DEGRADED; TRANSITION | Commissioning of the current configuration or the latest expansion | Commissioning witnessed by a commissioning authority independent of the installing contractor | Integrated test plan with acceptance criteria; Executed test scripts with results, conditions and anomalies; Failure-transfer test records; Signed acceptance and accepted configuration baseline | For an expansion of an accepted instance, a delta integrated test covering affected systems plus regression on shared systems | US3 Material: operating outcomes rest on unaccepted configuration; CG-02 and CG-08 evaluations record the gap | Expansion or major reconfiguration; Deferred commissioning tests outstanding; Failure in service of a function accepted at commissioning
MCF-CAP-023 | OPERATION | CP-3 | E1; E2; E3 | E4; E7 | P3 F4 C4 R4 T3 I3 | S4 | NORMAL; TRANSITION; MAINTENANCE | All changes in the twelve months preceding the assessment | Assessor selects samples of both material and non-material changes from the full change log | Change log for the period with materiality classification; Capability impact assessments for sampled material changes; Post-change validation records | Programme-level impact assessment for a coordinated set of changes, if each change references it | US4 Critical: CG-14 Gate Result UNKNOWN; decision capped at LIMITED | Change of materiality criteria; Material change implemented without assessment; Post-change incident
MCF-CAP-024 | IMPLEMENTATION | CP-2 | E1; E2; E3 | E5 | P3 F3 C4 R3 T3 I3 | S3 | SHUTDOWN; TRANSITION | Retirements completed in the twelve months preceding the assessment | Sanitisation evidence from the performing party verified against asset serial numbers by the assessor | Approved retirement plans; Data sanitisation certificates or records; Register, snapshot and graph update records | Physical destruction certificates for media where sanitisation was by destruction | US3 Material: residual data exposure or stale architecture records; decision condition recorded | Retirement of an entire instance; Provider service termination; Media found outside sanitisation process
MCF-DEP-001 | IMPLEMENTATION | CP-2 | E1; E2 | E3; E4; E5 | P3 F3 C3 R3 T3 I3 | S4 | NORMAL; MAINTENANCE; DEGRADED | Point-in-time reconciliation no older than the reconciliation interval; change log covering the 12 months preceding the assessment. | Reconciliation sample shall be selected and checked by a person other than the map author; physical verification by walk-down or E2 export, not by the author's attestation. | Versioned asset-to-function map; Reconciliation record against as-built register | Where no CMDB/DCIM exists, a controlled spreadsheet register is acceptable if versioned, owned and reconciled by walk-down with photographic or inspection evidence. | US4 Critical: an UNKNOWN result on this control sets CG-03 to UNKNOWN (CG-12 trigger); the decision is capped at LIMITED or INCONCLUSIVE per the gate ceiling until the UNKNOWN Record is dispositioned. Supporting gates CG-02 require gate-level evaluation. | Addition, removal or relocation of assets implementing a Required Function; Change to redundancy configuration or maintenance arrangement; New Capability Instance or Service Outcome definition; Reconciliation interval elapsed
MCF-DEP-002 | IMPLEMENTATION | CP-2 | E1; E2 | E3; E4; E5 | P3 F3 C3 R3 T3 I3 | S4 | NORMAL; MAINTENANCE; EMERGENCY; RECOVERY | Current at assessment date; graph reviewed within the revalidation interval of MCF-DEP-024. | Corroboration from a source independent of the graph author (provider document, configuration export or technical test). | Upstream dependency graph per Required Function; Configuration evidence for timing/information dependencies | Provider attestations may substitute for route records only where the provider refuses disclosure; the dependency is then recorded with confidence no higher than CONF-2 and an UNKNOWN Record for the undisclosed attribute. | US4 Critical: an UNKNOWN result on this control sets CG-03 to UNKNOWN (CG-12 trigger); the decision is capped at LIMITED or INCONCLUSIVE per the gate ceiling until the UNKNOWN Record is dispositioned. Supporting gates CG-15 require gate-level evaluation. | New or changed provider, circuit, utility connection or cloud/SaaS service; Change to control-system or management-plane architecture; Provider notification of network or route change; Incident revealing an unrecorded dependency
MCF-DEP-003 | DESIGN | CP-1 | E1; E7 | E3; E4; E5 | P3 F3 C3 R3 T2 I2 | S3 | NORMAL; MAINTENANCE; DEGRADED | Current approved version; reviewed within 12 months or after material change. | Technical review by a competent engineer who did not author the analysis. | Approved consequence analysis with time-to-impact values and sources | A fault tree or reliability block model may substitute for a tabular FMEA if it states outcomes, paths and time-to-impact. | US3 Material: an UNKNOWN result requires gate-level evaluation for CG-03, CG-09 and caps the decision at CONDITIONALLY_ASSURED with a recorded condition until resolved. | Change in rack power density or cooling method; Change in workload type (training vs inference) or checkpoint policy; New Service Outcome or tolerance; Incident with unexpected propagation
MCF-DEP-004 | IMPLEMENTATION | CP-2 | E1; E2 | E3; E4; E5 | P3 F3 C3 R3 T3 I3 | S3 | RECOVERY; EMERGENCY; SHUTDOWN | Current at assessment date; updated after each recovery test or real recovery event. | Analysis reviewed by a person from a different discipline (for example a facilities engineer reviewing an IT recovery map and vice versa). | Recovery dependency map; Circular-dependency analysis | A documented recovery exercise (RES-05) that exercised the full restoration path may substitute for part of the circular analysis for the paths it covered. | US3 Material: an UNKNOWN result requires gate-level evaluation for CG-03, CG-10 and caps the decision at CONDITIONALLY_ASSURED with a recorded condition until resolved. | Change to recovery sequence, golden-image location or licence model; Introduction of a cloud or SaaS dependency in a management path; Recovery test or real event revealing an unrecorded dependency
MCF-DEP-005 | IMPLEMENTATION | CP-2 | E1; E2 | E3; E4; E5 | P3 F3 C3 R3 T3 I3 | S4 | NORMAL; MAINTENANCE; EMERGENCY | Current; re-performed after any change to supply arrangements. | Independence claims corroborated by a provider document or as-built record, not the designer's statement. | Shared-source analysis; Provider evidence for each claimed external independence | Where a utility will not disclose supply topology, a utility-signed statement of the number of independent supply points is acceptable at confidence no higher than CONF-2. | US4 Critical: an UNKNOWN result on this control sets CG-03 to UNKNOWN (CG-12 trigger); the decision is capped at LIMITED or INCONCLUSIVE per the gate ceiling until the UNKNOWN Record is dispositioned. Supporting gates CG-05, CG-06, CG-09 require gate-level evaluation. | Utility network reconfiguration notice; Change of fuel or water supplier; New carrier circuit or carrier merger; Change to internal redundancy configuration
MCF-DEP-006 | IMPLEMENTATION | CP-2 | E1; E2 | E3; E4; E5 | P3 F3 C3 R3 T3 I3 | S3 | NORMAL; MAINTENANCE; DEGRADED; FAILED | Current; re-performed after control-system change. | Review by an engineer not responsible for the control-system design. | Common-controller analysis; Configuration evidence of controller failure behaviour | OEM documentation of default failure behaviour is acceptable where configuration export is not possible, with an UNKNOWN Record for the as-configured state. | US3 Material: an UNKNOWN result requires gate-level evaluation for CG-03, CG-07, CG-09 and caps the decision at CONDITIONALLY_ASSURED with a recorded condition until resolved. | BMS/EPMS/CDU controller replacement or reprogramming; Change to sequence of operation; Introduction of new automation or agent authority; Firmware baseline change across a redundant group
MCF-DEP-007 | IMPLEMENTATION | CP-2 | E1; E2 | E3; E4; E5 | P3 F3 C3 R3 T3 I3 | S4 | NORMAL; MAINTENANCE; EMERGENCY | Route evidence no older than the inspection interval; carrier documentation current within 12 months. | Inspection by a person other than the route record author; carrier statements are provider evidence (E5 where independently produced). | Route records with convergence register; Carrier route documentation for diversity-relied circuits | Where a carrier will not disclose routes, a contractual diversity commitment plus independent fibre-path verification (for example latency fingerprinting by a third party) may be used, at confidence no higher than CONF-2. | US4 Critical: an UNKNOWN result on this control sets CG-03 to UNKNOWN (CG-12 trigger); the decision is capped at LIMITED or INCONCLUSIVE per the gate ceiling until the UNKNOWN Record is dispositioned. Supporting gates CG-09 require gate-level evaluation. | Carrier reroute or maintenance notification; Construction or excavation affecting routes; New cable or pipe installation in shared spaces; Fire-zone change
MCF-DEP-008 | DESIGN | CP-1 | E1; E7 | E3; E4; E5 | P3 F3 C3 R3 T2 I2 | S3 | NORMAL; MAINTENANCE; EMERGENCY; RECOVERY | Roster sample covering at least 3 months including holiday periods. | Reviewed by a person outside the operations line management (for example HSE or assurance). | Human dependency analysis; Authorisation register | A tabletop exercise (RES-05) testing staffing for concurrent events may substitute for part of the roster analysis. | US3 Material: an UNKNOWN result requires gate-level evaluation for CG-03, CG-13 and caps the decision at CONDITIONALLY_ASSURED with a recorded condition until resolved. | Change of maintenance contractor; Departure of a key authorised person; Change to shift pattern; New system requiring specialist authorisation
MCF-DEP-009 | IMPLEMENTATION | CP-2 | E1; E2 | E3; E4; E5 | P3 F3 C3 R3 T3 I3 | S4 | NORMAL; MAINTENANCE; EMERGENCY; TRANSITION | Agreements current at assessment date; power quality records covering at least the preceding 12 months. | Contractual evidence from the utility (E5 provider evidence) corroborated by on-site metering (E3). | Grid connection agreement with firm capacity; Demand reconciliation by operating state | Where a connection agreement is under negotiation, a utility offer letter with stated capacity and conditions supports DESIGN-stage assessment only, and the IMPLEMENTATION claim remains UNKNOWN. | US4 Critical: an UNKNOWN result on this control sets CG-03 to UNKNOWN (CG-12 trigger); the decision is capped at LIMITED or INCONCLUSIVE per the gate ceiling until the UNKNOWN Record is dispositioned. Supporting gates CG-05 require gate-level evaluation. | Change to connection agreement, capacity or curtailment terms; Revised energisation date; Demand forecast change; Utility network reinforcement or reconfiguration notice; New water restriction or fuel contract change
MCF-DEP-010 | IMPLEMENTATION | CP-2 | E1; E2 | E3; E4; E5 | P3 F3 C3 R3 T3 I3 | S4 | NORMAL; MAINTENANCE; EMERGENCY; RECOVERY | Register current; carrier documents current within 12 months. | Register entries corroborated by carrier documents and, for a sample, by configuration evidence (router interface descriptions, BGP sessions). | External circuit register; Underlying carrier identification for each diversity-relied circuit | Independent path verification by a third party may substitute for undisclosed carrier routes, at confidence no higher than CONF-2. | US4 Critical: an UNKNOWN result on this control sets CG-03 to UNKNOWN (CG-12 trigger); the decision is capped at LIMITED or INCONCLUSIVE per the gate ceiling until the UNKNOWN Record is dispositioned. Supporting gates CG-10 require gate-level evaluation. | New or cancelled circuit; Carrier merger, acquisition or wholesale change; Carrier reroute notice; Change to out-of-band design
MCF-DEP-011 | IMPLEMENTATION | CP-2 | E1; E2 | E3; E4; E5 | P3 F3 C3 R3 T3 I3 | S3 | NORMAL; MAINTENANCE; RECOVERY | Register current at assessment; entitlements checked against OEM records within 90 days. | Entitlement status verified from the OEM record or portal, not from internal register alone. | OEM dependency register; Entitlement verification for sampled critical assets | An integrator-managed support arrangement is acceptable if the integrator's back-to-back OEM entitlement is evidenced. | US3 Material: an UNKNOWN result requires gate-level evaluation for CG-03, CG-10 and caps the decision at CONDITIONALLY_ASSURED with a recorded condition until resolved. | New asset class or OEM; Entitlement expiry or non-renewal; OEM change to licensing or telemetry model; OEM end-of-support notice
MCF-DEP-012 | IMPLEMENTATION | CP-2 | E1; E2 | E3; E4; E5 | P3 F3 C3 R3 T3 I3 | S4 | NORMAL; DEGRADED; EMERGENCY; RECOVERY | Register current; provider incident history for the preceding 12 months. | Failure behaviour corroborated by configuration evidence or test, not provider marketing material. | Cloud/SaaS dependency register; Evidence that safety and continuity loops do not require cloud services | A completed RES-05 exercise simulating SaaS unavailability may substitute for configuration evidence for the functions exercised. | US4 Critical: an UNKNOWN result on this control sets CG-03 to UNKNOWN (CG-12 trigger); the decision is capped at LIMITED or INCONCLUSIVE per the gate ceiling until the UNKNOWN Record is dispositioned. Supporting gates CG-15, CG-10 require gate-level evaluation. | New cloud/SaaS service adopted for operations; Provider region or architecture change; Provider incident affecting operations; Identity federation change
MCF-DEP-013 | DESIGN | CP-1 | E1; E7 | E3; E4; E5 | P3 F3 C3 R3 T2 I2 | S3 | NORMAL; MAINTENANCE; DEGRADED | Current deployment; recalculated at each capacity change. | Calculation checked by a second analyst. | Concentration analysis; Traceability of limit to impact tolerance | A scheduler-generated report of capacity per fault domain is acceptable if its fault-domain labels are reconciled to RES-02. | US3 Material: an UNKNOWN result requires gate-level evaluation for CG-03, CG-09 and caps the decision at CONDITIONALLY_ASSURED with a recorded condition until resolved. | Cluster expansion or consolidation; Change in job topology or placement policy; Change to fault-domain definitions
MCF-DEP-014 | DESIGN | CP-1 | E1; E7 | E3; E4; E5 | P3 F3 C3 R3 T2 I2 | S3 | NORMAL; RECOVERY | Current; reviewed at least annually. | Review by a person outside the procurement function (engineering or risk). | Supplier concentration analysis with treatments |  | US3 Material: an UNKNOWN result requires gate-level evaluation for CG-03 and caps the decision at CONDITIONALLY_ASSURED with a recorded condition until resolved. | Supplier exit, acquisition or allocation change; Sanctions or export-control change; New critical asset class
MCF-DEP-015 | DESIGN | CP-1 | E1; E7 | E3; E4; E5 | P3 F3 C3 R3 T2 I2 | S3 | NORMAL; EMERGENCY; RECOVERY | Current; reviewed annually and on staff change. | Demonstration observed by someone other than the original holder. | Knowledge concentration register; Evidence of control-logic ownership or escrow | OEM contractual commitment to provide logic within a stated time is acceptable for non-safety logic. | US3 Material: an UNKNOWN result requires gate-level evaluation for CG-13, CG-10 and caps the decision at CONDITIONALLY_ASSURED with a recorded condition until resolved. | Departure of a key holder; Contractor change; New proprietary system
MCF-DEP-016 | EFFECTIVENESS | CP-4 | E2; E3; E4 | E5; E6; E7 | P4 F4 C3 R4 T3 I3 | S4 | DEGRADED; EMERGENCY; RECOVERY | Validation within the interval. | Validation observed by a person independent of the plan owner. | Substitution plan; Validation record with demonstrated time | A documented real event in which the substitute was used is acceptable precedent if it occurred within the interval and conditions were comparable. | US3 Material: an UNKNOWN result requires gate-level evaluation for CG-10, CG-03 and caps the decision at CONDITIONALLY_ASSURED with a recorded condition until resolved. | Change to the dependency or substitute; Expiry of call-off contract; Validation interval elapsed
MCF-DEP-017 | IMPLEMENTATION | CP-2 | E1; E2 | E3; E4; E5 | P3 F3 C3 R3 T3 I3 | S4 | NORMAL; MAINTENANCE; EMERGENCY; RECOVERY | Approved for the current assessment; reconciled within 30 days of fieldwork start. | Boundary approved by a person with authority who is not the assessor performing reconciliation. | Approved boundary statement; Boundary-to-graph reconciliation record |  | US4 Critical: an UNKNOWN result on this control sets CG-02, CG-03 to UNKNOWN (CG-12 trigger); the decision is capped at LIMITED or INCONCLUSIVE per the gate ceiling until the UNKNOWN Record is dispositioned. Where the undetermined item concerns the boundary itself, the UNKNOWN is US5 and the decision is capped at INCONCLUSIVE. | Change in Capability Instance or Service Outcome; New dependency discovered; Provider change; Material architecture change
MCF-DEP-018 | IMPLEMENTATION | CP-2 | E1; E2 | E3; E4; E5 | P3 F3 C3 R3 T3 I3 | S3 | NORMAL; MAINTENANCE; EMERGENCY; RECOVERY | Current; reviewed at contract renewal and annually. | Records corroborated by the provider's own documentation (contract schedule, service description). | Demarcation record; Shared-responsibility record accepted by provider | Contract schedules containing equivalent allocation are acceptable if mapped to functions and states. | US4 Critical: an UNKNOWN result on this control sets CG-13 to UNKNOWN (CG-12 trigger); the decision is capped at LIMITED or INCONCLUSIVE per the gate ceiling until the UNKNOWN Record is dispositioned. Supporting gates CG-03 require gate-level evaluation. | Contract change or renewal; New provider; Incident revealing ambiguous responsibility; Change of demarcation point
MCF-DEP-019 | IMPLEMENTATION | CP-2 | E1; E2 | E3; E4; E5 | P3 F3 C3 R3 T3 I3 | S3 | NORMAL; MAINTENANCE; DEGRADED | Monitoring data for at least 3 months. | Enforcement verified from configuration, not from tenant attestation. | Allocation records; Enforcement configuration evidence |  | US3 Material: an UNKNOWN result requires gate-level evaluation for CG-09, CG-13 and caps the decision at CONDITIONALLY_ASSURED with a recorded condition until resolved. | New tenant; Tenant expansion or hardware generation change; Shared resource capacity change
MCF-DEP-020 | OPERATION | CP-3 | E2; E3 | E4; E5; E6 | P3 F3 C4 R3 T3 I3 | S4 | NORMAL; MAINTENANCE; DEGRADED | At least 6 months of operation (illustrative; profile-defined). | Telemetry extracted by the assessor or from a system not controlled by the party being monitored where possible. | Boundary telemetry for the period; Deviation tickets | Provider-supplied measurements are acceptable if cross-checked against at least one owner-side measurement. | US3 Material: an UNKNOWN result requires gate-level evaluation for CG-09, CG-15 and caps the decision at CONDITIONALLY_ASSURED with a recorded condition until resolved. | New interface or changed contract property; Repeated deviations; Metering change
MCF-DEP-021 | OPERATION | CP-3 | E2; E3 | E4; E5; E6 | P3 F3 C4 R3 T3 I3 | S4 | NORMAL; DEGRADED; MAINTENANCE | At least 6 months. | Indicator data sampled by the assessor from source systems. | Indicator definitions with thresholds; Indicator data for the period |  | US3 Material: an UNKNOWN result requires gate-level evaluation for CG-03 and caps the decision at CONDITIONALLY_ASSURED with a recorded condition until resolved. | New material dependency; Indicator source change; Incident not preceded by indicator warning
MCF-DEP-022 | OPERATION | CP-3 | E2; E3 | E4; E5; E6 | P3 F3 C4 R3 T3 I3 | S4 | NORMAL; DEGRADED | At least 12 months. | Measurement from owner-side tickets and telemetry, not provider self-reporting only. | Owner-side performance measurement | Provider reports are acceptable if reconciled to a sample of owner tickets. | US3 Material: an UNKNOWN result requires gate-level evaluation for CG-13 and caps the decision at CONDITIONALLY_ASSURED with a recorded condition until resolved. | Major provider incident; Contract renewal; Repeated shortfall
MCF-DEP-023 | OPERATION | CP-3 | E2; E3 | E4; E5; E6 | P3 F3 C4 R3 T3 I3 | S4 | NORMAL; TRANSITION | At least 6 months. | Reconciliation by assessor of notifications to graph versions. | Graph version history; Provider notifications |  | US3 Material: an UNKNOWN result requires gate-level evaluation for CG-14, CG-03 and caps the decision at CONDITIONALLY_ASSURED with a recorded condition until resolved. | Change-detection source added or lost; Missed change revealed by incident
MCF-DEP-024 | OPERATION | CP-3 | E2; E3 | E4; E5; E6 | P3 F3 C4 R3 T3 I3 | S4 | NORMAL | One full revalidation cycle. | Revalidation evidence from a source other than the record itself. | Revalidation schedule and evidence |  | US3 Material: an UNKNOWN result requires gate-level evaluation for CG-03 and caps the decision at CONDITIONALLY_ASSURED with a recorded condition until resolved. | Interval elapsed; Change in revalidation source
MCF-PHY-001 | DESIGN | CP-1 | E1; E7 | E5; E6 | P3 F3 C3 R3 T3 I2 | S3 | NORMAL; EMERGENCY | Current assessment within the review interval; hazard data at its latest published edition. | Hazard quantification by a competent specialist; acceptance by a reviewer independent of the site-selection sponsor. | Site hazard assessment; Flood-risk assessment with critical plant levels | Insurer-commissioned natural-hazard survey where it quantifies the same hazards at stated exceedance levels | US3 (Material): the decision is capped at CONDITIONALLY_ASSURED with a recorded condition; the UNKNOWN is carried into the gate-level evaluation of CG-02, CG-03, CG-04. | Revised flood, seismic or wildfire hazard maps; New climate projection adopted by the owner; Relocation or addition of critical plant; Hazard event at or near the site
MCF-PHY-002 | DESIGN | CP-2 | E1; E7 | E3; E5 | P3 F3 C3 R3 T3 I2 | S3 | NORMAL; EMERGENCY | Register current within the review interval. | Threat assessment by a security specialist not responsible for the perimeter budget. | External exposure register; Perimeter protection specification with ratings | Statutory land-use consultation-zone determinations in place of a bespoke industrial-hazard study, where they cover the declared radius | US3 (Material): the decision is capped at CONDITIONALLY_ASSURED with a recorded condition; the UNKNOWN is carried into the gate-level evaluation of CG-09, CG-03. | New hazardous installation, pipeline or transport route within the radius; Change in threat level from the security function; Perimeter layout change; Generator relocation or new exhaust stacks
MCF-PHY-003 | OPERATION | CP-3 | E1; E3 | E4; E6 | P3 F4 C4 R3 T3 I3 | S3 | NORMAL; MAINTENANCE; EMERGENCY | Twelve months of delivery and route records, including at least one heaviest-rack delivery. | Route verification records produced by the logistics or facilities team, sampled by the assessor against physical measurements. | Logistics and access plan; Route rating evidence for the heaviest declared rack | Structural engineer's statement for route slabs where load-test certificates are unavailable | US3 (Material): the decision is capped at CONDITIONALLY_ASSURED with a recorded condition; the UNKNOWN is carried into the gate-level evaluation of CG-10. | Introduction of a heavier rack type or integrated liquid-cooled rack; Site works obstructing a route; Lift or dock replacement; Change of fuel supplier vehicle type
MCF-PHY-004 | DESIGN | CP-1 | E1 | E6; E3 | P3 F3 C3 R3 T3 I2 | S3 | NORMAL; EMERGENCY | Register current within the review interval. | Register reviewed by someone other than the author; agreements verified against signed copies. | Adjacency register | Building fire strategy where it identifies all adjacent occupancies and separations | US3 (Material): the decision is capped at CONDITIONALLY_ASSURED with a recorded condition; the UNKNOWN is carried into the gate-level evaluation of CG-03. | New adjacent tenant or change of use; Construction or demolition adjacent to the facility; Incident in an adjacent occupancy
MCF-PHY-005 | DESIGN | CP-2 | E1; E7 | E5 | P3 F3 C3 R3 T3 I2 | S3 | NORMAL; MAINTENANCE | Current statement reconciled to the latest load schedule. | Capacity statement by a chartered or licensed structural engineer; load schedule reconciliation by the assessor. | Structural capacity statement; Operating-mass load schedule | Original design calculations plus a current letter of reliance from a structural engineer | US3 (Material): the decision is capped at CONDITIONALLY_ASSURED with a recorded condition; the UNKNOWN is carried into the gate-level evaluation of CG-02, CG-04. | New rack type with higher mass or density; Introduction of liquid or immersion cooling; Rooftop plant addition; Change of use of a room
MCF-PHY-006 | IMPLEMENTATION | CP-2 | E1; E2; E3 | E7 | P3 F4 C3 R3 T3 I3 | S3 | NORMAL | Register reconciled within the last 12 months and after each new rack type. | Reconciliation sample selected and checked by the assessor. | Rack-position load register | DCIM asset records with mass fields where they are the controlled source | US3 (Material): the decision is capped at CONDITIONALLY_ASSURED with a recorded condition; the UNKNOWN is carried into the gate-level evaluation of CG-04, CG-14. | New rack type; Retrofit of liquid cooling to existing racks; Hall re-layout
MCF-PHY-007 | IMPLEMENTATION | CP-2 | E1; E3 | E4; E5 | P3 F4 C3 R3 T3 I3 | S3 | NORMAL; EMERGENCY | Commissioning records and a vibration survey after the last plant change. | Sample inspection by the assessor or an independent structural inspector. | Anchorage design; Anchorage inspection records | Manufacturer seismic certification for pre-engineered racks where installed per instructions | US3 (Material): the decision is capped at CONDITIONALLY_ASSURED with a recorded condition; the UNKNOWN is carried into the gate-level evaluation of CG-09. | New equipment class; Seismic hazard revision; Generator or chiller replacement
MCF-PHY-008 | OPERATION | CP-3 | E1; E3 | E6 | P3 F4 C4 R3 T3 I3 | S3 | NORMAL; EMERGENCY | Twelve months including at least one wet season. | Records sampled and roof inspected by the assessor where safe access exists. | Envelope inspection records | Roofing contractor maintenance reports | US3 (Material): the decision is capped at CONDITIONALLY_ASSURED with a recorded condition; the UNKNOWN is carried into the gate-level evaluation of CG-06. | Water ingress incident; Roof works or new penetrations; Severe-weather event
MCF-PHY-009 | IMPLEMENTATION | CP-2 | E1; E2; E3 | E5 | P3 F4 C3 R3 T3 I3 | S3 | NORMAL; MAINTENANCE | Current configuration and plan at assessment date. | Zone continuity inspection by the assessor or an independent security consultant. | Zoning plan; Access-control configuration export | Certified physical-security audit report covering zone continuity, if current | US3 (Material): the decision is capped at CONDITIONALLY_ASSURED with a recorded condition; the UNKNOWN is carried into the gate-level evaluation of CG-15, CG-09. | Floor plan or use change; New critical plant area; Security incident; Threat level change
MCF-PHY-010 | IMPLEMENTATION | CP-4 | E1; E2; E3 | E5 | P3 F4 C3 R3 T3 I3 | S4 | NORMAL; EMERGENCY | Fire strategy current; penetration inspection within the last interval. | Penetration sample inspected by the assessor or a third-party fire-stopping inspector. | Compartmentation drawings; Redundant-path overlay; Penetration inspection records | Third-party certified fire-stopping installer records, where the inspector is independent of the installer | US4 (Critical): an UNKNOWN result on this gate-critical control sets CG-09 to UNKNOWN and caps the decision at LIMITED or INCONCLUSIVE per the gate ceiling until dispositioned. | New cable or pipe routes through compartment boundaries; Hall extension; Fire strategy revision; Introduction of lithium-ion batteries in a new location
MCF-PHY-011 | IMPLEMENTATION | CP-2 | E1; E2; E3 | E4 | P3 F4 C3 R3 T3 I3 | S3 | NORMAL; MAINTENANCE | Current layout; isolation tests within the last 12 months. | Overlay and inspection sample by the assessor. | Water-zone plan; Leak detection configuration | 3D coordination model where it is the controlled as-built source | US3 (Material): the decision is capped at CONDITIONALLY_ASSURED with a recorded condition; the UNKNOWN is carried into the gate-level evaluation of CG-09, CG-04. | Liquid-cooling retrofit or expansion; Leak incident; Re-routing of pipework or busway
MCF-PHY-012 | IMPLEMENTATION | CP-2 | E1; E2; E6 | E3 | P3 F4 C3 R3 T3 I3 | S3 | NORMAL; MAINTENANCE | Current at assessment date. | Disclosure verified by inspection by the assessor. | Shared-infrastructure disclosure; Responsibility matrix | Colocation service description and SLA where they enumerate shared elements | US3 (Material): the decision is capped at CONDITIONALLY_ASSURED with a recorded condition; the UNKNOWN is carried into the gate-level evaluation of CG-13, CG-02. | New tenant adjacent to assessed space; Provider infrastructure change; Contract renewal
MCF-PHY-013 | OPERATION | CP-3 | E2; E3 | E1; E7 | P3 F4 C4 R3 T3 I3 | S4 | NORMAL; MAINTENANCE; EMERGENCY | Twelve months of access reviews and leaver events. | Reconciliation performed by the assessor from system exports obtained under observation. | Rights export; Leaver reconciliation | Independent audit sample of the same population and period | US3 (Material): the decision is capped at CONDITIONALLY_ASSURED with a recorded condition; the UNKNOWN is carried into the gate-level evaluation of CG-15. | Access-control system migration; Security incident involving access; Change of security contractor
MCF-PHY-014 | OPERATION | CP-3 | E3 | E1; E6 | P3 F4 C4 R3 T3 I3 | S3 | NORMAL; MAINTENANCE | A sample from the last six months. | Sample selected by the assessor. | Visitor management records | Manual visitor log where electronic system not used, if sequential and complete | US3 (Material) where the control result could change a decision condition, otherwise US2 (Moderate) with a confidence ceiling of CONF-2 for the affected claims. | Visitor system change; Incident involving a visitor
MCF-PHY-015 | IMPLEMENTATION | CP-2 | E1; E2; E3 |  | P3 F4 C3 R3 T3 I3 | S3 | NORMAL; MAINTENANCE | Current configuration; health logs for three months. | Stills and retrieval performed under assessor observation. | Operational requirement; Retention configuration |  | US3 (Material) where the control result could change a decision condition, otherwise US2 (Moderate) with a confidence ceiling of CONF-2 for the affected claims. | Layout change; VMS upgrade; Security incident
MCF-PHY-016 | EFFECTIVENESS | CP-4 | E2; E3; E4 | E6 | P4 F4 C4 R4 T4 I3 | S4 | NORMAL; EMERGENCY | Twelve months of alarms and exercises, including night shifts. | At least one exercise designed and timed by the assessor or an independent party. | Alarm logs; Exercise records |  | US3 (Material) where the control result could change a decision condition, otherwise US2 (Moderate) with a confidence ceiling of CONF-2 for the affected claims. | Change of guard force or staffing; Control room relocation; Missed target in exercise
MCF-PHY-017 | OPERATION | CP-3 | E3 | E1; E2 | P3 F4 C4 R3 T3 I3 | S3 | NORMAL | Six months of receipts. | Sample selected by the assessor. | Goods-in records |  | US3 (Material) where the control result could change a decision condition, otherwise US2 (Moderate) with a confidence ceiling of CONF-2 for the affected claims. | New logistics provider; Discrepancy or tamper event
MCF-PHY-018 | OPERATION | CP-3 | E1; E3 | E6 | P3 F4 C4 R3 T3 I3 | S3 | NORMAL; MAINTENANCE | Twelve months of moves. | Sample selected by the assessor. | Move plans for sampled moves |  | US3 (Material): the decision is capped at CONDITIONALLY_ASSURED with a recorded condition; the UNKNOWN is carried into the gate-level evaluation of CG-04. | New rack type; Move incident; Change of moving contractor
MCF-PHY-019 | OPERATION | CP-3 | E2; E3 | E1 | P3 F4 C4 R3 T3 I3 | S4 | NORMAL; MAINTENANCE | Twelve months. | Reconciliation reperformed by the assessor for a sample. | Custody inventory; Reconciliation records |  | US3 (Material) where the control result could change a decision condition, otherwise US2 (Moderate) with a confidence ceiling of CONF-2 for the affected claims. | Missing media; Change of RMA provider; New media type
MCF-PHY-020 | OPERATION | CP-3 | E1; E3 | E5 | P3 F4 C4 R3 T3 I3 | S4 | NORMAL; MAINTENANCE | Twelve months of decommissioning. | Certificate reconciliation by the assessor. | Certificates per serial | Witnessed on-site destruction records | US3 (Material) where the control result could change a decision condition, otherwise US2 (Moderate) with a confidence ceiling of CONF-2 for the affected claims. | Change of disposal provider; Large refresh programme; Certificate discrepancy
MCF-PHY-021 | EFFECTIVENESS | CP-5 | E1; E4; E5 | E3 | P4 F4 C4 R4 T4 I3 | S4 | NORMAL; MAINTENANCE | Most recent full test cycle and twelve months of impairments. | Functional test performed or witnessed by a certified fire-system contractor or inspector independent of the design author. | Functional test reports; AHJ or certified inspection record | Insurer engineering survey including witnessed detection tests | US4 (Critical): an UNKNOWN result on this gate-critical control sets CG-04 to UNKNOWN and caps the decision at LIMITED or INCONCLUSIVE per the gate ceiling until dispositioned. | Change of airflow regime (containment, liquid-cooling retrofit); New battery installation; Detector or panel replacement; Fire or false-alarm incident
MCF-PHY-022 | EFFECTIVENESS | CP-5 | E1; E2; E4; E5 | E3 | P4 F4 C4 R4 T4 I3 | S4 | NORMAL; EMERGENCY | Most recent full interface test and enclosure test within interval. | Interface tests witnessed by a party independent of the fire contractor (assessor, insurer or AHJ). | Cause-and-effect matrix; End-to-end interface test report; Enclosure integrity test report | Integrated systems test (IST) report where it exercises the full matrix | US4 (Critical): an UNKNOWN result on this gate-critical control sets CG-04 to UNKNOWN and caps the decision at LIMITED or INCONCLUSIVE per the gate ceiling until dispositioned. | BMS or fire panel logic change; Liquid-cooling installation; Room alteration affecting integrity; Discharge event
MCF-PHY-023 | OPERATION | CP-5 | E1; E3; E4; E5 | E6 | P3 F4 C4 R3 T3 I3 | S4 | NORMAL; EMERGENCY; MAINTENANCE | Twelve months of tests; inspection at assessment. | Fire authority or certified inspector acceptance current; inspection by the assessor. | Egress plans; Door release test; Responder information pack |  | US4 (Critical): an UNKNOWN result on this gate-critical control sets CG-04 to UNKNOWN and caps the decision at LIMITED or INCONCLUSIVE per the gate ceiling until dispositioned. | Containment installation or change; Layout change; New battery or refrigerant system; Fire authority visit with findings
MCF-PHY-024 | EFFECTIVENESS | CP-5 | E1; E2; E4; E5 | E3 | P4 F4 C4 R4 T4 I3 | S4 | NORMAL; EMERGENCY; MAINTENANCE | Most recent test cycle and twelve months of activations. | Test witnessed by an independent electrical or fire engineer. | Scope schedule; Functional test reports | Test during integrated systems test with recorded scope verification | US4 (Critical): an UNKNOWN result on this gate-critical control sets CG-04 to UNKNOWN and caps the decision at LIMITED or INCONCLUSIVE per the gate ceiling until dispositioned. | Change in electrical distribution or CDU controls; Activation event; Code change
MCF-POW-001 | OPERATION | CP-5 | E1; E2; E3; E7 | E5 | P3 F4 C4 R3 T3 I3 | S5 | NORMAL; DEGRADED; RECOVERY | Twelve months of metered demand including the seasonal cooling peak and peak AI utilisation. | Demand model recomputed by the assessor from source data; metered data obtained from the revenue meter operator or EPMS export under observation. | Connection agreement; Demand model; Metered demand data; As-built single-line diagram | Utility capacity statement letter where the agreement is confidential, if it states firm capacity and curtailment terms | US4 (Critical): an UNKNOWN result on this gate-critical control sets CG-05 to UNKNOWN and caps the decision at LIMITED or INCONCLUSIVE per the gate ceiling until dispositioned. | New AI cluster or accelerator generation with higher power limit; Change to connection agreement; Metered peak within margin; Utility network reinforcement or constraint notice
MCF-POW-002 | OPERATION | CP-3 | E2; E3 | E1; E7 | P3 F4 C4 R3 T3 I3 | S4 | NORMAL; DEGRADED | Twelve months of continuous monitoring. | PQ data exported under observation; evaluation by an electrical engineer independent of operations where events exceeded design. | PQ event logs; PQ statistics | Utility-provided PQ data at the PCC, if Class A and covering the period | US3 (Material): the decision is capped at CONDITIONALLY_ASSURED with a recorded condition; the UNKNOWN is carried into the gate-level evaluation of CG-05. | Utility network change; New large load or generator nearby; Unexplained UPS transfers
MCF-POW-003 | DESIGN | CP-2 | E1; E7 | E5; E6 | P3 F3 C3 R3 T3 I2 | S3 | NORMAL; DEGRADED; EMERGENCY | Current topology; interruption history for the declared period. | Topology from the network operator, not the facility's own assumption. | Network operator topology statement | Independent grid study commissioned by the owner using network operator data | US3 (Material): the decision is capped at CONDITIONALLY_ASSURED with a recorded condition; the UNKNOWN is carried into the gate-level evaluation of CG-03, CG-05, CG-09. | Network operator reconfiguration; New substation; Multi-feed outage
MCF-POW-004 | RESILIENCE | CP-5 | E1; E3; E4 | E6; E7 | P4 F4 C4 R4 T4 I3 | S4 | EMERGENCY; DEGRADED; RECOVERY | Most recent exercise within interval; twelve months of curtailment events. | Exercise observed by the assessor or a party independent of the operations team. | Utility contingency plan; Exercise record | Record of a real curtailment event handled per plan | US3 (Material): the decision is capped at CONDITIONALLY_ASSURED with a recorded condition; the UNKNOWN is carried into the gate-level evaluation of CG-05, CG-10. | Change in connection agreement or flexibility contract; Grid emergency event; New AI cluster with different shed characteristics
MCF-POW-005 | EFFECTIVENESS | CP-5 | E1; E2; E3; E4 | E5 | P4 F4 C4 R4 T4 I3 | S5 | NORMAL; MAINTENANCE; EMERGENCY | Commissioning test plus the most recent periodic load test within interval. | Load tests witnessed by a party independent of the generator maintenance contractor. | Rating class evidence; Derating calculation; Load test reports | Recorded real-load operation during a utility outage at or above the declared load, with EPMS data | US4 (Critical): an UNKNOWN result on this gate-critical control sets CG-05 to UNKNOWN and caps the decision at LIMITED or INCONCLUSIVE per the gate ceiling until dispositioned. | Increase in critical load; Generator replacement or controller change; Design ambient revision; Failed load test
MCF-POW-006 | OPERATION | CP-5 | E1; E2; E3; E4 | E5 | P3 F4 C4 R3 T3 I3 | S5 | NORMAL; MAINTENANCE; EMERGENCY | Twelve months of monthly tests including winter and summer. | Test logs reconciled to controller event logs extracted under observation. | Monthly test logs; Controller event logs | Real utility-outage starts with controller logs, if timing is recorded | US4 (Critical): an UNKNOWN result on this gate-critical control sets CG-05 to UNKNOWN and caps the decision at LIMITED or INCONCLUSIVE per the gate ceiling until dispositioned. | Failed start; Controller firmware change; Starting system replacement
MCF-POW-007 | OPERATION | CP-5 | E1; E2; E3; E4 | E5 | P3 F4 C4 R3 T3 I3 | S5 | NORMAL; EMERGENCY; MAINTENANCE | Twelve months of levels and tests. | Fuel test by an accredited laboratory; autonomy recalculated by the assessor. | Autonomy calculation; Fuel level records; Fuel test certificates |  | US4 (Critical): an UNKNOWN result on this gate-critical control sets CG-05 to UNKNOWN and caps the decision at LIMITED or INCONCLUSIVE per the gate ceiling until dispositioned. | Load increase; Tank modification; Fuel type change; Failed fuel test
MCF-POW-008 | RESILIENCE | CP-5 | E1; E3; E4 | E5; E6 | P4 F4 C4 R4 T4 I3 | S4 | EMERGENCY; RECOVERY | Current contracts; exercise within twelve months. | Contracts reviewed directly; supplier capability confirmed with the supplier. | Fuel supply contracts; Refuelling procedure | Government or utility priority fuel scheme membership with documented terms | US3 (Material): the decision is capped at CONDITIONALLY_ASSURED with a recorded condition; the UNKNOWN is carried into the gate-level evaluation of CG-05, CG-03, CG-10. | Supplier change; Regional fuel disruption; Load increase reducing autonomy
MCF-POW-009 | IMPLEMENTATION | CP-5 | E1; E2; E3; E7 | E4; E5 | P3 F4 C3 R3 T3 I3 | S5 | NORMAL; MAINTENANCE; DEGRADED; TRANSITION | Current configuration and twelve months of path loading. | Failure analysis reviewed by an electrical engineer independent of the designer or operator. | As-built single-line diagram; Failure and maintenance-state analysis; Path load data | Independent engineer's topology review report covering the same states | US4 (Critical): an UNKNOWN result on this gate-critical control sets CG-05 to UNKNOWN and caps the decision at LIMITED or INCONCLUSIVE per the gate ceiling until dispositioned. | Load growth; UPS module addition or removal; Change to eco-mode; Distribution reconfiguration
MCF-POW-010 | OPERATION | CP-5 | E1; E2; E3; E4; E5 | E7 | P3 F4 C4 R3 T3 I3 | S5 | NORMAL; MAINTENANCE; DEGRADED; EMERGENCY | Twelve months of monitoring data and the latest capacity test cycle. | Battery safety assessment by a fire or battery safety engineer independent of the supplier; capacity tests witnessed or reviewed independently. | Monitoring alarm configuration; Capacity test reports; Battery safety assessment (Li-ion) | Continuous impedance trending with OEM-validated correlation in place of discharge test for VRLA, if the OEM supports it | US4 (Critical): an UNKNOWN result on this gate-critical control sets CG-04 to UNKNOWN and caps the decision at LIMITED or INCONCLUSIVE per the gate ceiling until dispositioned. | Battery replacement or chemistry change; BMS firmware change; Thermal event; Ambient change in battery room
MCF-POW-011 | EFFECTIVENESS | CP-5 | E1; E2; E3; E4 | E5; E7 | P4 F4 C4 R4 T4 I3 | S5 | NORMAL; EMERGENCY; MAINTENANCE | Latest discharge test within interval; twelve months of loads and battery temperatures. | Runtime recalculated by the assessor; test witnessed independently. | Runtime calculation; Discharge test report | Recorded real-event discharge with EPMS data of sufficient duration and load | US4 (Critical): an UNKNOWN result on this gate-critical control sets CG-05 to UNKNOWN and caps the decision at LIMITED or INCONCLUSIVE per the gate ceiling until dispositioned. | Load increase above threshold; Battery replacement; Battery room temperature change; Generator start-time change
MCF-POW-012 | OPERATION | CP-3 | E2; E3 | E1; E7 | P3 F4 C4 R3 T3 I3 | S4 | NORMAL; MAINTENANCE; DEGRADED | Twelve months. | Reconciliation to UPS controller logs by the assessor. | UPS event logs; Bypass log |  | US3 (Material): the decision is capped at CONDITIONALLY_ASSURED with a recorded condition; the UNKNOWN is carried into the gate-level evaluation of CG-05, CG-09. | Unplanned bypass event; Eco-mode enablement; UPS firmware change
MCF-POW-013 | OPERATION | CP-5 | E1; E3; E4; E5 | E2 | P3 F4 C4 R3 T3 I3 | S4 | NORMAL; MAINTENANCE | Current study; twelve months of condition maintenance. | Arc-flash study by a competent electrical engineer independent of operations; thermography by a certified thermographer. | Arc-flash study; Label sample; Thermography reports | Online thermal monitoring with trending in place of periodic thermography where coverage is complete | US4 (Critical): an UNKNOWN result on this gate-critical control sets CG-04 to UNKNOWN and caps the decision at LIMITED or INCONCLUSIVE per the gate ceiling until dispositioned. | Utility fault-level change; Protection setting change; Switchgear modification; Arc incident
MCF-POW-014 | IMPLEMENTATION | CP-5 | E1; E2; E4; E7 | E5 | P3 F4 C3 R3 T3 I3 | S4 | NORMAL; MAINTENANCE; EMERGENCY | Current study; most recent setting extraction and tests. | Study by a protection engineer; setting comparison reperformed by the assessor. | Coordination study; Setting exports; Secondary injection reports | Independent protection audit with setting verification | US4 (Critical): an UNKNOWN result on this gate-critical control sets CG-09 to UNKNOWN and caps the decision at LIMITED or INCONCLUSIVE per the gate ceiling until dispositioned. | Source change (new generator, UPS); Fault level change; Setting change; Nuisance or non-selective trip event
MCF-POW-015 | OPERATION | CP-3 | E2; E3; E7 | E1 | P3 F4 C4 R3 T3 I3 | S4 | NORMAL; DEGRADED; MAINTENANCE | Twelve months of per-phase peaks including peak AI utilisation. | Failover loads recomputed by the assessor from EPMS data. | Capacity register; Per-phase peak data | DCIM power capacity module if it is the controlled source and uses measured data | US3 (Material): the decision is capped at CONDITIONALLY_ASSURED with a recorded condition; the UNKNOWN is carried into the gate-level evaluation of CG-05, CG-14. | New rack deployment; Rack power-limit increase; Busway extension
MCF-POW-016 | IMPLEMENTATION | CP-4 | E1; E3; E4; E5 | E2 | P3 F4 C3 R3 T3 I3 | S4 | NORMAL; MAINTENANCE | Most recent periodic inspection within interval. | Inspection and test by a qualified electrical inspector. | Periodic inspection and test report |  | US4 (Critical): an UNKNOWN result on this gate-critical control sets CG-04 to UNKNOWN and caps the decision at LIMITED or INCONCLUSIVE per the gate ceiling until dispositioned. | Electrical installation change; Liquid-cooling installation; Lightning strike
MCF-POW-017 | OPERATION | CP-3 | E2; E3 | E7 | P3 F4 C4 R3 T3 I3 | S3 | NORMAL; EMERGENCY; DEGRADED | Twelve months including generator tests. | Data exported under observation. | Voltage statistics; Excursion log |  | US3 (Material): the decision is capped at CONDITIONALLY_ASSURED with a recorded condition; the UNKNOWN is carried into the gate-level evaluation of CG-05. | New load type; UPS mode change; Repeated PSU failures
MCF-POW-018 | OPERATION | CP-3 | E1; E2; E3 | E7 | P3 F4 C4 R3 T3 I3 | S4 | NORMAL; EMERGENCY | Twelve months of PQ data and at least one generator-supplied measurement. | Study by an electrical engineer; data exported under observation. | Harmonic study; PCC measurements |  | US3 (Material): the decision is capped at CONDITIONALLY_ASSURED with a recorded condition; the UNKNOWN is carried into the gate-level evaluation of CG-05. | New rectifier or inverter loads; Filter or PFC change; Generator change
MCF-POW-019 | EFFECTIVENESS | CP-5 | E1; E2; E3; E4 | E5 | P4 F4 C4 R4 T4 I3 | S5 | NORMAL; TRANSITION; EMERGENCY; RECOVERY | Commissioning and most recent periodic transfer tests; twelve months of dip events. | Transfer tests witnessed by an independent commissioning or electrical engineer. | Transfer test reports; Restart test records | Integrated systems test results covering the same transfers | US4 (Critical): an UNKNOWN result on this gate-critical control sets CG-05 to UNKNOWN and caps the decision at LIMITED or INCONCLUSIVE per the gate ceiling until dispositioned. | UPS, STS or ATS change; Cooling drive change; New load class (e.g. accelerator generation); Unexpected load loss on a dip
MCF-POW-020 | EFFECTIVENESS | CP-5 | E1; E2; E3; E4 | E5; E7 | P4 F4 C4 R4 T4 I3 | S5 | NORMAL; EMERGENCY; TRANSITION | Characterisation for each cluster generation; test on generator within the declared interval. | Characterisation reviewed by a power-systems engineer independent of the cluster operator. | Power-dynamics characterisation; Generator load-step or oscillation test record | Validated dynamic simulation calibrated against measured data, where testing on generator with real cluster load is not authorised; supports DESIGN depth only | US4 (Critical): an UNKNOWN result on this gate-critical control sets CG-05 to UNKNOWN and caps the decision at LIMITED or INCONCLUSIVE per the gate ceiling until dispositioned. | New accelerator generation or cluster expansion; Change of power-smoothing configuration; Generator governor or AVR change; Unexplained UPS or generator alarms during training
MCF-POW-021 | IMPLEMENTATION | CP-4 | E1; E2; E3; E4 | E7 | P3 F4 C3 R3 T3 I3 | S4 | NORMAL; TRANSITION; EMERGENCY | Current configuration; twelve months of data completeness. | Point-list reconciliation reperformed by the assessor. | Point list; Configuration baseline; Alarm configuration |  | US4 (Critical): an UNKNOWN result on this gate-critical control sets CG-07 to UNKNOWN and caps the decision at LIMITED or INCONCLUSIVE per the gate ceiling until dispositioned. | EPMS upgrade; Distribution change; Data gap above threshold; Security incident on OT network
MCF-POW-022 | OPERATION | CP-3 | E1; E3 | E7 | P3 F4 C4 R3 T3 I3 | S4 | NORMAL; MAINTENANCE | Twelve months. | Completion statistics recomputed by the assessor from work-order data. | Work order history; Asset-to-programme reconciliation |  | US3 (Material): the decision is capped at CONDITIONALLY_ASSURED with a recorded condition; the UNKNOWN is carried into the gate-level evaluation of CG-05. | Maintenance contractor change; Asset additions; Failure attributed to maintenance
MCF-POW-023 | OPERATION | CP-4 | E1; E3; E5 | E6 | P3 F4 C4 R3 T3 I3 | S4 | MAINTENANCE; EMERGENCY; TRANSITION | Twelve months of switching operations. | Authorisation scheme audited by an independent authorising engineer. | MOP sample; Permit/LOTO records; Authorisation register |  | US4 (Critical): an UNKNOWN result on this gate-critical control sets CG-04 to UNKNOWN and caps the decision at LIMITED or INCONCLUSIVE per the gate ceiling until dispositioned. | Distribution change; Switching incident; Change of maintenance contractor
MCF-POW-024 | RESILIENCE | CP-5 | E1; E2; E3; E4 | E5; E6 | P4 F4 C4 R4 T4 I3 | S5 | FAILED; RECOVERY; SHUTDOWN | Most recent exercise within interval. | Exercise witnessed by a party independent of the operations team. | Restoration plan; Exercise report with milestone times | Record of a real total-loss event and restoration with milestone times | US4 (Critical): an UNKNOWN result on this gate-critical control sets CG-10 to UNKNOWN and caps the decision at LIMITED or INCONCLUSIVE per the gate ceiling until dispositioned. | Change in distribution or control architecture; Generator change; Real total-loss event; Major cooling plant change
MCF-THM-001 | DESIGN | CP-1 | E1; E7 | E5; E6 | P3 F3 C3 R3 T3 I2 | S3 | NORMAL; TRANSITION | Current model version; reviewed at least every 12 months and at each deployment phase | Model review by an engineer not responsible for producing the model | Approved heat-load model version; OEM thermal data per platform | Computational fluid dynamics study that includes the same apportionment; Measured heat-load dataset from metered CDUs and air handlers for existing halls | US3 Material: capacity controls MCF-THM-002/003 cannot be rated CONFORMING against an unverified demand; decision condition recorded | New accelerator platform or rack density; Change of liquid-capture ratio; Measured load deviates beyond tolerance; Deployment phase change
MCF-THM-002 | IMPLEMENTATION | CP-5 | E1; E2; E3; E4 | E5 | P4 F4 C4 R4 T4 I3 | S5 | NORMAL; TRANSITION | Commissioning record plus most recent 3 months of load telemetry | Commissioning witnessed by a commissioning authority independent of the installing contractor | Commissioning report with load-bank results; Current admitted-load register | Retro-commissioning test at partial load with validated extrapolation method reviewed by an independent engineer | US4 Critical: CG-06 Gate Result becomes UNKNOWN for the affected fault domains; decision ceiling per CG-06 | Admitted IT load approaches demonstrated capacity; Equipment replacement or capacity upgrade; Change of design supply temperature
MCF-THM-003 | RESILIENCE | CP-5 | E1; E2; E3; E4 | E5; E7 | P4 F4 C4 R4 T4 I3 | S5 | NORMAL; DEGRADED; MAINTENANCE; EMERGENCY; TRANSITION; RECOVERY | Most recent integrated transient test (≤ 24 months) plus 12 months of operating data | Integrated test witnessed by an independent commissioning or engineering party | N−1 capacity analysis; Time-stamped transient test traces | Validated dynamic thermal simulation calibrated against a partial transient test, reviewed independently | US4 Critical: CG-06 UNKNOWN for affected fault domains; decision ≤ LIMITED until ride-through is evidenced | Load growth above tested level; Change to UPS coverage of mechanical loads; Thermal-storage modification; Any thermal excursion during a power event
MCF-THM-004 | OPERATION | CP-5 | E2; E3; E7 | E1; E6 | P4 F4 C4 R4 T4 I3 | S5 | NORMAL; DEGRADED; EMERGENCY | At least 12 months including the local peak-ambient season | Ambient data cross-checked against an independent meteorological source | Climatic design basis; Peak-season capacity-versus-load trend | Where less than a year of operation exists, manufacturer derated performance plus a witnessed high-ambient test or validated simulation | US4 Critical: CG-06 UNKNOWN for high-ambient states; decision ceiling applied to EMERGENCY/peak-season claims | Observed ambient above design basis; Fouling or performance decline of heat-rejection units; Change to economiser or setpoint strategy; Load growth
MCF-THM-005 | OPERATION | CP-3 | E2; E3; E7 | E1; E6 | P3 F4 C4 R3 T3 I3 | S4 | NORMAL; MAINTENANCE | Most recent 6 months | Sample inspection by a party other than the hall operations team | Inlet temperature telemetry; Sample inspection record | Handheld survey grid at defined points where rack sensors are not deployed | US3 Material: air-side adequacy uncertain; condition recorded against CG-06 supporting evaluation | Rack layout change; New platform with different airflow; Hot-spot alarms above threshold
MCF-THM-006 | IMPLEMENTATION | CP-2 | E1; E2; E3 | E4; E5 | P3 F4 C3 R3 T3 I3 | S3 | NORMAL; MAINTENANCE | Inspection within 6 months | Fire-safety acceptance from the competent fire authority or fire engineer | As-built inspection; Fire-safety acceptance | Thermal imaging survey demonstrating separation where physical inspection is restricted | US3 Material: air separation unverified; CG-06 supporting; any fire-safety acceptance gap escalated to CG-04 evaluation | Row reconfiguration; Containment modification; Fire system change
MCF-THM-007 | IMPLEMENTATION | CP-2 | E1; E2; E3 | E4; E6 | P3 F4 C3 R3 T3 I3 | S3 | NORMAL; MAINTENANCE; DEGRADED | Current configuration plus 6 months maintenance history | Configuration export obtained directly from BMS rather than operator summary | Zone N−1 capacity analysis; Configuration export | Commissioning functional performance test results at site conditions | US3 Material: zone air-side capacity uncertain; CG-06 supporting evaluation required | Supply water temperature change; Unit replacement; Zone load change
MCF-THM-008 | OPERATION | CP-3 | E2; E3; E7 | E1; E6 | P3 F4 C4 R3 T3 I3 | S4 | NORMAL; DEGRADED; MAINTENANCE | Most recent 3 months of telemetry and alarm logs | Spot check with a calibrated reference instrument by the assessor | Point list with thresholds; Alarm and response log | Portable logger survey for halls with incomplete fixed sensors | US2 Moderate: confidence ceiling CONF-2 for air-side operating claims | Sensor replacement or relocation; Threshold change; Missed alarm incident
MCF-THM-009 | DESIGN | CP-1 | E1; E7 | E5; E6 | P3 F3 C3 R3 T3 I2 | S3 | NORMAL; TRANSITION | Current design-basis version | Design review by an engineer independent of the cooling vendor | Design basis; P&ID; OEM requirement documents | OEM-supplied reference design adopted without modification, with deviations listed | US3 Material: liquid-cooling design adequacy uncertain; CG-06 supporting; downstream CDU and loop controls conditioned | New platform or cold-plate generation; Change of TCS fluid; Change of FWS temperature strategy
MCF-THM-010 | EFFECTIVENESS | CP-5 | E1; E2; E3; E4 | E5 | P4 F4 C4 R4 T4 I3 | S5 | NORMAL; DEGRADED; MAINTENANCE; TRANSITION | Test within 12 months plus 3 months of telemetry | Failover test witnessed by a party independent of the CDU vendor | Design-load test record; Pump failover test traces | Operational evidence of an unplanned pump failure with full telemetry, analysed against criteria | US4 Critical: CG-06 UNKNOWN for racks served by untested CDU groups | Racks added to CDU group; CDU firmware or control change; Pump replacement; Filter change to finer rating
MCF-THM-011 | OPERATION | CP-5 | E1; E2; E3; E4 | E5; E7 | P4 F4 C4 R4 T4 I3 | S5 | NORMAL; DEGRADED; MAINTENANCE; RECOVERY | Most recent 6 months of telemetry and all pressure tests since last fill | Pressure test witnessed by a party other than the installer | Telemetry trends; Pressure-test certificates; Make-up log | Inventory reconciliation by expansion-tank level where make-up meters are absent | US4 Critical: CG-06 UNKNOWN for loops with unverified integrity | Loop modification; Unexplained fluid loss; Pressure excursion; Hose or manifold replacement
MCF-THM-012 | OPERATION | CP-3 | E2; E3; E7 | E1; E6 | P3 F4 C4 R3 T3 I3 | S4 | NORMAL; MAINTENANCE; TRANSITION | Most recent 6 months of work orders | Observation of a live connection by the assessor | Coupling register; Sample work orders | Witnessed demonstration on a non-production rack | US3 Material: leak initiation risk unbounded; supports CG-06 and CG-04 evaluation | New coupling type; Coupling leak incident; Rack swap campaign
MCF-THM-013 | EFFECTIVENESS | CP-5 | E2; E3; E4 | E1; E5 | P4 F4 C4 R4 T4 I3 | S5 | NORMAL; DEGRADED; EMERGENCY; RECOVERY | Tests within 12 months; refrigerant records for 12 months | Refrigerant safety inspection by a certified refrigeration engineer | Capacity test at design conditions; Restart test; Refrigerant register | Manufacturer factory witness test plus site performance verification at partial load | US4 Critical: CG-06 UNKNOWN for chilled-water-dependent paths; refrigerant safety gaps escalated to CG-04 | Chiller replacement or refrigerant change; Restart failure; Refrigerant leak
MCF-THM-014 | OPERATION | CP-3 | E2; E3; E7 | E1; E6 | P3 F4 C4 R3 T3 I3 | S4 | NORMAL; DEGRADED; MAINTENANCE | 12 months including summer and winter | Thermal imaging or independent recirculation survey | Approach temperature trends; Maintenance records | Seasonal performance test by the manufacturer | US3 Material: heat-rejection capacity condition recorded; CG-06 supporting | New adjacent heat source; Unit failure; Fouling event
MCF-THM-015 | RESILIENCE | CP-5 | E1; E2; E3; E4 | E5; E7 | P4 F4 C4 R4 T4 I3 | S5 | NORMAL; DEGRADED; EMERGENCY | Test within 12 months; 12 months level data | Utility restriction scenario reviewed with the water utility or an independent hydrologist | Consumption calculation; Switchover test | Contracted tanker supply with tested delivery and connection | US4 Critical: CG-06 UNKNOWN for water-dependent heat rejection under EMERGENCY states | Drought order or utility restriction; Change to evaporative capacity; Storage modification
MCF-THM-016 | DESIGN | CP-1 | E1; E7 | E2; E5 | P3 F3 C3 R3 T3 I2 | S3 | NORMAL; DEGRADED; EMERGENCY | Current version | Review by an engineer independent of the designer | Dependency map; Common-mode register | Fault tree for loss of heat rejection covering the same elements | US3 Material: hidden common mode possible; referred to CG-03 and CG-09 evaluation | New shared plant; Heat-reuse connection; Tenant change in shared facility
MCF-THM-017 | DESIGN | CP-1 | E1; E7 | E5; E6 | P3 F3 C3 R3 T3 I2 | S3 | NORMAL; MAINTENANCE | Current specification | Compatibility confirmed by OEM or fluid supplier technical service | Coolant specification; Safety data sheets | Laboratory compatibility test report for non-standard materials | US3 Material: corrosion or fluid-hazard risk unbounded; CG-04 supporting evaluation | Coolant supplier change; New wetted material; Immersion fluid change
MCF-THM-018 | OPERATION | CP-4 | E1; E3; E4; E5 | E2 | P3 F4 C4 R3 T3 I3 | S4 | NORMAL; MAINTENANCE | 12 months of results | Accredited laboratory analysis; legionella scheme reviewed by an independent competent person | Sample results; Legionella risk assessment (where evaporative systems exist) | Inline monitoring of conductivity/pH with periodic laboratory confirmation | US4 Critical where evaporative systems exist (CG-04 life safety); otherwise US3 Material for CG-06 | Out-of-limit result; Positive legionella result; Change of treatment supplier; System modification
MCF-THM-019 | EFFECTIVENESS | CP-4 | E2; E3; E4 | E1; E5; E7 | P4 F4 C3 R4 T4 I3 | S4 | NORMAL; MAINTENANCE; DEGRADED | 12 months of alarm records; tests within interval | Assessor-witnessed functional test of sampled sensors | Coverage map; Functional test records | Incident evidence of real leak detection with full alarm timeline | US3 Material: leak detection effectiveness uncertain; CG-09 and CG-04 supporting evaluation | New wetted zone; Sensor disabled; Undetected leak incident
MCF-THM-020 | EFFECTIVENESS | CP-5 | E1; E2; E3; E4 | E5 | P4 F4 C3 R4 T4 I3 | S4 | NORMAL; DEGRADED; EMERGENCY; MAINTENANCE | Tests within 12 months | Isolation test witnessed by a party independent of the maintenance contractor | Isolation design; Representative isolation test | Documented real leak incident showing isolation and containment within fault domain | US4 Critical: CG-09 UNKNOWN for liquid-leak containment | Pipework change; Valve failure; Leak propagating beyond domain
MCF-THM-021 | EFFECTIVENESS | CP-5 | E1; E2; E3; E4 | E5 | P4 F4 C3 R4 T4 I3 | S4 | NORMAL; DEGRADED; TRANSITION; FAILED | Tests within 12 months; 3 months control trends | Fail-safe test witnessed by an independent controls engineer | Fail-safe test; Step-load test; Configuration baseline | Recorded production load step with full telemetry analysed against criteria | US4 Critical: CG-07 UNKNOWN for cooling controls | Controller firmware or logic change; Oscillation event; New load profile
MCF-THM-022 | OPERATION | CP-3 | E2; E3; E7 | E1; E6 | P3 F4 C4 R3 T3 I3 | S4 | NORMAL; DEGRADED; MAINTENANCE | 12 months of calibration and fault records | Assessor spot check with reference instrument | Sensor register; Calibration records | Cross-comparison analysis of redundant sensors over the period | US3 Material: telemetry reliability reduced; dependent operating claims capped at CONF-2 | Sensor replacement; Control incident traced to sensor; Calibration overdue
MCF-THM-023 | OPERATION | CP-3 | E2; E3; E7 | E1; E6 | P3 F4 C4 R3 T3 I3 | S4 | MAINTENANCE; TRANSITION; NORMAL | Most recent 6 months of cooling maintenance | Observation of a maintenance activity by the assessor | Method statements; Return-to-service checks | Computerised maintenance management system records with embedded checklists | US3 Material: maintenance-state continuity uncertain; CG-06 and CG-14 supporting | Maintenance-induced incident; New maintenance contractor; Plant change
MCF-THM-024 | RESILIENCE | CP-5 | E1; E2; E3; E4 | E5; E6; E7 | P4 F4 C4 R4 T4 I3 | S5 | RECOVERY; EMERGENCY; FAILED; TRANSITION | Exercise within 12 months | Exercise observed by a party independent of the operating shift | Recovery procedure; Exercise record | Real recovery event with full timeline and analysis | US4 Critical: CG-10 UNKNOWN for thermal recovery | Plant or control change; Failed recovery; Load growth
MCF-ENV-001 | OPERATION | CP-3 | E1; E2; E3 | E7 | P3 F4 C4 R3 T3 I3 | S4 | NORMAL; DEGRADED; MAINTENANCE | Twelve months including the hottest season. | Telemetry extracted under observation; excursion statistics recomputed by the assessor. | Envelope declaration; Telemetry export; Calibration records | Third-party monitoring service data where it is the sensor source | US3 (Material): the decision is capped at CONDITIONALLY_ASSURED with a recorded condition; the UNKNOWN is carried into the gate-level evaluation of CG-06, CG-08. | New hall or loop; Containment change; Setpoint change; Excursion event
MCF-ENV-002 | OPERATION | CP-3 | E2; E3 | E1 | P3 F4 C4 R3 T3 I3 | S3 | NORMAL; DEGRADED | Twelve months including the most humid season. | Telemetry extracted under observation. | Humidity telemetry; Dew point margin trend |  | US3 (Material): the decision is capped at CONDITIONALLY_ASSURED with a recorded condition; the UNKNOWN is carried into the gate-level evaluation of CG-06. | Coolant supply temperature change; Envelope change; Condensation event
MCF-ENV-003 | OPERATION | CP-3 | E3; E4 | E1 | P3 F4 C4 R3 T3 I3 | S3 | NORMAL | Twelve months of coupons. | Coupons analysed by an independent laboratory. | Coupon or monitor reports |  | US3 (Material): the decision is capped at CONDITIONALLY_ASSURED with a recorded condition; the UNKNOWN is carried into the gate-level evaluation of CG-08. | Economiser introduction; Nearby pollution source; Hardware failure trend with corrosion cause
MCF-ENV-004 | IMPLEMENTATION | CP-2 | E1; E3 | E4; E5 | P3 F4 C3 R3 T3 I3 | S3 | NORMAL; EMERGENCY; MAINTENANCE | Current surveys; boundary data covering generator testing. | Noise surveys by a competent acoustic consultant. | Suppression acoustic design note (if gaseous suppression); Occupational noise survey |  | US3 (Material): the decision is capped at CONDITIONALLY_ASSURED with a recorded condition; the UNKNOWN is carried into the gate-level evaluation of CG-08. | New suppression system; New dense hall; Generator or heat-rejection additions; Noise complaint
MCF-ENV-005 | OPERATION | CP-3 | E1; E2; E3; E7 | E5 | P3 F4 C4 R3 T3 I3 | S3 | NORMAL | Twelve consecutive months. | Calculation reperformed by the assessor from meter data. | Calculation workbook; Meter mapping |  | US3 (Material) where the control result could change a decision condition, otherwise US2 (Moderate) with a confidence ceiling of CONF-2 for the affected claims. | Meter change; Boundary change; New on-site generation
MCF-ENV-006 | IMPLEMENTATION | CP-2 | E1; E2; E7 | E3 | P3 F4 C3 R3 T3 I3 | S3 | NORMAL | Twelve months. | Reconciliation reperformed by the assessor. | Allocation method; Reconciliation |  | US3 (Material) where the control result could change a decision condition, otherwise US2 (Moderate) with a confidence ceiling of CONF-2 for the affected claims. | New tenant or cluster; Meter change
MCF-ENV-007 | OPERATION | CP-3 | E2; E3; E7 | E1 | P3 F4 C4 R3 T3 I3 | S3 | NORMAL | Twelve months. | Heat meter data from the off-taker where available. | Load-point efficiency report |  | US3 (Material) where the control result could change a decision condition, otherwise US2 (Moderate) with a confidence ceiling of CONF-2 for the affected claims. | Large occupancy change; Heat reuse contract change
MCF-ENV-008 | DESIGN | CP-2 | E1; E7 | E4 | P3 F3 C3 R3 T3 I2 | S3 | NORMAL; DEGRADED; EMERGENCY | All measures active at assessment date. | Assessment reviewed by an engineer not sponsoring the efficiency measure. | Efficiency measure register; Resilience impact assessments |  | US3 (Material): the decision is capped at CONDITIONALLY_ASSURED with a recorded condition; the UNKNOWN is carried into the gate-level evaluation of CG-05, CG-06, CG-14. | New efficiency measure; Change in redundancy configuration; Incident linked to an efficiency measure
MCF-ENV-009 | OPERATION | CP-3 | E1; E3 | E5 | P3 F4 C4 R3 T3 I3 | S3 | NORMAL; MAINTENANCE | Twelve months. | Microbiological samples analysed by an accredited laboratory. | Treatment monitoring records; Legionella risk assessment (if evaporative) |  | US3 (Material): the decision is capped at CONDITIONALLY_ASSURED with a recorded condition; the UNKNOWN is carried into the gate-level evaluation of CG-06, CG-04. | Source change; Out-of-limit microbiology; System modification
MCF-ENV-010 | OPERATION | CP-3 | E2; E3; E7 | E1 | P3 F4 C4 R3 T3 I3 | S3 | NORMAL | Twelve consecutive months. | Calculation reperformed by the assessor. | WUE calculation; Meter reconciliation to bills |  | US3 (Material) where the control result could change a decision condition, otherwise US2 (Moderate) with a confidence ceiling of CONF-2 for the affected claims. | Meter change; Cooling technology change
MCF-ENV-011 | RESILIENCE | CP-4 | E1; E3; E4 | E7 | P4 F4 C4 R4 T4 I3 | S4 | DEGRADED; EMERGENCY | Exercise within interval. | Exercise observed by the assessor or independent party. | Response plan; Exercise records |  | US3 (Material): the decision is capped at CONDITIONALLY_ASSURED with a recorded condition; the UNKNOWN is carried into the gate-level evaluation of CG-06, CG-03. | Drought declaration; Source change; Cooling plant change
MCF-ENV-012 | OPERATION | CP-3 | E1; E3 | E5 | P3 F4 C4 R3 T3 I3 | S3 | NORMAL; EMERGENCY | Twelve months. | Laboratory results from an accredited laboratory. | Discharge consents; Monitoring records |  | US3 (Material) where the control result could change a decision condition, otherwise US2 (Moderate) with a confidence ceiling of CONF-2 for the affected claims. | New discharge; Permit variation; Spill event
MCF-ENV-013 | DESIGN | CP-1 | E1; E7 | E5 | P3 F3 C3 R3 T3 I2 | S3 | NORMAL | Current reporting year. | Methodology reviewed by an independent verifier where externally reported. | Inventory methodology; Boundary statement | Third-party verification statement covering methodology | US3 (Material) where the control result could change a decision condition, otherwise US2 (Moderate) with a confidence ceiling of CONF-2 for the affected claims. | Acquisition or new site; Methodology change; New regulatory reporting requirement
MCF-ENV-014 | IMPLEMENTATION | CP-2 | E1; E2; E7 | E5 | P3 F4 C3 R3 T3 I3 | S3 | NORMAL | Reporting year. | Registry records obtained from the registry, not only from the broker. | Registry retirement statements |  | US3 (Material) where the control result could change a decision condition, otherwise US2 (Moderate) with a confidence ceiling of CONF-2 for the affected claims. | New PPA; Change in matching claim; Registry change
MCF-ENV-015 | DESIGN | CP-1 | E1; E7 | E5 | P3 F3 C3 R3 T3 I2 | S2 | NORMAL | Current inventory. | Method reviewed by a competent LCA practitioner. | LCA method; EPD/PCF register |  | US3 (Material) where the control result could change a decision condition, otherwise US2 (Moderate) with a confidence ceiling of CONF-2 for the affected claims. | Hardware refresh; New build; Method change
MCF-ENV-016 | OPERATION | CP-3 | E1; E3; E7 | E5 | P3 F4 C4 R3 T3 I3 | S3 | NORMAL | Last two reporting cycles. | Reperformance by the assessor. | Reporting register; Regulatory submissions (if in scope) | Limited or reasonable assurance report by an external verifier | US3 (Material) where the control result could change a decision condition, otherwise US2 (Moderate) with a confidence ceiling of CONF-2 for the affected claims. | New regulatory requirement; Error discovered; Metering change
MCF-ENV-017 | OPERATION | CP-3 | E1; E3 | E5 | P3 F4 C4 R3 T3 I3 | S4 | NORMAL; MAINTENANCE | Twelve months. | Physical count sample by the assessor. | Battery inventory; Quarantine procedure |  | US3 (Material): the decision is capped at CONDITIONALLY_ASSURED with a recorded condition; the UNKNOWN is carried into the gate-level evaluation of CG-04. | Battery replacement programme; Damaged-cell event; Regulation change
MCF-ENV-018 | OPERATION | CP-5 | E1; E3; E4; E5 | E2 | P3 F4 C4 R3 T3 I3 | S4 | NORMAL; MAINTENANCE; EMERGENCY | Twelve months. | Detector tests by a certified contractor; inventory reconciled by the assessor. | Inventory; Leak-check records; Detector test records |  | US4 (Critical): an UNKNOWN result on this gate-critical control sets CG-04 to UNKNOWN and caps the decision at LIMITED or INCONCLUSIVE per the gate ceiling until dispositioned. | Refrigerant change (e.g. to A2L); Leak event; New machinery room; Immersion cooling introduction
MCF-ENV-019 | OPERATION | CP-3 | E1; E3 | E5 | P3 F4 C4 R3 T3 I3 | S4 | NORMAL; MAINTENANCE; EMERGENCY | Twelve months. | Tank inspection by a competent third party where required by regulation. | Containment calculations; Inspection records; Suppressant inventory |  | US3 (Material): the decision is capped at CONDITIONALLY_ASSURED with a recorded condition; the UNKNOWN is carried into the gate-level evaluation of CG-04. | Tank modification; Spill; Suppression system change
MCF-ENV-020 | OPERATION | CP-3 | E1; E3 | E5 | P3 F4 C4 R3 T3 I3 | S3 | NORMAL | Twelve months. | Sample traced by the assessor. | Disposition records; Waste transfer notes |  | US3 (Material) where the control result could change a decision condition, otherwise US2 (Moderate) with a confidence ceiling of CONF-2 for the affected claims. | Large refresh; Change of recycler
MCF-ENV-021 | RESILIENCE | CP-4 | E1; E3; E4; E7 | E5 | P4 F4 C4 R4 T4 I3 | S4 | DEGRADED; EMERGENCY | Exercise before the current hot season; last heat event. | Analysis reviewed by a mechanical engineer independent of operations. | Capacity-at-ambient analysis; Heatwave procedure; Exercise record | Recorded performance during an event at or above design ambient | US3 (Material): the decision is capped at CONDITIONALLY_ASSURED with a recorded condition; the UNKNOWN is carried into the gate-level evaluation of CG-06, CG-05. | Record temperature at site; Climate projection update; Heat-rejection plant change
MCF-ENV-022 | DESIGN | CP-2 | E1; E7 | E5 | P3 F3 C3 R3 T3 I2 | S3 | NORMAL; DEGRADED | Current assessment within three years. | Assessment by a competent hydrology or sustainability specialist. | Water-stress assessment |  | US3 (Material): the decision is capped at CONDITIONALLY_ASSURED with a recorded condition; the UNKNOWN is carried into the gate-level evaluation of CG-03. | Drought declaration; Entitlement renewal; Expansion plan
MCF-ENV-023 | DESIGN | CP-2 | E1; E7 | E4; E5 | P3 F3 C3 R3 T3 I2 | S3 | NORMAL; EMERGENCY | Current assessment; drill within twelve months where defences are demountable. | Assessment by a competent flood-risk specialist. | Climate-adjusted flood assessment |  | US3 (Material): the decision is capped at CONDITIONALLY_ASSURED with a recorded condition; the UNKNOWN is carried into the gate-level evaluation of CG-09. | Flood map revision; Flood event; Climate projection update
MCF-ENV-024 | DESIGN | CP-1 | E1 | E6; E7 | P3 F3 C3 R3 T3 I2 | S3 | NORMAL | Current register. | Reviewed by capability owners. | Resource constraints register |  | US3 (Material): the decision is capped at CONDITIONALLY_ASSURED with a recorded condition; the UNKNOWN is carried into the gate-level evaluation of CG-01, CG-03. | Demand forecast change; Permit renewal; Grid constraint notice
MCF-CMP-001 | DESIGN | CP-1 | E1; E7 | E5; E6 | P3 F3 C3 R3 T3 I2 | S3 | NORMAL; TRANSITION | Current record version | Review by an architect not responsible for procurement | Architecture record; Workload requirement linkage | OEM reference architecture adopted with documented site deviations | US3 Material: compute sufficiency for outcome unverified; CG-08 supporting evaluation | New accelerator generation; Change of workload class; Change of scale-up domain size
MCF-CMP-002 | IMPLEMENTATION | CP-2 | E1; E2; E3 | E4; E6 | P3 F4 C3 R3 T3 I3 | S3 | NORMAL; MAINTENANCE | Most recent 3 conformance scans | Assessor re-runs collection on a sample of nodes | Configuration specification; Per-node conformance report | Manual sample inspection where automation coverage is below target, with sample sized per AIDCF-009 | US3 Material: node configuration drift possible; CG-08 supporting | New node type; BIOS/BMC update; Conformance coverage below target
MCF-CMP-003 | IMPLEMENTATION | CP-2 | E1; E2; E3 | E4; E6 | P3 F4 C3 R3 T3 I3 | S3 | NORMAL; TRANSITION | All racks accepted in the last 12 months (sampled) | Joint sign-off by facility and platform teams | Composition record; Signed interface checklists | OEM factory integration report plus site interface verification | US3 Material: facility interface conformance uncertain; CG-06 and CG-05 supporting | New rack type; Rack relocation; Power shelf change
MCF-CMP-004 | IMPLEMENTATION | CP-2 | E1; E2; E3 | E4; E6 | P3 F4 C3 R3 T3 I3 | S3 | NORMAL; MAINTENANCE; TRANSITION | Current baseline and 3 months of reconciliation | Assessor reconciliation of a node sample against the manifest | Baseline manifest; Fleet reconciliation report | Configuration management database export with per-node attributes | US3 Material: as-built state uncertain; CG-02 supporting | Baseline change; Reconciliation below target; Emergency change
MCF-CMP-005 | DESIGN | CP-1 | E1; E7 | E2; E5 | P3 F3 C3 R3 T3 I2 | S3 | NORMAL; TRANSITION | Current version | Reconciliation performed by assessor against independent sources (fabric LLDP, facility asset register) | Topology export; Reconciliation report | Generated topology from fabric discovery plus manual mapping to facility domains | US3 Material: placement and failure analysis uncertain; CG-02 supporting | Cluster expansion; Rack move; Fabric recabling
MCF-CMP-006 | EFFECTIVENESS | CP-4 | E2; E3; E4 | E5; E7 | P4 F4 C3 R4 T4 I3 | S4 | NORMAL; DEGRADED; RECOVERY | 3 months of telemetry and the last re-validation cycle | Assessor re-runs the bandwidth test on a sample of domains | Bandwidth test results; Drain event log | Vendor diagnostic suite results that include equivalent bandwidth tests | US4 Critical: CG-08 UNKNOWN for training outcomes relying on unvalidated scale-up domains | Interconnect firmware change; Switch tray replacement; Rise in link errors
MCF-CMP-007 | IMPLEMENTATION | CP-2 | E1; E2; E3 | E4; E6 | P3 F4 C3 R3 T3 I3 | S3 | NORMAL; MAINTENANCE | Current configuration | Assessor-designed negative test | Configuration exports; Negative test | Policy-as-code repository with automated tests | US3 Material: isolation uncertain; CG-09 and CG-15 supporting | New tenant; Scheduler upgrade; Partition change
MCF-CMP-008 | RESILIENCE | CP-5 | E1; E2; E4; E7 | E3; E5 | P4 F4 C4 R4 T4 I3 | S5 | NORMAL; DEGRADED; FAILED; RECOVERY | Test or event within 12 months | Concentration analysis reperformed by the assessor | Fault-domain mapping; Concentration analysis; Drain test or incident record | Tabletop plus simulation using scheduler replay, where no live test is authorised (supports DESIGN only) | US4 Critical: CG-09 UNKNOWN for compute containment | Cluster expansion; Facility fault-domain change; Fault-domain loss event
MCF-CMP-009 | OPERATION | CP-4 | E2; E3; E7 | E1; E6 | P3 F4 C4 R3 T3 I3 | S4 | NORMAL; DEGRADED; MAINTENANCE | Most recent 90 days | Assessor reconciliation of one day's report to scheduler and telemetry data | Daily reports; Reconciliation sample | Goodput metrics from the training platform with equivalent exclusions | US4 Critical: CG-08 UNKNOWN for capacity-dependent outcomes | Usable capacity below required; Definition change; Fleet expansion
MCF-CMP-010 | IMPLEMENTATION | CP-2 | E1; E2; E3 | E4; E6 | P3 F4 C3 R3 T3 I3 | S3 | NORMAL; DEGRADED; MAINTENANCE | Current configuration and 3 months of admin logs | Assessor review of configuration export, not operator summary | Configuration export; Admin action logs | Policy-as-code repository with tests | US3 Material: job placement integrity uncertain; CG-08 supporting | Scheduler upgrade; Policy change; Unauthorised admin action
MCF-CMP-011 | OPERATION | CP-3 | E2; E3; E7 | E1; E6 | P3 F4 C4 R3 T3 I3 | S4 | NORMAL; DEGRADED; RECOVERY | Most recent 90 days | Assessor sample of daily reports against scheduler state | Reservation health reports; Reclaim evidence | Scheduler logs showing successful use of reserve during failures | US3 Material: recovery capacity uncertain; CG-10 supporting | Change in failure rate; Reservation change; Failed reclaim
MCF-CMP-012 | OPERATION | CP-3 | E2; E3; E7 | E1; E6 | P3 F4 C4 R3 T3 I3 | S4 | NORMAL; DEGRADED; EMERGENCY | Most recent 90 days | Assessor analysis of raw indicators | Contention policy; Event records | Post-incident reviews covering contention | US2 Moderate: confidence ceiling CONF-2 for performance outcomes | New tenant; Workload mix change; Power-cap event
MCF-CMP-013 | IMPLEMENTATION | CP-4 | E1; E2; E3 | E4; E5 | P4 F4 C4 R3 T3 I3 | S4 | NORMAL; MAINTENANCE; TRANSITION | Current inventory and 3 months of drift history | Assessor queries device firmware directly on a sample | Firmware matrix; Fleet inventory | Vendor fleet-management tool report with raw export | US4 Critical: CG-08 UNKNOWN where fleet firmware state is unverified | Firmware release; Drift above threshold; Security advisory
MCF-CMP-014 | IMPLEMENTATION | CP-2 | E1; E2; E3 | E4; E6 | P3 F4 C3 R3 T3 I3 | S3 | NORMAL; TRANSITION | Current matrix | Assessor sample check of running node stacks | Compatibility matrix; Test records | Vendor-certified stack documentation plus site regression tests | US3 Material: stack compatibility uncertain; CG-08 supporting | Driver or library release; Kernel update; Image change
MCF-CMP-015 | EFFECTIVENESS | CP-4 | E1; E2; E3; E4 | E5 | P4 F4 C3 R4 T4 I3 | S4 | TRANSITION; NORMAL; DEGRADED | Most recent 3 upgrades | Review of go/no-go by a role independent of the release engineer | Staging test records; Stage go/no-go records | Vendor-managed rollout with equivalent stage evidence | US4 Critical: CG-14 UNKNOWN for compute change control | Skipped stage; Fleet-wide incident after upgrade; Process change
MCF-CMP-016 | RESILIENCE | CP-5 | E1; E2; E3; E4 | E5; E7 | P4 F4 C4 R4 T4 I3 | S5 | TRANSITION; RECOVERY; DEGRADED | Most recent 3 changes | Assessor verification of image hashes | Rollback procedures; Staging rollback tests | Real rollback event records | US3 Material: recovery from defective change uncertain; CG-10 supporting | New anti-rollback firmware; Failed rollback; Image retention change
MCF-CMP-017 | OPERATION | CP-3 | E2; E3; E7 | E1; E6 | P3 F4 C4 R3 T3 I3 | S4 | NORMAL; DEGRADED; MAINTENANCE; EMERGENCY | Most recent 90 days | Assessor comparison of raw device query with stored telemetry | Completeness report; Time-sync evidence | Vendor fleet telemetry service export | US3 Material: degradation detection and thermal correlation limited; CG-08 and CG-06 supporting | Collector change; Completeness below target; New accelerator type
MCF-CMP-018 | OPERATION | CP-3 | E2; E3; E7 | E1; E6 | P3 F4 C4 R3 T3 I3 | S4 | NORMAL; DEGRADED; MAINTENANCE | Most recent 90 days | Assessor sample of job failures traced to node health records | Check logs; Drain events | Vendor diagnostic scheduler integration logs | US3 Material: job reliability uncertain; CG-08 supporting | Check suite change; Rise in node-attributed job failures
MCF-CMP-019 | EFFECTIVENESS | CP-5 | E2; E3; E4 | E1; E5; E7 | P4 F4 C3 R4 T4 I3 | S4 | NORMAL; DEGRADED; FAILED | Most recent 90 days | Assessor reconstructs timeline for sampled events | Classification table; Event-to-action timelines; SDC screening results | Vendor RAS service reports with raw events | US4 Critical: CG-08 UNKNOWN for integrity outcomes | New error class; SDC finding; Detection miss
MCF-CMP-020 | OPERATION | CP-3 | E2; E3; E7 | E1; E6 | P3 F4 C4 R3 T3 I3 | S4 | NORMAL; DEGRADED; TRANSITION | Most recent 6 months | Assessor review of raw benchmark output | Baselines; Run results | Production job step-time telemetry with normalisation | US2 Moderate: confidence ceiling CONF-2 for performance outcomes | Baseline change; Unexplained regression
MCF-CMP-021 | IMPLEMENTATION | CP-2 | E1; E2; E3 | E4; E6 | P3 F4 C3 R3 T3 I3 | S3 | TRANSITION; NORMAL | Nodes provisioned in the last 6 months (sample) | Assessor trace of sampled nodes from receipt to acceptance | Burn-in results; Acceptance records | OEM factory burn-in with site acceptance subset | US3 Material: infant-mortality risk; CG-08 supporting | New supplier or lot; Burn-in suite change
MCF-CMP-022 | OPERATION | CP-3 | E2; E3; E7 | E1; E6 | P3 F4 C4 R3 T3 I3 | S4 | NORMAL; DEGRADED; RECOVERY | Most recent 6 months | Assessor physical count of a spares sample | Sizing analysis; Inventory and RMA records | Supplier-managed spares pool contract with evidence of availability | US3 Material: restoration capacity uncertain; CG-10 supporting | Failure-rate increase; Supplier change; Stock-out
MCF-CMP-023 | RESILIENCE | CP-5 | E1; E2; E3; E4 | E5; E7 | P4 F4 C4 R4 T4 I3 | S5 | RECOVERY; FAILED; TRANSITION | Exercise within 12 months | Exercise observed by a party independent of the provisioning team | Dependency map; Mass rebuild exercise record | Real mass-recovery event with full timeline | US4 Critical: CG-10 UNKNOWN for compute recovery | Provisioning system change; Failed rebuild; Cluster growth beyond tested fraction
MCF-CMP-024 | IMPLEMENTATION | CP-2 | E1; E2; E3 | E5; E6 | P3 F4 C3 R3 T3 I3 | S3 | SHUTDOWN; TRANSITION | Retirements in the last 12 months (sample) | Third-party sanitisation certificate or assessor verification sample | Sanitisation certificates; Custody records | Physical destruction certificates | US2 Moderate: no gate; record for data-protection and inventory assertions | Retirement campaign; Disposal vendor change
MCF-STO-001 | DESIGN | CP-1 | E1; E7 | E2; E5 | P3 F3 C3 R3 T3 I2 | S3 | NORMAL; TRANSITION | Current design version | Residency register cross-checked against storage configuration by the assessor | Tier design; Location register; Residency approval | Cloud provider data-location attestations with configuration export | US3 Material: data-tier adequacy or residency uncertain; CG-08 supporting; residency gaps reported to the decision as condition | New dataset class; New storage location or provider; Change in residency obligations
MCF-STO-002 | DESIGN | CP-1 | E1; E7 | E2; E3; E5 | P3 F3 C3 R3 T3 I2 | S3 | NORMAL; DEGRADED; RECOVERY | Current design; interruption data for 90 days | Assessor recomputes bandwidth and interval | Size/bandwidth derivation; Fault-domain separation analysis | Training framework configuration plus measured checkpoint timings | US3 Material: checkpoint adequacy uncertain; CG-10 and CG-08 supporting | New model scale; Change of checkpoint strategy; Interruption rate change
MCF-STO-003 | IMPLEMENTATION | CP-2 | E1; E2; E3 | E4; E6 | P3 F4 C3 R3 T3 I3 | S3 | NORMAL; RECOVERY | Current configuration and 3 months of logs | Assessor recomputes hashes for sampled artefacts | Artefact records; Access logs | Signed artefact manifests verified by deployment tooling | US3 Material: artefact integrity uncertain; CG-10 supporting | Registry migration; Access policy change
MCF-STO-004 | IMPLEMENTATION | CP-2 | E1; E2; E3 | E4; E5 | P3 F4 C3 R3 T3 I3 | S3 | NORMAL | 12 months | Assessor-selected retrieval sample | Fixity results; Retrieval tests | Cloud archive service attestations with retrieval evidence | US2 Moderate: long-term reproducibility confidence capped | Media end-of-life; Retention obligation change
MCF-STO-005 | EFFECTIVENESS | CP-5 | E2; E3; E4 | E5; E7 | P4 F4 C3 R4 T4 I3 | S4 | NORMAL; DEGRADED; RECOVERY | Benchmarks within 12 months; 90 days production timings | Assessor review of raw benchmark output and configuration | Benchmark reports including degraded state; Production checkpoint timings | Production telemetry under peak concurrent checkpoint demonstrating required throughput | US4 Critical: CG-08 UNKNOWN for training outcomes | Storage expansion or upgrade; Client count growth; Checkpoint window breach
MCF-STO-006 | OPERATION | CP-3 | E2; E3; E7 | E1; E6 | P3 F4 C4 R3 T3 I3 | S4 | NORMAL; DEGRADED | 90 days | Assessor review of raw telemetry | Telemetry; Targets | Metadata benchmark at declared concurrency | US3 Material: metadata-induced stalls possible; CG-08 supporting | New dataset format; Saturation event; Metadata server change
MCF-STO-007 | OPERATION | CP-3 | E2; E3; E7 | E1; E6 | P3 F4 C4 R3 T3 I3 | S4 | NORMAL; DEGRADED | 90 days | Assessor check of raw utilisation | Utilisation trend; Quota configuration | Cloud bucket metrics plus quota policies | US3 Material: exhaustion risk; CG-08 supporting | Threshold breach; New tenant; Retention change
MCF-STO-008 | EFFECTIVENESS | CP-4 | E2; E3; E4 | E1; E5; E7 | P4 F4 C3 R4 T4 I3 | S4 | NORMAL; DEGRADED; RECOVERY | Test within 12 months or event in 90 days | Assessor analysis of raw telemetry | Burst test or event telemetry | Simulation calibrated to measured single-job checkpoint | US3 Material: burst resilience uncertain; CG-08 and CG-09 supporting | New large job; Checkpoint scheduling change; Timeout incident
MCF-STO-009 | EFFECTIVENESS | CP-5 | E2; E3; E4 | E1; E5 | P4 F4 C3 R4 T4 I3 | S4 | NORMAL; DEGRADED; RECOVERY | 90 days logs; injection test within 12 months | Assessor recomputes checksums for sampled objects | Checksum records; Injection test record | Real corruption event detected with full trace | US4 Critical: CG-08 UNKNOWN for integrity outcomes | Storage software change; Integrity incident; New checkpoint format
MCF-STO-010 | EFFECTIVENESS | CP-5 | E2; E3; E4 | E1; E5 | P4 F4 C3 R4 T4 I3 | S4 | NORMAL; DEGRADED; FAILED; RECOVERY | Failover test within 12 months | Failover test witnessed by a party independent of the storage vendor | Failover test; Consistency results | Real failover event telemetry | US4 Critical: CG-08 UNKNOWN for storage function | Metadata server change; Consistency error; Failed failover
MCF-STO-011 | OPERATION | CP-3 | E2; E3; E7 | E1; E6 | P3 F4 C4 R3 T3 I3 | S4 | NORMAL; DEGRADED | Most recent 3 cycles | Assessor review of raw scrub logs | Completion records; Error logs | Object-store background verification reports | US2 Moderate: confidence ceiling CONF-2 for integrity operating claims | Scrub cycle overrun; Error-rate rise
MCF-STO-012 | IMPLEMENTATION | CP-2 | E1; E2; E3 | E4; E6 | P3 F4 C3 R3 T3 I3 | S3 | NORMAL; MAINTENANCE; TRANSITION | Current state and 3 months changes | Assessor sample of client mounts | Baseline; Drift report | Infrastructure-as-code repository with plan/apply logs | US3 Material: protection settings may differ from design; CG-14 supporting | Storage software upgrade; Unapproved change
MCF-STO-013 | OPERATION | CP-3 | E2; E3; E7 | E1; E6 | P3 F4 C4 R3 T3 I3 | S4 | NORMAL; RECOVERY | 90 days | Assessor-selected restore sample | Success monitoring; Sample restores | Backup system restores providing the same RPO | US3 Material: logical recovery uncertain; CG-10 supporting | Policy change; Snapshot failures; Restore failure
MCF-STO-014 | RESILIENCE | CP-5 | E1; E2; E3; E4 | E5; E7 | P4 F4 C4 R4 T4 I3 | S5 | NORMAL; DEGRADED; RECOVERY; EMERGENCY | 90 days lag data; test within 12 months | Restore test witnessed or reperformed by a party other than the replication administrator | Lag telemetry; Replica restore test | Provider-managed replication with attestation and customer-run restore | US3 Material: off-domain recovery uncertain; CG-10 supporting | Target change; RPO breach; Jurisdiction change
MCF-STO-015 | RESILIENCE | CP-5 | E1; E2; E4; E7 | E3; E5 | P4 F4 C4 R4 T4 I3 | S5 | NORMAL; DEGRADED; RECOVERY | Rebuild evidence within 12 months | Placement reconciliation reperformed by the assessor | Placement reconciliation; Rebuild record | Vendor durability analysis with site topology inputs | US4 Critical: CG-09 UNKNOWN for storage containment | Expansion; Topology change; Rebuild overrun
MCF-STO-016 | RESILIENCE | CP-5 | E1; E2; E3; E4 | E5; E7 | P4 F4 C4 R4 T4 I3 | S5 | NORMAL; EMERGENCY; RECOVERY | Test within 12 months | Restore test witnessed by a party independent of storage administration | Retention-lock configuration; Deletion-refusal test; Restore test | Offline media copy with custody and restore test | US4 Critical: CG-10 UNKNOWN for recovery from destructive events | Credential model change; Retention change; Restore failure
MCF-STO-017 | EFFECTIVENESS | CP-5 | E2; E3; E4 | E1; E5 | P4 F4 C3 R4 T4 I3 | S4 | NORMAL; DEGRADED; FAILED; RECOVERY | 90 days; test within 12 months | Assessor verification of manifests and checksums | Manifests; Interrupted-write test | Real interruption event showing safe fallback | US4 Critical: CG-08 UNKNOWN for training integrity | Framework change; Checkpoint failure
MCF-STO-018 | RESILIENCE | CP-5 | E1; E2; E3; E4 | E5; E7 | P4 F4 C4 R4 T4 I3 | S5 | RECOVERY; FAILED; DEGRADED | 90 days events; exercise within 12 months | Exercise observed by a party independent of the job owner | Restart timing records; Post-event exercise | Real recovery events with timelines | US4 Critical: CG-10 UNKNOWN for training recovery | Framework change; Restart failure; Cluster change
MCF-STO-019 | RESILIENCE | CP-5 | E1; E2; E3; E4 | E5; E6 | P4 F4 C4 R4 T4 I3 | S5 | RECOVERY; FAILED; SHUTDOWN | Exercise within 12 months | Exercise observed by a party independent of storage operations | Sequence document; Exercise record | Real recovery event timeline | US3 Material: recovery order uncertain; CG-10 supporting | Architecture change; Failed recovery
MCF-STO-020 | RESILIENCE | CP-5 | E1; E2; E3; E4 | E5; E7 | P4 F4 C4 R4 T4 I3 | S5 | RECOVERY; NORMAL | 12 months | Assessor-selected restore sample | Restore records; Checksum results; Resume evidence | Real restores in incidents with full evidence | US4 Critical: CG-10 UNKNOWN for data recovery | Protection change; Restore failure
MCF-STO-021 | OPERATION | CP-3 | E2; E3; E7 | E1; E6 | P3 F4 C4 R3 T3 I3 | S4 | NORMAL; DEGRADED; RECOVERY | 90 days | Assessor comparison with device counters | Completeness reports; Alert definitions | Vendor monitoring service export | US2 Moderate: confidence ceiling CONF-2 | Collector change; Completeness drop
MCF-STO-022 | OPERATION | CP-3 | E2; E3; E7 | E1; E6 | P3 F4 C4 R3 T3 I3 | S4 | NORMAL | 12 months | Assessor review of forecast against actuals | Forecast; Forecast-versus-actual review | Cloud capacity reservations covering forecast | US2 Moderate: capacity confidence capped | Major new workload; Lead-time change
MCF-STO-023 | OPERATION | CP-3 | E2; E3; E7 | E1; E6 | P3 F4 C4 R3 T3 I3 | S4 | NORMAL; DEGRADED | 12 months | Assessor sample of raw health logs | Health data; Replacement records | Vendor predictive-failure service | US2 Moderate: confidence capped | AFR rise; New media model
MCF-STO-024 | IMPLEMENTATION | CP-2 | E1; E2; E3 | E5; E6 | P3 F4 C3 R3 T3 I3 | S3 | SHUTDOWN; TRANSITION | 12 months | Third-party certificates or assessor verification | Certificates; Custody records | Physical destruction certificates | US2 Moderate: no gate; record for data-protection assertions | Disposal vendor change; Media type change
MCF-NET-001 | IMPLEMENTATION | CP-2 | E1; E2; E3 | E5; E6 | P3 F3 C3 R3 T3 I2 | S4 | NORMAL; MAINTENANCE | Point-in-time reconciliation no older than the reconciliation-age parameter, plus change history since the previous reconciliation. | Reconciliation produced from machine-discovered topology, not from the design author's own drawings; reviewed by an engineer other than the design author. | Discovered topology export; Design-to-as-built reconciliation report | Witnessed physical port audit of a statistically justified sample of racks where automated discovery is unavailable, with the sample rationale recorded | US4: CG-08 cannot PASS while as-built topology of a gate-critical fabric is unreconciled; record UNKNOWN U5 or U3 as applicable. | Fabric expansion or re-cabling; Change of topology class or tier count; Major NOS or subnet-manager upgrade altering discovery; Discovery showing unreconciled links
MCF-NET-002 | IMPLEMENTATION | CP-2 | E1; E2; E3 | E5; E6 | P3 F3 C3 R3 T3 I2 | S4 | NORMAL; MAINTENANCE; DEGRADED | Current route evidence within the evidence-age parameter; carrier change notices for the prior 12 months. | External route claims corroborated by a second source (site walk-down of entries, independent route survey, or carrier-signed route letter). | Route evidence for each external circuit in a redundant group; Shared-segment register | Where a carrier will not disclose routes, a contractual diversity guarantee plus an independent survey of building entry and first-kilometre routes, with the remainder recorded as UNKNOWN U2 | US3 by default; US4 against CG-03 where the undisclosed segment carries the only DCI path for a gate-critical outcome. | Carrier grooming or re-routing notice; New circuit or carrier; Civil works near cable routes; Incident affecting two nominally diverse paths
MCF-NET-003 | DESIGN | CP-1 | E1; E7 | E5; E6 | P3 F3 C2 R3 T2 I2 | S3 | NORMAL; DEGRADED; MAINTENANCE; TRANSITION | Current design baseline; reconfirmed at each fabric expansion phase. | Analysis reviewed by a network engineer independent of the design author or by the workload performance team. | Per-tier ratio table; Workload-justification analysis | Simulation or emulation results from a vendor or internal fabric model, provided inputs are traceable to declared workloads | US3: unjustified ratios cap performance assurance; CG-08 SUPPORTING evaluation required. | Change of workload mix (for example introduction of expert-parallel models); Fabric expansion phase; Change of link speed at one tier only
MCF-NET-004 | RESILIENCE | CP-5 | E1; E2; E3; E4 | E5; E7 | P4 F4 C4 R4 T3 I3 | S5 | NORMAL; DEGRADED; MAINTENANCE; FAILED; RECOVERY | Tests or incidents within the previous 24 months and after any topology class change. | Test witnessed by a party independent of the fabric operations team, or independent review of incident analysis. | Fault-domain register; At least one test or analysed incident per fault-domain class; Power/cooling co-location analysis | Pre-production or staging fabric test at representative scale, with a documented representativeness argument | US4: CG-09 cannot PASS while a gate-critical fabric's single-failure blast radius is untested and unanalysed. | Topology or scale change; Subnet-manager or controller architecture change; Power or cooling re-zoning of network rows; Incident with impact beyond the declared domain
MCF-NET-005 | OPERATION | CP-3 | E2; E3 | E1; E7 | P3 F3 C3 R3 T3 I3 | S3 | NORMAL; DEGRADED; MAINTENANCE | Representative operating period of at least 90 days (illustrative) including a maintenance window. | Telemetry extracted directly from the probe system by the assessor, not summarised by the operations team. | Baseline report; Probe telemetry for the period | Workload-derived step-time telemetry where synthetic probes are not permitted, with mapping to path classes | US2: absent baselines reduce confidence in performance claims; US3 if a performance Service Outcome depends on latency tolerance. | NOS or NIC firmware change; Congestion-control parameter change; Topology change; Sustained deviation alert
MCF-NET-006 | OPERATION | CP-3 | E2; E3 | E1; E7 | P3 F3 C3 R3 T3 I3 | S3 | NORMAL; DEGRADED; MAINTENANCE | At least 90 days (illustrative) of continuous counter data. | Counter data sampled directly from devices or the telemetry store by the assessor. | Port error telemetry; Isolation/drain ticket history | Periodic counter snapshots at defined intervals where streaming telemetry is unavailable, with interval justification | US3: unmonitored error classes may hide job-defeating link faults; CG-08 SUPPORTING evaluation. | New optic or cable type; NIC firmware change; Rise in job failures attributed to network; Threshold change
MCF-NET-007 | EFFECTIVENESS | CP-4 | E2; E3; E4 | E5; E7 | P3 F4 C3 R4 T3 I3 | S4 | NORMAL; DEGRADED; MAINTENANCE | Tests within the previous 12 months and after any congestion-control parameter or NOS change; 90 days (illustrative) of counter telemetry. | Test designed or witnessed by an engineer independent of the person who tuned the parameters. | Configuration reconciliation; Incast test results; Pause-storm/watchdog test result | Representative staging-fabric tests with identical NOS, NIC firmware and parameters where production testing is not authorised, with representativeness argument | US4: CG-08 cannot PASS for an RDMA-over-Ethernet fabric while lossless behaviour under congestion is untested. | NOS or NIC firmware change; Change of ECN/PFC/rate-control parameters; Addition of lossless traffic class; Observed pause storm or deadlock
MCF-NET-008 | EFFECTIVENESS | CP-4 | E2; E3; E4 | E5; E7 | P3 F4 C3 R4 T3 I3 | S4 | NORMAL; DEGRADED; TRANSITION | Most recent periodic run within the interval parameter, and runs after each material change in the previous 12 months. | Assessor reperforms or witnesses at least one benchmark run, or raw outputs are independently parsed. | Raw benchmark outputs; Approved targets | Production job step-time telemetry from instrumented workloads, where synthetic benchmarks are impractical, with mapping to operations and scales | US4: CG-08 cannot PASS while collective performance at required scale is unmeasured. | Collective library upgrade; NIC firmware or driver change; Topology or congestion-control change; Regression detected in workloads
MCF-NET-009 | EFFECTIVENESS | CP-4 | E2; E3; E4 | E5; E7 | P3 F4 C3 R4 T3 I3 | S4 | NORMAL; DEGRADED | Test within 12 months and after storage or network capacity change. | Joint test witnessed by an assessor or a party independent of both storage and network teams. | Checkpoint-burst test result; Traffic-class configuration extract | Production checkpoint telemetry from large jobs showing achieved write throughput and concurrent step time | US4: CG-08 cannot PASS while checkpoint-path throughput at declared scale is unverified (scenario X06). | Storage capacity or server change; Checkpoint size growth; Traffic-class change; Cluster expansion
MCF-NET-010 | IMPLEMENTATION | CP-2 | E1; E2; E3 | E5; E6 | P3 F3 C3 R3 T3 I2 | S3 | NORMAL; DEGRADED; MAINTENANCE | Reconciliation within 90 days (illustrative); peak telemetry over a representative period. | Reconciliation reviewed by someone other than the implementer. | Configuration reconciliation; Attachment inventory | Witnessed sample inspection of attachment where automated inventory is incomplete | US3: unreconciled front-end attachment may hide single points of failure for inference outcomes. | Front-end expansion; Routing design change; Load-balancer platform change
MCF-NET-011 | OPERATION | CP-3 | E2; E3 | E1; E7 | P3 F3 C3 R3 T3 I3 | S3 | NORMAL; DEGRADED; MAINTENANCE | At least six months (illustrative) of capacity data and reviews. | Assessor samples telemetry directly. | Capacity telemetry; Failover evidence | Provider service-level reports for managed gateways, with evidence rights per SUP-006 | US3: unknown gateway capacity or failover behaviour conditions the inference availability claim. | Gateway platform change; Traffic growth beyond forecast; Failover anomaly
MCF-NET-012 | EFFECTIVENESS | CP-4 | E2; E3; E4 | E5; E7 | P3 F4 C3 R4 T3 I3 | S4 | NORMAL; DEGRADED | Tests within 12 months and after isolation model change; onboarding records for the period. | Reachability tests executed or witnessed by the security function independent of fabric operations. | Reachability test results; Configuration-to-tenant reconciliation | Staging-fabric performance-isolation tests with identical configuration, with representativeness argument | US3 for single-tenant estates; US4 against CG-09 for multi-tenant platforms where isolation is a declared outcome. | New tenant class; Isolation mechanism change; Cross-tenant incident
MCF-NET-013 | IMPLEMENTATION | CP-2 | E1; E2; E3 | E5; E6 | P3 F3 C3 R3 T3 I2 | S3 | NORMAL; MAINTENANCE | Reconciliation within 90 days (illustrative). | Reachability scan run by the security function. | Device-to-segment inventory; Reachability evidence | Firewall and ACL rule analysis where active scanning is not permitted | US3; escalates to US4 against CG-15 where BMCs or facility gateways are reachable from tenant networks. | New device class; Management network redesign; Scan finding
MCF-NET-014 | IMPLEMENTATION | CP-2 | E1; E2; E3 | E5; E6 | P3 F3 C3 R3 T3 I2 | S3 | NORMAL; MAINTENANCE; FAILED; RECOVERY | Most recent reachability check within the interval and checks over the prior six months. | Assessor samples console reachability live with read-only login. | Console mapping inventory; Reachability check reports | Witnessed manual console checks on a sample where automated checks are unavailable | US3: unknown console reach weakens recovery assurance; SUPPORTING evaluation for CG-10. | Console server replacement; Rack moves; Identity source change
MCF-NET-015 | RESILIENCE | CP-5 | E1; E2; E3; E4 | E5; E7 | P4 F4 C4 R4 T3 I3 | S5 | NORMAL; FAILED; EMERGENCY; RECOVERY | Isolation test within the interval parameter; health telemetry for six months. | Test witnessed by the recovery or resilience function independent of network operations. | OOB dependency analysis; Isolation test record | Scenario exercise with simulated isolation (credentials and paths forced to fallback) where full isolation is not authorised, with residual UNKNOWN recorded | US4: CG-10 cannot PASS while OOB independence from the systems it recovers is unverified. | OOB redesign; Identity provider change; Change of OOB carrier; Recovery exercise failure
MCF-NET-016 | EFFECTIVENESS | CP-4 | E2; E3; E4 | E5; E7 | P3 F4 C3 R4 T3 I3 | S4 | NORMAL; EMERGENCY; FAILED; RECOVERY | Test within the interval; all uses in the previous 12 months. | Security function reviews use logs independently of network operations. | Test records; Use and rotation records | Tabletop plus a single live test on a non-production device of each class where production tests are not authorised | US3; US4 against CG-10 if no tested emergency access exists for gate-critical fabric controllers. | Vault platform change; Identity provider change; Break-glass use; Personnel departure from dual-control holders
MCF-NET-017 | DESIGN | CP-1 | E1; E7 | E5; E6 | P3 F3 C2 R3 T2 I2 | S3 | NORMAL; MAINTENANCE | Current approved version. | Review by a qualified cabling designer other than the author. | Site cabling standard | Adoption of an operator-wide standard with site addendum | US2: absent standard reduces confidence in physical-layer claims; US3 where NET-018 shows optics failures attributable to cabling. | New fibre or connector type; New hall or density class; Recurring physical-layer incidents
MCF-NET-018 | IMPLEMENTATION | CP-2 | E1; E2; E3 | E5; E6 | P3 F3 C3 R3 T3 I2 | S3 | NORMAL; MAINTENANCE | Inventory within 30 days (illustrative); diagnostics for 90 days. | Inventory extracted by assessor from devices. | Installed optics inventory; Qualified-optics matrix | Sample-based physical inspection with serial capture where diagnostics are not readable | US3: unqualified optics at scale are a common-mode exposure; escalate to US4 under CG-08 if failure analysis shows lot-level defects. | New optic vendor or part; Optics firmware release; Failure-rate spike; Supplier substitution
MCF-NET-019 | OPERATION | CP-3 | E2; E3 | E1; E7 | P3 F3 C3 R3 T3 I3 | S3 | NORMAL; MAINTENANCE | At least six months (illustrative) of changes. | Assessor selects the sample from device link-event logs rather than from the work-order system. | Work orders; Link-event logs for reconciliation |  | US3: link events without matching work orders indicate uncontrolled physical change; CG-14 SUPPORTING. | Unplanned outage caused by patching; Change of field services provider
MCF-NET-020 | IMPLEMENTATION | CP-2 | E1; E2; E3 | E5; E6 | P3 F3 C3 R3 T3 I2 | S3 | NORMAL; MAINTENANCE; RECOVERY | Most recent audit within 12 months (illustrative). | Physical audit performed by the assessor or a party independent of the record maintainers. | Audit records; Electronic reconciliation |  | US3: inaccurate path records undermine diversity (CG-03) and recovery (CG-10) analysis. | Major expansion; Audit accuracy below target; Incident where records misled responders
MCF-NET-021 | EFFECTIVENESS | CP-4 | E2; E3; E4 | E5; E7 | P3 F4 C3 R4 T3 I3 | S4 | NORMAL; DEGRADED; FAILED; RECOVERY | Failover test within the interval and after the last upgrade. | Test witnessed by a party independent of fabric operations. | Failover test record; Placement analysis | Staging test at representative scale where production failover is not authorised | US3; US4 against CG-08 for InfiniBand fabrics where subnet-manager failover is untested. | Controller software upgrade; Fabric scale change; Controller incident
MCF-NET-022 | OPERATION | CP-3 | E2; E3 | E1; E7 | P3 F3 C3 R3 T3 I3 | S4 | NORMAL; MAINTENANCE; TRANSITION; RECOVERY | At least six months (illustrative) of changes and drift reports. | Assessor runs or reperforms a drift comparison on a sample of devices. | Drift reports; Staged change records; Restore test record |  | US4: uncontrolled NOS/firmware change on a gate-critical fabric defeats CG-14; CG-08 SUPPORTING. | NOS major version; Automation platform change; Change-induced incident; Drift above threshold
MCF-NET-023 | OPERATION | CP-3 | E2; E3 | E1; E7 | P3 F3 C3 R3 T3 I3 | S3 | NORMAL; DEGRADED; MAINTENANCE; RECOVERY | At least 90 days (illustrative). | Assessor queries the telemetry store directly. | Coverage report; Gap reports |  | US2: gaps reduce confidence of all NET OPERATION claims relying on telemetry. | Telemetry platform change; New device class; Gap rate above tolerance
MCF-NET-024 | EFFECTIVENESS | CP-4 | E2; E3; E4 | E5; E7 | P3 F4 C3 R4 T3 I3 | S4 | NORMAL; DEGRADED; FAILED; RECOVERY | Tests within 12 months (illustrative); telemetry for 90 days. | Assessor samples device time offset directly. | Circular-dependency analysis; Failure test records | Analysed incidents of time-source or DNS loss in the period | US3; US4 against CG-10 where a circular dependency could prevent cold start (X19). | Time architecture change; GNSS anomaly; DNS/AAA platform change; Cluster hosting a core service
MCF-OPS-001 | OPERATION | CP-3 | E2; E3 | E4; E5; E6 | P3 F3 C4 R3 T3 I3 | S4 | NORMAL; EMERGENCY; MAINTENANCE | At least 3 months of rosters including night, weekend and holiday periods. | Attendance records from access-control or time systems, not rosters alone. | Emergency task analysis; Attendance records against minimum | For unstaffed or lightly staffed sites (for example edge inference), a remote NOC with demonstrated dispatch times plus automated safe-state design may substitute, if the task analysis shows no manual action is required within the time-to-impact. | US3 Material: an UNKNOWN result requires gate-level evaluation for CG-13, CG-10 and caps the decision at CONDITIONALLY_ASSURED with a recorded condition until resolved. | Change in shift pattern or headcount; New system with manual emergency actions; Change in time-to-impact (density increase); Incident where response was delayed
MCF-OPS-002 | IMPLEMENTATION | CP-2 | E1; E2 | E3; E4; E5 | P3 F3 C3 R3 T3 I3 | S3 | NORMAL; MAINTENANCE; EMERGENCY; RECOVERY | Current. | Interviews performed by the assessor with role holders selected by the assessor. | Responsibility and authority matrix with named holders |  | US4 Critical: an UNKNOWN result on this control sets CG-13 to UNKNOWN (CG-12 trigger); the decision is capped at LIMITED or INCONCLUSIVE per the gate ceiling until the UNKNOWN Record is dispositioned. Supporting gates CG-14 require gate-level evaluation. | Organisational change; Role holder change; New function or provider; Incident with authority confusion
MCF-OPS-003 | OPERATION | CP-3 | E2; E3 | E4; E5; E6 | P3 F3 C4 R3 T3 I3 | S4 | NORMAL; MAINTENANCE; DEGRADED | Sample of at least 20 handovers over 3 months (illustrative). | Assessor reconciles handover content to registers. | Handover records; Reconciliation to permit register |  | US3 Material: an UNKNOWN result requires gate-level evaluation for CG-04, CG-14 and caps the decision at CONDITIONALLY_ASSURED with a recorded condition until resolved. | Change to shift pattern; Incident attributable to handover
MCF-OPS-004 | OPERATION | CP-3 | E2; E3 | E4; E5; E6 | P3 F3 C4 R3 T3 I3 | S4 | NORMAL; MAINTENANCE; EMERGENCY | 12 months of permits. | Assessor cross-references permits to register independently. | Authorisation register; Permit-to-authorisation reconciliation |  | US4 Critical: an UNKNOWN result on this control sets CG-04 to UNKNOWN (CG-12 trigger); the decision is capped at LIMITED or INCONCLUSIVE per the gate ceiling until the UNKNOWN Record is dispositioned. Supporting gates CG-13 require gate-level evaluation. | New task class or system; Incident involving competence; Change of contractor
MCF-OPS-005 | IMPLEMENTATION | CP-2 | E1; E2 | E3; E4; E5 | P3 F3 C3 R3 T3 I3 | S3 | NORMAL; MAINTENANCE; EMERGENCY; RECOVERY | Current. | As-built cross-check by assessor during walk-down. | Procedure register with EOP coverage; As-built cross-check | Electronic procedures on a system with independent power and offline availability. | US3 Material: an UNKNOWN result requires gate-level evaluation for CG-10, CG-13, CG-14 and caps the decision at CONDITIONALLY_ASSURED with a recorded condition until resolved. | Change to equipment or configuration; Incident revealing procedure gap; Review interval elapsed
MCF-OPS-006 | OPERATION | CP-3 | E2; E3 | E4; E5; E6 | P3 F3 C4 R3 T3 I3 | S4 | MAINTENANCE; TRANSITION | 12 months of non-routine work. | Sample selected by the assessor from work-order system, not from MOP register. | Executed MOPs with sign-off; Linked approvals |  | US4 Critical: an UNKNOWN result on this control sets CG-14 to UNKNOWN (CG-12 trigger); the decision is capped at LIMITED or INCONCLUSIVE per the gate ceiling until the UNKNOWN Record is dispositioned. Supporting gates CG-04 require gate-level evaluation. | Incident during maintenance; New equipment type
MCF-OPS-007 | OPERATION | CP-3 | E2; E3 | E4; E5; E6 | P3 F3 C4 R3 T3 I3 | S4 | MAINTENANCE; EMERGENCY; NORMAL | 12 months of permits. | Worksite verification by assessor or HSE function. | Permit sample; Worksite audit records |  | US4 Critical: an UNKNOWN result on this control sets CG-04 to UNKNOWN (CG-12 trigger); the decision is capped at LIMITED or INCONCLUSIVE per the gate ceiling until the UNKNOWN Record is dispositioned. | Safety incident or near miss; New hazard type; Change of permit system
MCF-OPS-008 | OPERATION | CP-3 | E2; E3 | E4; E5; E6 | P3 F3 C4 R3 T3 I3 | S4 | MAINTENANCE; EMERGENCY | 12 months. | Field audit by HSE or a person independent of the work team. | Equipment-specific LOTO procedures; LOTO records for sampled hazardous jobs |  | US4 Critical: an UNKNOWN result on this control sets CG-04 to UNKNOWN (CG-12 trigger); the decision is capped at LIMITED or INCONCLUSIVE per the gate ceiling until the UNKNOWN Record is dispositioned. | Near miss or injury; New equipment with stored energy; Procedure change
MCF-OPS-009 | DESIGN | CP-1 | E1; E7 | E3; E4; E5 | P3 F3 C3 R3 T2 I2 | S3 | MAINTENANCE; NORMAL | Current approved version. | Engineering approval independent of the maintenance contractor. | Maintenance strategy per critical class with capacity check | An RCM analysis record may substitute for a narrative strategy. | US3 Material: an UNKNOWN result requires gate-level evaluation for CG-05, CG-06 and caps the decision at CONDITIONALLY_ASSURED with a recorded condition until resolved. | New asset class; OEM requirement change; Failure revealing strategy gap; Load increase reducing maintenance headroom
MCF-OPS-010 | OPERATION | CP-3 | E2; E3 | E4; E5; E6 | P3 F3 C4 R3 T3 I3 | S4 | NORMAL; MAINTENANCE | 12 months. | Specialist reports from qualified technicians; assessor samples raw data. | Condition monitoring records; Exceedance work orders | Continuous online monitoring data in lieu of periodic surveys. | US3 Material: an UNKNOWN result requires gate-level evaluation for CG-05, CG-06 and caps the decision at CONDITIONALLY_ASSURED with a recorded condition until resolved. | Failure not preceded by detected deterioration; New asset class
MCF-OPS-011 | OPERATION | CP-3 | E2; E3 | E4; E5; E6 | P3 F3 C4 R3 T3 I3 | S4 | NORMAL; MAINTENANCE | 12 months. | Certificates from accredited calibration providers where available (E5). | Calibration register; Certificates for sample | In-situ comparison against a calibrated reference with recorded results. | US3 Material: an UNKNOWN result requires gate-level evaluation for CG-07 and caps the decision at CONDITIONALLY_ASSURED with a recorded condition until resolved. | Sensor replacement; Control instability; Out-of-tolerance result
MCF-OPS-012 | OPERATION | CP-3 | E2; E3 | E4; E5; E6 | P3 F3 C4 R3 T3 I3 | S4 | NORMAL; DEGRADED; MAINTENANCE | 12 months. | CMMS extract by assessor reconciled to register. | CMMS overdue report reconciled to register |  | US3 Material: an UNKNOWN result requires gate-level evaluation for CG-05, CG-06, CG-13 and caps the decision at CONDITIONALLY_ASSURED with a recorded condition until resolved. | Overdue count rises above threshold; Failure of deferred asset
MCF-OPS-013 | OPERATION | CP-3 | E2; E3 | E4; E5; E6 | P3 F3 C4 R3 T3 I3 | S4 | NORMAL; DEGRADED; EMERGENCY | At least 3 months of alarm logs including at least one upset event where one occurred. | Assessor computes metrics from raw alarm logs. | Master alarm database; Raw alarm logs |  | US4 Critical: an UNKNOWN result on this control sets CG-07 to UNKNOWN (CG-12 trigger); the decision is capped at LIMITED or INCONCLUSIVE per the gate ceiling until the UNKNOWN Record is dispositioned. Supporting gates CG-06, CG-05 require gate-level evaluation. | New monitoring system or integration; Alarm flood incident; Setpoint change programme
MCF-OPS-014 | OPERATION | CP-3 | E2; E3 | E4; E5; E6 | P3 F3 C4 R3 T3 I3 | S4 | DEGRADED; EMERGENCY; RECOVERY | 12 months. | Assessor reconstructs timelines from source logs for a sample. | Incident records with timelines | Where no qualifying incident occurred, a scenario exercise (RES-05) supports the OPERATION claim at confidence no higher than CONF-2. | US3 Material: an UNKNOWN result requires gate-level evaluation for CG-10, CG-13 and caps the decision at CONDITIONALLY_ASSURED with a recorded condition until resolved. | Major incident; Process change; Organisational change
MCF-OPS-015 | OPERATION | CP-3 | E2; E3 | E4; E5; E6 | P3 F3 C4 R3 T3 I3 | S4 | NORMAL; RECOVERY | 12 months. | RCA facilitated by a person not directly involved in the incident. | RCA reports for incidents above threshold |  | US3 Material: an UNKNOWN result requires gate-level evaluation for CG-09 and caps the decision at CONDITIONALLY_ASSURED with a recorded condition until resolved. | Recurring incident; RCA overdue
MCF-OPS-016 | EFFECTIVENESS | CP-4 | E2; E3; E4 | E5; E6; E7 | P4 F4 C3 R4 T3 I3 | S4 | NORMAL | At least 12 months. | Verification by a person other than the action owner. | Effectiveness verification records |  | US3 Material: an UNKNOWN result requires gate-level evaluation for CG-14 and caps the decision at CONDITIONALLY_ASSURED with a recorded condition until resolved. | Recurrence; Overdue actions
MCF-OPS-017 | IMPLEMENTATION | CP-2 | E1; E2 | E3; E4; E5 | P3 F3 C3 R3 T3 I3 | S4 | NORMAL; MAINTENANCE; RECOVERY | Current; reconciliations for 12 months. | Live state captured by assessor or automated system independent of the configuration manager. | Baseline index; Live-to-baseline reconciliation |  | US4 Critical: an UNKNOWN result on this control sets CG-14 to UNKNOWN (CG-12 trigger); the decision is capped at LIMITED or INCONCLUSIVE per the gate ceiling until the UNKNOWN Record is dispositioned. Supporting gates CG-02, CG-07 require gate-level evaluation. | Change implemented; Drift detected; Recovery event
MCF-OPS-018 | OPERATION | CP-3 | E2; E3 | E4; E5; E6 | P3 F3 C4 R3 T3 I3 | S4 | MAINTENANCE; TRANSITION; NORMAL | 12 months. | Assessor reconciles detected changes (drift, logs) to records independently. | Change records; Unrecorded-change reconciliation |  | US4 Critical: an UNKNOWN result on this control sets CG-14 to UNKNOWN (CG-12 trigger); the decision is capped at LIMITED or INCONCLUSIVE per the gate ceiling until the UNKNOWN Record is dispositioned. Supporting gates CG-03 require gate-level evaluation. | Change-related incident; Process or tool change
MCF-OPS-019 | OPERATION | CP-3 | E2; E3 | E4; E5; E6 | P3 F3 C4 R3 T3 I3 | S4 | MAINTENANCE; DEGRADED; EMERGENCY; NORMAL | 6 months. | Assessor extracts forced points and overrides from systems directly. | Register; System override extract reconciled |  | US3 Material: an UNKNOWN result requires gate-level evaluation for CG-14, CG-07, CG-04 and caps the decision at CONDITIONALLY_ASSURED with a recorded condition until resolved. | Incident involving temporary configuration; System upgrade affecting override visibility
MCF-OPS-020 | EFFECTIVENESS | CP-4 | E2; E3; E4 | E5; E6; E7 | P4 F4 C3 R4 T3 I3 | S4 | MAINTENANCE; TRANSITION; NORMAL | 12 months. | Validation reviewed by someone other than the implementer. | Validation evidence attached to closed changes |  | US4 Critical: an UNKNOWN result on this control sets CG-14 to UNKNOWN (CG-12 trigger); the decision is capped at LIMITED or INCONCLUSIVE per the gate ceiling until the UNKNOWN Record is dispositioned. Supporting gates CG-10 require gate-level evaluation. | Failed change; Change process modification
MCF-OPS-021 | OPERATION | CP-3 | E2; E3 | E4; E5; E6 | P3 F3 C4 R3 T3 I3 | S4 | NORMAL; MAINTENANCE | 12 months. | Assessor recomputes headroom for a sample from telemetry. | Capacity reports by element; Admission records |  | US3 Material: an UNKNOWN result requires gate-level evaluation for CG-05, CG-06 and caps the decision at CONDITIONALLY_ASSURED with a recorded condition until resolved. | Deployment; Density increase; Capacity element change
MCF-OPS-022 | OPERATION | CP-3 | E2; E3 | E4; E5; E6 | P3 F3 C4 R3 T3 I3 | S4 | NORMAL; DEGRADED | 6 months. | Assessor recomputes indicators from source data for a sample. | Indicator definitions and data |  | US3 Material: an UNKNOWN result caps the decision at CONDITIONALLY_ASSURED with a recorded condition; downgrade to US2 (confidence ceiling CONF-2) only where the assessor records that no control result or decision condition depends on it. | New Service Outcome; Monitoring platform change
MCF-OPS-023 | OPERATION | CP-3 | E2; E3 | E4; E5; E6 | P3 F3 C4 R3 T3 I3 | S4 | NORMAL; MAINTENANCE | 6 months. | Assessor extracts balance data directly. | Balance monitoring data |  | US3 Material: an UNKNOWN result requires gate-level evaluation for CG-05, CG-06, CG-09 and caps the decision at CONDITIONALLY_ASSURED with a recorded condition until resolved. | Deployment; Hardware generation change
MCF-OPS-024 | OPERATION | CP-3 | E2; E3 | E4; E5; E6 | P3 F3 C4 R3 T3 I3 | S4 | NORMAL | 12 months. | Assessor traces figures to sources. | Reports for period |  | US3 Material: an UNKNOWN result requires gate-level evaluation for CG-13 and caps the decision at CONDITIONALLY_ASSURED with a recorded condition until resolved. | Reporting change; Organisational change
MCF-RES-001 | DESIGN | CP-1 | E1; E7 | E5; E6 | P3 F3 C2 R3 T2 I2 | S3 | NORMAL; DEGRADED; EMERGENCY; RECOVERY | Current approved version, reviewed within 12 months (illustrative). | Approved by the capability owner and reviewed by the resilience owner; author distinct from approver. | Approved tolerance statement; Business-impact analysis | Contractual service levels where they fully express the tolerances, with the business-impact rationale recorded | US5: undefined tolerances affect every resilience and recovery gate (CG-09, CG-10); decision ≤ INCONCLUSIVE. | New Capability Instance; New customer commitment; Change in workload criticality; Regulatory change
MCF-RES-002 | EFFECTIVENESS | CP-4 | E2; E3; E4 | E5; E7 | P3 F4 C3 R4 T3 I3 | S4 | DEGRADED; EMERGENCY; TRANSITION | Tests within 12 months (illustrative) and after material change to power, cooling or scheduler. | Test witnessed by a party independent of platform operations. | Degradation mode catalogue; Test or event records | Partial-scale tests extrapolated with documented analysis where full-scale tests are not authorised | US3: unverified degradation modes condition the decision; CG-09/CG-10 SUPPORTING evaluation. | Change in UPS autonomy or cooling ride-through; Scheduler change; New workload priority class
MCF-RES-003 | DESIGN | CP-1 | E1; E7 | E5; E6 | P3 F3 C2 R3 T2 I2 | S3 | NORMAL; DEGRADED; MAINTENANCE; EMERGENCY; RECOVERY; TRANSITION | Current version, reviewed within 12 months (illustrative). | Reviewed by a cross-domain panel including facilities, network, compute, storage and security. | Scenario library; Applicability rationale |  | US3: missing scenarios limit coverage of CG-09/CG-10 evidence; US4 if a prioritised scenario is excluded without rationale. | Major incident; Architecture change; New site hazard; Annual review
MCF-RES-004 | DESIGN | CP-1 | E1; E7 | E5; E6 | P3 F3 C2 R3 T2 I2 | S3 | NORMAL; EMERGENCY; RECOVERY | Current version. | Matrix confirmed by interviews with a sample of named owners. | Appointment record; Responsibility matrix |  | US4 against CG-13 where a recovery-critical element has no owner. | Organisational change; New provider; Owner departure
MCF-RES-005 | IMPLEMENTATION | CP-2 | E1; E2; E3 | E5; E6 | P3 F3 C3 R3 T3 I2 | S4 | NORMAL; MAINTENANCE; DEGRADED | Reconciliation within the age parameter. | Reconciled by a party other than the model author, using primary as-built sources. | Fault-domain model; Reconciliation record; Shared-domain register | Graph-based dependency model meeting AIDCF-014 with automated reconciliation | US4: CG-09 cannot PASS while the site fault-domain model is unreconciled for gate-critical outcomes. | Electrical or cooling re-zoning; Rack placement change; Expansion; Incident affecting more than one domain
MCF-RES-006 | IMPLEMENTATION | CP-2 | E1; E2; E3 | E5; E6 | P3 F3 C3 R3 T3 I2 | S4 | NORMAL; MAINTENANCE; DEGRADED | Current configuration; maintenance within manufacturer interval. | Inspection by domain specialists independent of the register author. | Boundary register; Configuration or inspection evidence |  | US3; US4 against CG-09 where the boundary protects a gate-critical outcome. | Boundary device replacement; Bypass applied; Layout change
MCF-RES-007 | IMPLEMENTATION | CP-2 | E1; E2; E7 | E3; E4; E5 | P3 F3 C3 R3 T3 I2 | S4 | NORMAL; DEGRADED; MAINTENANCE; FAILED | Current; updated after material change. | Reviewed by a cross-domain panel independent of the analyst. | Blast-radius analysis; Exceedance register | Graph-query outputs from a conformant AIDCF-014 model with human review | US4: CG-09 cannot PASS while blast radius for gate-critical scenarios is unquantified. | Fault-domain model change; New common-mode dependency; Incident exceeding predicted blast radius
MCF-RES-008 | RESILIENCE | CP-5 | E1; E2; E3; E4 | E5; E7 | P4 F4 C4 R4 T3 I3 | S5 | NORMAL; DEGRADED; MAINTENANCE; FAILED; EMERGENCY | Within the validation cycle. | Tests witnessed by an independent party (E5) for gate-critical boundaries. | Validation plan; Results for gate-critical boundaries | Analysed real incident demonstrating isolation, with event evidence | US4: untested gate-critical boundaries leave CG-09 UNKNOWN. | Boundary change; Failed test; Incident; Cycle expiry
MCF-RES-009 | DESIGN | CP-1 | E1; E7 | E5; E6 | P3 F3 C2 R3 T2 I2 | S3 | EMERGENCY; FAILED; RECOVERY | Current approved version, reviewed within 12 months (illustrative). | Approved by the capability owner and reviewed by the resilience owner. | Approved strategy |  | US3; US4 against CG-10 where no strategy exists for a gate-critical outcome. | New site or provider; Tolerance change; Major incident
MCF-RES-010 | EFFECTIVENESS | CP-4 | E2; E3; E4 | E5; E7 | P3 F4 C3 R4 T3 I3 | S4 | EMERGENCY; RECOVERY; FAILED | Test within the interval. | Test witnessed by the resilience owner's function. | Relocation test record; Contract or reservation evidence |  | US3; US4 against CG-10 where the continuity strategy depends solely on alternate capacity. | Capacity contract change; Accelerator generation change; Software stack change
MCF-RES-011 | IMPLEMENTATION | CP-2 | E1; E2; E5 | E3; E6 | P3 F3 C3 R3 T3 I2 | S3 | EMERGENCY; FAILED; RECOVERY | Within evidence age. | Third-party evidence (E5) where available; otherwise contractual attestation corroborated by inquiry. | Provider continuity evidence; Reconciliation | Independent audit reports covering continuity scope | US3; US4 against CG-03 where a sole provider's continuity is unknown. | Provider change; Provider incident; Contract renewal
MCF-RES-012 | DESIGN | CP-1 | E1; E7 | E5; E6 | P3 F3 C2 R3 T2 I2 | S3 | DEGRADED; EMERGENCY; RECOVERY | Current approved version. | Approval by the capability owner, review by commercial/contract owner. | Approved priority scheme |  | US3: absent priorities condition recovery decisions. | New tenant commitment; Workload criticality change
MCF-RES-013 | IMPLEMENTATION | CP-2 | E1; E2; E3 | E5; E6 | P3 F3 C3 R3 T3 I2 | S5 | FAILED; RECOVERY; SHUTDOWN; EMERGENCY | Verified against a test within 24 months (illustrative). | Verified by a party independent of the map author, preferably through test observation. | Recovery dependency map; Circular-dependency analysis | Graph-based dependency model with automated cycle detection and human review | US4: CG-10 cannot PASS while circular recovery dependencies are unanalysed. | New control-plane service; Identity architecture change; Storage platform change; Recovery test discovering missing dependency
MCF-RES-014 | RESILIENCE | CP-5 | E1; E2; E3; E4 | E5; E7 | P4 F4 C4 R4 T3 I3 | S5 | SHUTDOWN; FAILED; RECOVERY; TRANSITION; EMERGENCY | Integrated test within the interval. | Witnessed by an independent party (E5) for gate-critical outcomes. | Restoration sequence; Integrated test record with stage timings | Segmented tests (for example power-to-cooling at site level; network-to-control-plane at cluster level) with interface hand-offs explicitly tested, plus a full tabletop walk-through | US4: CG-10 cannot PASS while the restoration sequence is untested end-to-end or by segments with tested hand-offs. | Major architecture change; New control-plane dependency; Failed or incomplete test; Real restoration event
MCF-RES-015 | EFFECTIVENESS | CP-4 | E2; E3; E4 | E5; E7 | P3 F4 C3 R4 T3 I3 | S4 | RECOVERY; FAILED; MAINTENANCE | Restore tests within interval. | Restore test observed by a party independent of the system administrators. | Restore test records; Integrity verification evidence |  | US3; US4 against CG-10 where BMS/EPMS or fabric controller configuration has no tested restore. | Backup platform change; System class added; Compromise incident
MCF-RES-016 | RESILIENCE | CP-5 | E1; E2; E3; E4 | E5; E7 | P4 F4 C4 R4 T3 I3 | S5 | NORMAL; FAILED; RECOVERY; DEGRADED | Restart test within 6 months (illustrative); integrity logs for 90 days. | Restart test witnessed independently of the training team. | Checkpoint policy; Restart test record; Integrity verification logs | Production restart events with recorded resumption times and training-state checks | US4: CG-10 cannot PASS while checkpoint restart is untested for gate-critical training outcomes. | Model size growth; Storage platform change; Framework change; Failed restart
MCF-RES-017 | OPERATION | CP-3 | E3; E4 | E1; E2 | P3 F3 C3 R3 T3 I3 | S3 | NORMAL; MAINTENANCE | 12 months (illustrative). | Assessor samples from asset registers rather than from completed-test lists. | Test records; Defect records |  | US3: programme gaps reduce support for CG-05/06/08/10 claims. | Programme change; Repeated test failures
MCF-RES-018 | RESILIENCE | CP-5 | E1; E2; E3; E4 | E5; E7 | P4 F4 C4 R4 T3 I3 | S5 | NORMAL; DEGRADED; EMERGENCY; FAILED; RECOVERY; TRANSITION | Within the cycle for each prioritised scenario. | Witnessed by an independent party (E5). | Integrated test records; Safety case | Analysed real events with equivalent capability-level measurements | US4: CG-10 cannot PASS for an outcome whose prioritised scenarios have never been integrated-tested or analysed from real events. | Major architecture change; New prioritised scenario; Cycle expiry; Real event revealing new behaviour
MCF-RES-019 | OPERATION | CP-3 | E3; E6 | E1; E4 | P3 F3 C3 R3 T3 I3 | S3 | EMERGENCY; RECOVERY; FAILED | 12 months (illustrative). | Facilitated or observed by a party independent of the plan authors. | Exercise reports; Action tracker |  | US2 for confidence; US3 if no cyber-physical scenario was ever exercised. | Crisis team change; Major incident; New scenario
MCF-RES-020 | OPERATION | CP-3 | E1; E3 | E4; E7 | P3 F3 C3 R3 T3 I3 | S3 | NORMAL; RECOVERY | 12 months (illustrative). | Assessor traces from source test/incident reports to the register. | Lessons register; Retest evidence for closed gate-critical items |  | US3: unclosed gate-critical lessons condition the decision. | New test or incident report
MCF-RES-021 | EFFECTIVENESS | CP-4 | E1; E3; E4; E6 | E5 | P3 F4 C3 R4 T3 I3 | S4 | EMERGENCY; FAILED; RECOVERY | Exercises within 12 months (illustrative). | Exercises observed by a party independent of the crisis team. | Exercise/event records with timings; Decision logs |  | US3; escalates to US4 against CG-13 if no decision authority exists for controlled shutdown. | Organisational change; Communication platform change; Event post-review
MCF-RES-022 | OPERATION | CP-3 | E1; E3 | E6 | P3 F3 C3 R3 T3 I3 | S3 | EMERGENCY; RECOVERY | 12 months (illustrative). | Assessor reconciles logs with obligation deadlines. | Notification logs; Obligation register |  | US2; US3 where regulatory notification timeliness cannot be established. | New regulatory obligation; New customer contract
MCF-RES-023 | OPERATION | CP-3 | E1; E2; E3 | E6 | P3 F3 C3 R3 T3 I3 | S3 | EMERGENCY; RECOVERY | 12 months (illustrative). | Assessor identifies emergency changes from configuration drift and logs, not only from the change system. | Emergency change records; Retrospective reviews |  | US3; affects CG-14 SUPPORTING evaluation. | Major incident; Procedure change
MCF-RES-024 | OPERATION | CP-3 | E1; E3; E7 | E6 | P3 F3 C3 R3 T3 I3 | S3 | RECOVERY; NORMAL | 24 months (illustrative). | Reviews facilitated by a party independent of the teams involved. | Post-event reviews; Reassessment trigger records |  | US3: unreviewed events may invalidate existing evidence. | Material event
MCF-SUP-001 | DESIGN | CP-1 | E1; E7 | E3; E4; E5 | P3 F3 C3 R3 T2 I2 | S3 | NORMAL | Assessment valid for the current contract term. | Technical approval by an engineer not in the procurement line. | Capability assessment with engineering approval | Prior successful delivery of the same product at a comparable site by the same supplier, documented by acceptance records, may replace part of the reference check. | US3 Material: an UNKNOWN result requires gate-level evaluation for CG-03 and caps the decision at CONDITIONALLY_ASSURED with a recorded condition until resolved. | New critical supplier; Contract renewal; Supplier acquisition or restructuring; Significant delivery or quality failure
MCF-SUP-002 | OPERATION | CP-3 | E2; E3 | E4; E5; E6 | P3 F3 C4 R3 T3 I3 | S4 | NORMAL | At least 12 months. | At least one external information source (credit agency, public filings) per supplier. | Monitoring records for the period | Group-level monitoring by a parent organisation is acceptable if it covers the specific suppliers. | US3 Material: an UNKNOWN result requires gate-level evaluation for CG-03 and caps the decision at CONDITIONALLY_ASSURED with a recorded condition until resolved. | Adverse financial signal; Plant disruption; Sanctions or export-control change; Allocation change
MCF-SUP-003 | IMPLEMENTATION | CP-2 | E1; E2 | E3; E4; E5 | P3 F3 C3 R3 T3 I3 | S3 | NORMAL | Certificates current; incoming quality for 12 months. | Third-party certificates or audit reports preferred (E5). | QMS evidence; PSIRT/disclosure evidence for firmware suppliers | Owner-performed supplier audit may replace third-party certificate. | US3 Material: an UNKNOWN result requires gate-level evaluation for CG-08, CG-15 and caps the decision at CONDITIONALLY_ASSURED with a recorded condition until resolved. | Certificate expiry; Product security incident; Quality escape
MCF-SUP-004 | IMPLEMENTATION | CP-2 | E1; E2 | E3; E4; E5 | P3 F3 C3 R3 T3 I3 | S4 | NORMAL; RECOVERY | Current; refreshed at renewal. | Corroboration from a second source (market intelligence, teardown, certification records) for a sample. | Sub-tier disclosure records for critical classes | Industry consortium sub-tier mapping may substitute where suppliers participate. | US4 Critical: an UNKNOWN result on this control sets CG-03 to UNKNOWN (CG-12 trigger); the decision is capped at LIMITED or INCONCLUSIVE per the gate ceiling until the UNKNOWN Record is dispositioned. | Supplier change of contract manufacturer; Sub-tier disruption reported; Renewal
MCF-SUP-005 | IMPLEMENTATION | CP-2 | E1; E2 | E3; E4; E5 | P3 F3 C3 R3 T3 I3 | S3 | NORMAL; EMERGENCY; RECOVERY | Current contracts. | Comparison checked by engineering, not only procurement. | Contracts with measurable service levels |  | US3 Material: an UNKNOWN result requires gate-level evaluation for CG-10, CG-13 and caps the decision at CONDITIONALLY_ASSURED with a recorded condition until resolved. | Contract renewal; Tolerance change; Supplier change
MCF-SUP-006 | IMPLEMENTATION | CP-2 | E1; E2 | E3; E4; E5 | P3 F3 C3 R3 T3 I3 | S3 | NORMAL | Current contracts; request log for 12 months. | Not applicable beyond document review. | Evidence-rights clauses | Independent assurance reports (for example SOC 2 or ISO certification audit reports) with access to underlying evidence on request. | US3 Material: an UNKNOWN result requires gate-level evaluation for CG-03 and caps the decision at CONDITIONALLY_ASSURED with a recorded condition until resolved. | Renewal; Refused evidence request
MCF-SUP-007 | OPERATION | CP-3 | E2; E3 | E4; E5; E6 | P3 F3 C4 R3 T3 I3 | S4 | NORMAL; DEGRADED | At least 6 months. | Assessor cross-checks a sample of public supplier advisories against the intake log. | Notification log; Intake test record |  | US3 Material: an UNKNOWN result requires gate-level evaluation for CG-03, CG-15 and caps the decision at CONDITIONALLY_ASSURED with a recorded condition until resolved. | Missed notification; Contact change; New supplier
MCF-SUP-008 | DESIGN | CP-1 | E1; E7 | E3; E4; E5 | P3 F3 C3 R3 T2 I2 | S3 | NORMAL; TRANSITION | Current contracts. | Legal and engineering review recorded. | Exit clauses; Exit plans for sole-source suppliers |  | US3 Material: an UNKNOWN result requires gate-level evaluation for CG-10 and caps the decision at CONDITIONALLY_ASSURED with a recorded condition until resolved. | Renewal; Supplier distress; Licensing model change
MCF-SUP-009 | IMPLEMENTATION | CP-2 | E1; E2 | E3; E4; E5 | P3 F3 C3 R3 T3 I3 | S3 | NORMAL; RECOVERY | 12 months of purchase orders. | Sample drawn by assessor from the purchasing system. | Approved source list; Purchase order sample | Where a purchasing system cannot enforce restrictions, a documented manual pre-approval with monthly reconciliation is acceptable. | US3 Material: an UNKNOWN result requires gate-level evaluation for CG-08, CG-04 and caps the decision at CONDITIONALLY_ASSURED with a recorded condition until resolved. | OEM changes authorised distributors; Exception purchase; Counterfeit incident
MCF-SUP-010 | OPERATION | CP-3 | E2; E3 | E4; E5; E6 | P3 F3 C4 R3 T3 I3 | S4 | NORMAL; RECOVERY | 12 months of receipts. | Inspection by receiving staff independent of the requisitioner. | Receipt inspection records; Quarantine log | OEM-direct shipment with tamper-evident seals verified on receipt may reduce inspection depth. | US3 Material: an UNKNOWN result requires gate-level evaluation for CG-04, CG-08 and caps the decision at CONDITIONALLY_ASSURED with a recorded condition until resolved. | Counterfeit alert from industry or OEM; Change of distributor; Emergency purchase
MCF-SUP-011 | OPERATION | CP-3 | E2; E3 | E4; E5; E6 | P3 F3 C4 R3 T3 I3 | S4 | NORMAL | 12 months of critical shipments. | Assessor reconciles records from forwarder and site independently. | Custody records for sampled shipments | Secure freight programme certification of the carrier may reduce sampling depth. | US3 Material: an UNKNOWN result requires gate-level evaluation for CG-08 and caps the decision at CONDITIONALLY_ASSURED with a recorded condition until resolved. | Theft or tamper event; Change of forwarder; New staging location
MCF-SUP-012 | EFFECTIVENESS | CP-4 | E2; E3; E4 | E5; E6; E7 | P4 F4 C3 R4 T3 I3 | S4 | NORMAL | Exercise within the interval. | Exercise scenario set by the assessor or a party independent of the asset manager. | Exercise record; Reconciliation sample | A real recall response within the interval is acceptable in place of an exercise. | US3 Material: an UNKNOWN result requires gate-level evaluation for CG-08, CG-03 and caps the decision at CONDITIONALLY_ASSURED with a recorded condition until resolved. | Asset register platform change; Major deployment; Interval elapsed
MCF-SUP-013 | IMPLEMENTATION | CP-2 | E1; E2 | E3; E4; E5 | P3 F3 C3 R3 T3 I3 | S3 | NORMAL; MAINTENANCE; RECOVERY | Current; sample from the preceding 12 months of deployments. | Reconciliation by assessor from device-reported versions. | Repository inventory; Deployed-version reconciliation | For devices updated only by OEM field engineers, an OEM-signed release record per update is acceptable. | US3 Material: an UNKNOWN result requires gate-level evaluation for CG-15, CG-14 and caps the decision at CONDITIONALLY_ASSURED with a recorded condition until resolved. | New device class; Repository platform change; OEM channel change
MCF-SUP-014 | EFFECTIVENESS | CP-4 | E2; E3; E4 | E5; E6; E7 | P4 F4 C3 R4 T3 I3 | S4 | NORMAL; MAINTENANCE; RECOVERY | Verification logs for 12 months; tests within 24 months (illustrative). | Rejection test witnessed or performed by security function. | Verification logs; Rejection test records | OEM documentation of enforced verification may substitute for testing of device classes where no non-production unit exists, at confidence no higher than CONF-2. | US3 Material: an UNKNOWN result requires gate-level evaluation for CG-15, CG-08 and caps the decision at CONDITIONALLY_ASSURED with a recorded condition until resolved. | New device class; Change to signing keys or enforcement settings; OEM key compromise advisory
MCF-SUP-015 | EFFECTIVENESS | CP-4 | E2; E3; E4 | E5; E6; E7 | P4 F4 C3 R4 T3 I3 | S4 | MAINTENANCE; TRANSITION; NORMAL | Rollouts in the preceding 12 months. | Health-gate criteria set by a team other than the deploying team. | Compatibility matrix; Wave records |  | US3 Material: an UNKNOWN result requires gate-level evaluation for CG-14, CG-08, CG-09 and caps the decision at CONDITIONALLY_ASSURED with a recorded condition until resolved. | New hardware generation; Major software stack change; Rollout incident
MCF-SUP-016 | OPERATION | CP-3 | E2; E3 | E4; E5; E6 | P3 F3 C4 R3 T3 I3 | S4 | NORMAL; MAINTENANCE | 12 months. | Assessor checks a sample of public advisories against the log. | Advisory tracking log |  | US3 Material: an UNKNOWN result requires gate-level evaluation for CG-15 and caps the decision at CONDITIONALLY_ASSURED with a recorded condition until resolved. | Exploited vulnerability in a used product; New product class
MCF-SUP-017 | OPERATION | CP-3 | E2; E3 | E4; E5; E6 | P3 F3 C4 R3 T3 I3 | S4 | NORMAL; RECOVERY; DEGRADED | 12 months of stock movement. | Physical count by the assessor or a party independent of the stores controller. | Spares strategy with basis; Physical count reconciliation | Vendor-managed inventory with real-time stock visibility and audit rights. | US3 Material: an UNKNOWN result requires gate-level evaluation for CG-10, CG-05, CG-06 and caps the decision at CONDITIONALLY_ASSURED with a recorded condition until resolved. | Change in installed population; Lead-time change; Stock-out event; New asset class
MCF-SUP-018 | DESIGN | CP-1 | E1; E7 | E3; E4; E5 | P3 F3 C3 R3 T2 I2 | S3 | NORMAL; RECOVERY | Register refreshed within interval. | Observed lead times from recent orders corroborate quotations. | Lead-time register; Tolerance comparison |  | US3 Material: an UNKNOWN result requires gate-level evaluation for CG-10, CG-03 and caps the decision at CONDITIONALLY_ASSURED with a recorded condition until resolved. | Supplier lead-time change; Growth plan change; Failure of a long-lead unit
MCF-SUP-019 | RESILIENCE | CP-5 | E1; E2; E3; E4 | E5; E6; E7 | P4 F4 C4 R4 T3 I3 | S5 | EMERGENCY; RECOVERY | Validation within interval. | Exercise facilitated by a party independent of the recovery owner. | Prerequisite register; Validation record | Real event precedent within interval. | US3 Material: an UNKNOWN result requires gate-level evaluation for CG-10, CG-05 and caps the decision at CONDITIONALLY_ASSURED with a recorded condition until resolved. | Change of logistics provider; Site access change; Export-control change; Regional event
MCF-SUP-020 | OPERATION | CP-3 | E2; E3 | E4; E5; E6 | P3 F3 C4 R3 T3 I3 | S4 | NORMAL | Current; review records for 12 months. | Vendor dates verified against vendor notices. | Lifecycle register |  | US3 Material: an UNKNOWN result requires gate-level evaluation for CG-03 and caps the decision at CONDITIONALLY_ASSURED with a recorded condition until resolved. | Vendor end-of-life notice; Asset class addition
MCF-SUP-021 | IMPLEMENTATION | CP-2 | E1; E2 | E3; E4; E5 | P3 F3 C3 R3 T3 I3 | S4 | NORMAL; MAINTENANCE; EMERGENCY | Current; register changes over 12 months. | Account exports obtained by the assessor directly or under observation. | Account exports from sampled control-plane systems; Third-party identity register | For devices without local account export, configuration backup files reviewed by the assessor. | US4 Critical: an UNKNOWN result on this control sets CG-15 to UNKNOWN (CG-12 trigger); the decision is capped at LIMITED or INCONCLUSIVE per the gate ceiling until the UNKNOWN Record is dispositioned. Supporting gates CG-13 require gate-level evaluation. | New supplier access; System added; Credential exposure event
MCF-SUP-022 | OPERATION | CP-3 | E2; E3 | E4; E5; E6 | P3 F3 C4 R3 T3 I3 | S4 | NORMAL; MAINTENANCE; EMERGENCY | At least 3 months of sessions. | Session logs extracted from the gateway by the assessor. | Session logs; Approval records |  | US4 Critical: an UNKNOWN result on this control sets CG-15 to UNKNOWN (CG-12 trigger); the decision is capped at LIMITED or INCONCLUSIVE per the gate ceiling until the UNKNOWN Record is dispositioned. Supporting gates CG-14 require gate-level evaluation. | New remote access path; Gateway change; Unapproved session detected
MCF-SUP-023 | OPERATION | CP-3 | E2; E3 | E4; E5; E6 | P3 F3 C4 R3 T3 I3 | S4 | NORMAL; MAINTENANCE; EMERGENCY | At least 3 months. | Assessor retrieves sample recordings directly. | Recording configuration; Sample recordings | Where recording is not technically feasible, continuous live supervision with a written session log. | US3 Material: an UNKNOWN result requires gate-level evaluation for CG-15 and caps the decision at CONDITIONALLY_ASSURED with a recorded condition until resolved. | New system; Recording failure; Suspicious session
MCF-SUP-024 | OPERATION | CP-3 | E2; E3 | E4; E5; E6 | P3 F3 C4 R3 T3 I3 | S4 | NORMAL | 12 months. | Assessor samples accounts independently. | Recertification records; Account sample reconciliation |  | US3 Material: an UNKNOWN result requires gate-level evaluation for CG-15, CG-13 and caps the decision at CONDITIONALLY_ASSURED with a recorded condition until resolved. | Contract end; Supplier personnel change; Recertification interval elapsed
MCF-SEC-001 | IMPLEMENTATION | CP-2 | E1; E2; E3 | E5; E6 | P3 F3 C3 R3 T3 I2 | S4 | NORMAL; MAINTENANCE; EMERGENCY | Account extracts within 30 days (illustrative); leaver sample over 6 months. | Account extracts taken by the assessor directly from target systems, not from the identity system alone. | Account extracts from target systems; Leaver reconciliation | Witnessed screen extraction from legacy OT systems that cannot export accounts | US3; US4 against CG-15 where accounts on BMS/EPMS or BMC planes cannot be enumerated. | Identity platform change; New in-scope system; Mass onboarding of contractors
MCF-SEC-002 | IMPLEMENTATION | CP-2 | E1; E2; E3 | E5; E6 | P3 F3 C3 R3 T3 I2 | S4 | NORMAL; MAINTENANCE; RECOVERY | Inventory within 30 days (illustrative); admission logs for 90 days. | Inventory reconciled by the assessor to secrets stores and target-system configurations. | Machine-identity inventory; Attestation admission logs where supported | Secrets-manager reports combined with target-side token listings | US3; US4 against CG-15 where unscoped machine credentials with OT or control-plane write authority exist. | New automation or agent; PKI change; Node hardware generation change
MCF-SEC-003 | EFFECTIVENESS | CP-4 | E2; E3; E4 | E5; E7 | P3 F4 C3 R4 T3 I3 | S4 | NORMAL; MAINTENANCE; EMERGENCY; RECOVERY | Test within interval; 90 days (illustrative) of session logs. | Bypass-path testing by the security function or an independent tester. | Effective-permission analysis; Bypass-path test results | Configuration analysis of network and host controls proving non-brokered paths are blocked, where active testing is not authorised | US4: CG-15 cannot PASS while consequential cross-domain authority is unanalysed or untested. | New control plane; Role model change; PAM platform change; Incident involving privileged misuse
MCF-SEC-004 | OPERATION | CP-3 | E1; E2; E3 | E4 | P3 F3 C3 R3 T3 I3 | S4 | EMERGENCY; FAILED; RECOVERY | 12 months (illustrative) of uses; test within 12 months. | Use reviews by security function independent of the user. | Use and review records; Retrieval test record |  | US3; US4 against CG-10 if no tested emergency access exists for recovery-critical control planes. | Use event; Vault change; Identity provider change; Holder change
MCF-SEC-005 | EFFECTIVENESS | CP-4 | E1; E2; E3; E4 | E5 | P3 F4 C3 R4 T3 I3 | S4 | NORMAL; MAINTENANCE; DEGRADED; EMERGENCY | Tests within 12 months (illustrative); integrity monitoring for 90 days. | Testing by an OT security specialist independent of the BMS/EPMS integrator. | Risk assessment with SL-T; Protection-independence analysis; Write/command blocking test; Fail-safe evidence | Test on a representative OT test bench with identical firmware and configuration, plus production configuration review | US4: CG-07 cannot PASS while BMS/EPMS write/command exposure or fail-safe behaviour is unverified (scenario X05). | Controller firmware or logic change; New integration (for example IT/OT data export); Integrator change; OT security incident
MCF-SEC-006 | EFFECTIVENESS | CP-4 | E2; E3; E4 | E5; E7 | P3 F4 C3 R4 T3 I3 | S4 | NORMAL; MAINTENANCE; RECOVERY | Test within interval; admission logs 90 days. | Escalation tests by an independent tester. | Escalation test report; Admission policy evidence |  | US4: CG-15 cannot PASS while tenant-to-infrastructure escalation paths are untested. | Control-plane version upgrade; New tenant model; Admission policy change
MCF-SEC-007 | IMPLEMENTATION | CP-2 | E1; E2; E3 | E5; E6 | P3 F3 C3 R3 T3 I2 | S3 | NORMAL; MAINTENANCE | Reconciliation within 90 days (illustrative). | Reconciliation by security function. | Access configuration; Action logs |  | US3: unknown controller exposure conditions CG-15 and CG-08 claims. | Controller upgrade; Automation platform change
MCF-SEC-008 | IMPLEMENTATION | CP-2 | E1; E2; E3 | E5; E6 | P3 F3 C3 R3 T3 I2 | S3 | NORMAL; MAINTENANCE; RECOVERY | Configuration within 90 days (illustrative). | Configuration extracted by assessor. | Retention lock configuration; Destructive-operation protection configuration |  | US3; US4 against CG-10 where checkpoint recovery copies lack immutability. | Storage platform change; Retention policy change
MCF-SEC-009 | IMPLEMENTATION | CP-2 | E1; E2; E3 | E5; E7 | P3 F3 C3 R3 T3 I2 | S4 | NORMAL; MAINTENANCE; EMERGENCY | Reconciliation within interval; passive discovery covering at least 30 days (illustrative). | Reconciliation and discovery by a party independent of the network implementers. | Zone-and-conduit model; Configuration reconciliation; Discovery results | Physical inspection of OT network cabinets for undocumented links where passive monitoring is not deployed | US4: CG-07 cannot PASS while an undocumented path into a power or cooling control zone cannot be ruled out. | New integration between zones; Vendor installation; Firewall platform change; Discovery of bridging device
MCF-SEC-010 | EFFECTIVENESS | CP-4 | E2; E3; E4 | E5; E7 | P3 F4 C3 R4 T3 I3 | S4 | NORMAL; MAINTENANCE; RECOVERY | Test within interval. | Tests by security function or independent tester. | Reachability test report; Pivot test report | Rule-base analysis with path computation tooling where active tests are not authorised | US4: CG-15 cannot PASS while BMC or control-plane reachability from tenant workloads is untested. | New hardware generation; Network redesign; Tenant model change
MCF-SEC-011 | OPERATION | CP-3 | E2; E3 | E1; E7 | P3 F3 C3 R3 T3 I3 | S3 | NORMAL; MAINTENANCE | 12 months (illustrative) of reviews. | Rule analysis by assessor using exported rule sets. | Rule sets; Review records |  | US3: unreviewed rules condition CG-07/CG-15 evaluation. | New conduit; Boundary platform change; Incident
MCF-SEC-012 | EFFECTIVENESS | CP-4 | E2; E3; E4 | E5; E7 | P3 F4 C3 R4 T3 I3 | S4 | NORMAL; MAINTENANCE; EMERGENCY | Six months (illustrative) of sessions; revocation test within 12 months. | Discovery and revocation tests by security function. | Session approval and recording samples; Discovery results; Revocation test |  | US4: CG-15 cannot PASS while an unmanaged remote path into OT or control planes cannot be ruled out. | New vendor support contract; Remote access platform change; Discovery of unmanaged path
MCF-SEC-013 | IMPLEMENTATION | CP-2 | E1; E2; E3 | E5; E6 | P3 F3 C3 R3 T3 I2 | S3 | NORMAL; MAINTENANCE; RECOVERY | Assessment within interval. | Assessor reperforms compliance checks on a sample. | Compliance reports; Firmware inventory | Manual inspection of OT controller firmware versions where automated assessment is unavailable | US3; US4 against CG-07 where OT controller firmware integrity is unknown. | New device class; Firmware release; Baseline change
MCF-SEC-014 | OPERATION | CP-3 | E2; E3 | E1; E7 | P3 F3 C3 R3 T3 I3 | S3 | NORMAL; MAINTENANCE | Six months (illustrative). | Assessor samples from asset inventory. | Coverage report; Remediation SLA reports |  | US3: unknown vulnerability state conditions CG-07/CG-15 evaluation. | New asset class; Critical advisory
MCF-SEC-015 | OPERATION | CP-3 | E2; E3 | E1; E7 | P3 F3 C3 R3 T3 I3 | S3 | MAINTENANCE; TRANSITION; NORMAL | Six months (illustrative). | Assessor samples from deployed version changes. | Staged change records; Test records |  | US3; CG-14 SUPPORTING evaluation. | Patch-induced incident; Process change
MCF-SEC-016 | OPERATION | CP-3 | E1; E2; E3 | E4 | P3 F3 C3 R3 T3 I3 | S3 | NORMAL; MAINTENANCE | Current register; 12 months of approvals (illustrative). | Assessor cross-checks deviations from SEC-013/SEC-014 against the register. | Exception register; Verification records |  | US3: unapproved deviations condition the decision. | Exception expiry; New deviation
MCF-SEC-017 | OPERATION | CP-3 | E2; E3 | E1; E7 | P3 F3 C3 R3 T3 I3 | S3 | NORMAL; MAINTENANCE; EMERGENCY; RECOVERY | 90 days (illustrative). | Assessor queries telemetry platform directly. | Coverage report; Source health records |  | US2 for confidence; US3 where OT write events are not visible. | New source class; Platform change
MCF-SEC-018 | EFFECTIVENESS | CP-4 | E2; E3; E4 | E5; E7 | P3 F4 C3 R4 T3 I3 | S4 | NORMAL; MAINTENANCE; EMERGENCY | Simulations within interval. | Simulations designed by red/purple team independent of detection engineers. | Simulation results | Analysed real detections covering the same use cases | US3: untested detection reduces CG-15 confidence. | New scenario; Detection platform change; Missed detection
MCF-SEC-019 | RESILIENCE | CP-5 | E1; E2; E3; E4 | E5; E7 | P4 F4 C4 R4 T3 I3 | S4 | EMERGENCY; DEGRADED; RECOVERY | Exercise within interval. | Exercises observed by an independent party. | Playbooks; Exercise records; Safe fallback definitions | Analysed real incidents demonstrating containment | US3; US4 against CG-09 for cyber-physical scenarios with no exercised containment. | New scenario; Incident; Facility control architecture change
MCF-SEC-020 | IMPLEMENTATION | CP-2 | E1; E2; E3 | E5; E6 | P3 F3 C3 R3 T3 I2 | S3 | EMERGENCY; RECOVERY | Current. | Reviewed by forensic specialist. | Procedures; Baseline repository |  | US2: affects investigation confidence; US3 if baseline programs are absent. | New system class; Incident
MCF-SEC-021 | IMPLEMENTATION | CP-2 | E1; E2; E3; E7 | E4 | P3 F3 C3 R3 T3 I2 | S4 | NORMAL; DEGRADED; MAINTENANCE; EMERGENCY | Reconciliation within 90 days (illustrative). | Reconciliation by security function independent of automation owners. | Authority register; Effective permission reconciliation | Graph-based authority path analysis per AIDCF-005 with human review | US4: CG-15 cannot PASS while any automation or agent with consequential infrastructure authority is unregistered or unreconciled. | New agent or automation; New tool or API granted; Model or prompt change to an agent with infrastructure tools
MCF-SEC-022 | EFFECTIVENESS | CP-4 | E2; E3; E4 | E5; E7 | P3 F4 C3 R4 T3 I3 | S4 | NORMAL; MAINTENANCE; EMERGENCY | Test within 12 months (illustrative); records for 90 days. | Bypass tests by security function. | Bypass test results |  | US3; US4 against CG-15 where OT command approvals are self-enforced by the agent. | New action class; Automation platform change
MCF-SEC-023 | EFFECTIVENESS | CP-4 | E1; E2; E3; E4 | E5 | P3 F4 C3 R4 T3 I3 | S4 | NORMAL; MAINTENANCE; EMERGENCY | Test within interval. | Testing by OT security specialist independent of the automation owner. | Test results; Allowlist definitions | Test-bench testing with identical gateway configuration | US4: CG-07 cannot PASS while automated or remote writes to power/cooling controllers are unrestricted or untested. | Control-logic change; New automation; Gateway change
MCF-SEC-024 | RESILIENCE | CP-5 | E1; E2; E3; E4 | E5; E7 | P4 F4 C4 R4 T3 I3 | S4 | NORMAL; EMERGENCY; RECOVERY; DEGRADED | Test within 12 months (illustrative). | Tests witnessed by security and facility operations. | Halt and rollback test records |  | US3; US4 against CG-15 for automations with OT command authority lacking tested halt. | New automation; Automation platform change; Incident involving automation
MCF-EVA-001 | DESIGN | CP-1 | E1; E7 | E2 | P3 F4 C4 R3 T3 I3 | S3 | NORMAL | Profiles in force at the assessment date | Comparison to registry profiles performed by the assessor using the published registry release | Evidence Requirement profiles for in-scope controls; Local subtype-to-class mapping | Profiles held as machine-readable records in the assessment tool, exported with version | US3 Material: evidence sufficiency judgements for affected controls lack a stated basis; CG-11 evaluation records the gap | New AIDCF-008 or AIDCF-007A release adopted; New local evidence subtype introduced; Change in capability profile strengthening requirements
MCF-EVA-002 | IMPLEMENTATION | CP-2 | E1; E3 | E6 | P3 F3 C4 R3 T3 I3 | S3 | NORMAL | The current or most recent completed assessment | Assessor reconciles evidence request records to the UNKNOWN register | Evidence request records for the assessment; UNKNOWN Records for unfulfilled requests | Ticketing system records used for evidence requests, exported with full history | US2 Moderate: attribution of missing evidence uncertain; confidence ceiling CONF-2 for affected controls | Change of provider; Repeated refusal of requests by a source; Change of evidence lead
MCF-EVA-003 | IMPLEMENTATION | CP-2 | E1; E2 | E7 | P4 F3 C4 R4 T3 I4 | S3 | NORMAL | Repository configuration at the assessment date and manifests for decisions issued in the last twelve months | Hash verification run by the assessor with an independent tool | Repository configuration export; EvidenceManifests for decisions in the period; Hash verification output | Write-once storage with an external manifest generated per decision | US3 Material: reproducibility of decisions uncertain; affected decisions treated as integrity-uncertain for CG-11 | Repository platform change or migration; Schema change; Failed hash verification
MCF-EVA-004 | RESILIENCE | CP-5 | E1; E2; E3; E4 | E5 | P4 F4 C3 R4 T3 I4 | S4 | NORMAL; RECOVERY | Retention events over twelve months and the latest restoration test | Restoration test observed or verified by the assessor; hash comparison performed independently | Retention schedule and classification policy; Backup configuration showing separate fault domain; Restoration test record with hash verification | Restoration from an actual repository incident, with verification records, in place of a test | US3 Material: future challenge and reassessment of decisions may be impossible; decision condition recorded | Repository platform change; Legal hold instruction; Failed restoration; Change of retention law or contract
MCF-EVA-005 | OPERATION | CP-3 | E1; E3; E7 | E2 | P4 F3 C4 R4 T3 I3 | S4 | NORMAL | Evidence accepted for assessments completed in the last twelve months | Assessor reperforms provenance verification for a sub-sample at source | Sample of accepted Evidence Object provenance records; Derived evidence lineage records; AI-assisted processing records with review | W3C PROV-compatible provenance graph export in place of per-object records | US3 Material: affected results may become UNKNOWN (U6); CG-11 evaluation records the gap | Introduction of AI-assisted evidence processing; New derived analytics; Provenance failure found
MCF-EVA-006 | EFFECTIVENESS | CP-4 | E2; E3; E4 | E1; E5 | P4 F4 C3 R4 T3 I4 | S4 | NORMAL | Decisions issued in the last twelve months and the latest tamper exercise | Tamper exercise designed by a party other than the repository administrators | Integrity values and custody logs for sampled evidence; Pre-decision integrity verification records; Tamper exercise record | Detection of a real integrity event, with investigation record, in place of a tamper exercise | US3 Material: affected evidence treated as U7; dependent gate results may become UNKNOWN under CG-11 | Integrity failure; Repository change; Custody gap discovered
MCF-EVA-007 | OPERATION | CP-3 | E1; E7 | E6 | P3 F4 C4 R4 T3 I3 | S4 | NORMAL | Assessments completed in the last twelve months | Re-rating by an assessor who did not perform the original rating | Quality ratings with rationale for sampled evidence; Independent re-rating records | Assessor re-rates a sample during this assessment if no re-rating records exist, with a Finding raised | US3 Material: result support uncertain; CG-11 evaluation records the gap | New assessor team; Change in quality anchors; Systematic rating disagreement found
MCF-EVA-008 | OPERATION | CP-3 | E1; E3; E7 | E2 | P3 F4 C4 R3 T4 I3 | S4 | NORMAL | Assessments completed in the last twelve months | Assessor compares evidence dates with the change log independently | Currency checks for sampled evidence; Coverage records in sampled Control Assessments; Change log for subjects of sampled evidence | Machine-generated freshness flags from the assessment tool, if the rules are verified | US3 Material: affected results may be STALE; CG-11 evaluation records the gap | Material change to assessed subjects; Expiry of evidence currency windows; New operating state introduced
MCF-EVA-009 | DESIGN | CP-1 | E1 | E6 | P3 F4 C3 R3 T3 I3 | S3 | NORMAL | The assessment under review | Approval by the decision authority, separate from the lead assessor | Approved decision question record; Assurance case top claim | Engagement letter containing all required elements, approved by the decision authority | US5 Systemic: decision question undefined; CG-01 Gate Result UNKNOWN and decision capped at INCONCLUSIVE | Change in intended users or use; Change of Capability Instance or Service Outcome in scope; Change of as-of date
MCF-EVA-010 | DESIGN | CP-2 | E1; E7 | E2 | P3 F4 C4 R3 T3 I3 | S3 | NORMAL | The assessment under review | Reconciliation reperformed by the independent reviewer for a sample of snapshot elements | Approved scope record; Exclusion register with residual effect; Boundary-to-ArchitectureSnapshot reconciliation | Machine-readable scope object in the assessment tool, exported with approval history | US5 Systemic: assessment boundary unresolved; CG-02 Gate Result UNKNOWN and decision capped at INCONCLUSIVE | Change of boundary during assessment; New ArchitectureSnapshot version; Exclusion added or removed
MCF-EVA-011 | IMPLEMENTATION | CP-2 | E1; E3; E4 | E6 | P3 F4 C4 R4 T3 I3 | S3 | NORMAL; MAINTENANCE; DEGRADED | The assessment under review | Independent reviewer reperforms selection from the population frame for one sample | Sampling plans and records; Test authorisations; Test records with required conditional metadata | Use of the operator's own test records as evidence, if they contain the required metadata and authorisation | US3 Material: affected results may be over-extrapolated or unsafe to rely on; CG-11 evaluation records the gap | Test incident or abort; Change of sampling approach; Failed sample not expanded
MCF-EVA-012 | IMPLEMENTATION | CP-2 | E1; E3 | E6 | P3 F3 C4 R3 T3 I3 | S3 | NORMAL | The assessment under review | Independent reviewer confirms coverage of specialist domains | Specialist appointment and reliance records; Specialist approvals on methods and results | Specialist report with explicit scope and sign-off, incorporated by reference | US3 Material: affected domain results carry CONF-2 ceiling and a decision condition | New domain in scope; Specialist change mid-assessment; Technical disagreement unresolved
MCF-EVA-013 | OPERATION | CP-3 | E1; E3; E7 |  | P3 F4 C4 R3 T3 I4 | S4 | NORMAL | Findings raised or closed in the last twelve months | Assessor selects Findings from the full register including closed and superseded items | Findings register extract; Sampled Finding records with evidence links; Closure evidence and re-assessment records | Findings exported from the assessment tool in AIDCF-014 format with history | US3 Material: residual deficiency status uncertain; decision condition recorded | Register migration; Finding closed without evidence; Finding deleted
MCF-EVA-014 | EFFECTIVENESS | CP-4 | E3; E4; E7 | E1 | P4 F4 C4 R4 T3 I4 | S4 | NORMAL | Assessments completed in the last twelve months | Traceability test designed and scored by the independent reviewer | UNKNOWN register extract; Gate Results and decision record; Traceability or seeded-UNKNOWN test record | Reperformance by the assessor tracing every US3+ UNKNOWN Record of one completed assessment from workpaper to report | US4 Critical: the reliability of every Gate Result is in doubt; CG-12 evaluation cannot conclude and decisions are capped at LIMITED | UNKNOWN missing from a report; Severity scheme change; Assessment tool change affecting UNKNOWN handling
MCF-EVA-015 | OPERATION | CP-3 | E1; E7 | E2; E3 | P3 F4 C4 R4 T3 I4 | S4 | NORMAL | Assessments completed in the last twelve months | Assessor searches workpapers for contradictory evidence not registered as conflicts | Evidence conflict register; Conflict analysis and review records | Graph CHALLENGES relationships with linked EvidenceConflict nodes exported from the assessment tool | US3 Material: results may rest on contested evidence; CG-11 evaluation records the gap | Conflict escalated; New contradictory evidence after decision; Conflict register not maintained
MCF-EVA-016 | OPERATION | CP-3 | E1; E7 |  | P3 F4 C4 R3 T3 I3 | S4 | NORMAL | Assessments completed in the last twelve months | Reconciliation by the independent reviewer | Limitations register; All reports and statements for the assessment | Limitations section in the technical report, if it is the single source for other reports | US3 Material: intended users may over-rely; decision condition recorded | New audience-specific report; Redaction of a report; Change of scope after issue
MCF-EVA-017 | DESIGN | CP-1 | E1; E7 |  | P3 F4 C4 R3 T3 I3 | S3 | NORMAL | The assessment under review | Reconciliation to registry mappings reperformed by the assessor using the published registry | Gate applicability record; Gate-to-control lists per applicable gate; Registry gate mapping extract for the declared version | Machine-generated gate-control lists from the assessment tool, if the tool configuration is verified under MCF-GOV-004 | US4 Critical: affected Gate Results cannot be relied upon; decision capped at LIMITED | Registry gate mapping revision; Scope change; APPROVED_NA proposed
MCF-EVA-018 | OPERATION | CP-3 | E1; E7 | E5 | P4 F4 C4 R4 T3 I4 | S4 | NORMAL | Assessments completed in the last twelve months | Reperformance by a party other than the lead assessor | Gate Evidence Packages; Gate sufficiency assessments; Gate Result computation records | Machine-readable gate packages and results in AIDCF-014 format | US4 Critical: Gate Results unverified; decision capped at LIMITED | Gate floor revision; Gate PASS later contradicted; Evidence withdrawn from a gate package
MCF-EVA-019 | IMPLEMENTATION | CP-2 | E1; E2; E3 | E6 | P3 F4 C4 R3 T3 I4 | S3 | NORMAL | Decisions issued in the last twelve months | Workflow configuration and audit log extracted by the assessor | Decision records; Decision workflow configuration and audit log | Signed paper decision records with a decision register, where no workflow tool is used | US3 Material: decisions' authority uncertain; intended reliance restricted and condition recorded | Change of decision authority; Workflow tool change; Automated status change detected
MCF-EVA-020 | OPERATION | CP-3 | E1; E3 | E7 | P3 F4 C4 R3 T3 I3 | S4 | NORMAL | Reports and statements issued in the last twelve months | Assessor screens all issued documents, not a management-selected subset | Sampled reports and statements; Independent review records for claim language | Automated vocabulary screening output, verified by manual review of a sample | US3 Material: external reliance may exceed decision; condition recorded | Change of AIDCF-012 controlled wording; Prohibited claim found; New report format
MCF-EVA-021 | OPERATION | CP-3 | E2; E3 | E1; E7 | P3 F4 C4 R4 T4 I3 | S4 | NORMAL | Twelve months preceding the assessment | Assessor runs an independent expiry query against currency records | Evidence currency records for current decisions; Expiry monitoring outputs; Dependent claim review records | Manual quarterly expiry review records, if complete for the period | US3 Material: current decisions may rely on stale evidence; condition recorded | Monitoring failure; Change in currency bases; Expired evidence found in use
MCF-EVA-022 | EFFECTIVENESS | CP-4 | E2; E3; E4 | E1; E7 | P3 F4 C4 R4 T3 I3 | S4 | NORMAL; TRANSITION | Twelve months preceding the assessment and the latest trigger test | Assessor reconciles the full change and incident logs to trigger responses | Trigger definitions per decision; Trigger response records; Injected test event record | A genuine trigger event fully traced from source system to reassessment, in place of an injected test | US3 Material: current decisions may persist after invalidating change; CG-14 evaluation records the gap | Integration change; Missed trigger found; New change or incident system
MCF-EVA-023 | OPERATION | CP-3 | E2; E3; E7 | E1 | P4 F4 C4 R4 T4 I3 | S4 | NORMAL; DEGRADED; MAINTENANCE | Twelve months preceding the assessment | Assessor reconciles feed coverage to asset registers independently | Continuing assurance claim definitions; Feed coverage reconciliation; Feed-health monitoring records | Observability platform coverage reports, if they map to assurance claims | US3 Material: continuing-assurance claims unsupported; continuing claims reverted to point-in-time with condition | New assets not onboarded to monitoring; Feed outage beyond tolerance; Change of observability platform
MCF-EVA-024 | RESILIENCE | CP-5 | E1; E3; E4; E7 | E6 | P4 F4 C4 R4 T3 I4 | S4 | NORMAL; RECOVERY | Twelve months preceding the assessment and the latest rehearsal | Rehearsal observed by the independent reviewer | Suspension, withdrawal and supersession criteria; Trigger response and decision lifecycle records; Rehearsal or real-event record | Real suspension event fully traced, in place of a rehearsal | US3 Material: reliance on invalid decisions may continue; condition recorded and current decisions reviewed | Qualifying trigger not acted upon; Change of intended users; Change of decision authority

## Gate Mapping
Control ID | Control Title | Gate | Role
MCF-GOV-001 | Governance Charter | CG-13 | SUPPORTING
MCF-GOV-002 | Decision Rights | CG-13 | CRITICAL
MCF-GOV-003 | Committee Oversight | CG-13 | SUPPORTING
MCF-GOV-005 | RACI and Role Ownership | CG-13 | CRITICAL
MCF-GOV-006 | Critical Function Accountability | CG-13 | CRITICAL
MCF-GOV-006 | Critical Function Accountability | CG-03 | SUPPORTING
MCF-GOV-007 | Risk Acceptance Authority | CG-13 | CRITICAL
MCF-GOV-008 | Evidence Custody | CG-13 | SUPPORTING
MCF-GOV-010 | Technical Standard Baselines | CG-14 | SUPPORTING
MCF-GOV-011 | Exception Governance | CG-14 | SUPPORTING
MCF-GOV-011 | Exception Governance | CG-13 | SUPPORTING
MCF-GOV-012 | Document Lifecycle | CG-14 | SUPPORTING
MCF-GOV-015 | Critical Gate Governance | CG-13 | SUPPORTING
MCF-GOV-016 | Independent Review | CG-13 | SUPPORTING
MCF-GOV-017 | Stakeholder Obligations | CG-01 | SUPPORTING
MCF-GOV-018 | Regulatory Monitoring | CG-14 | SUPPORTING
MCF-GOV-019 | Customer Commitments | CG-01 | SUPPORTING
MCF-GOV-022 | Assessor Independence | CG-13 | SUPPORTING
MCF-CAP-001 | Capability Register | CG-01 | CRITICAL
MCF-CAP-002 | Capability Ownership | CG-13 | CRITICAL
MCF-CAP-002 | Capability Ownership | CG-01 | SUPPORTING
MCF-CAP-003 | Lifecycle Status | CG-01 | SUPPORTING
MCF-CAP-003 | Lifecycle Status | CG-14 | SUPPORTING
MCF-CAP-004 | Architecture Linkage | CG-02 | CRITICAL
MCF-CAP-004 | Architecture Linkage | CG-03 | SUPPORTING
MCF-CAP-004 | Architecture Linkage | CG-01 | SUPPORTING
MCF-CAP-005 | Availability Outcomes | CG-01 | CRITICAL
MCF-CAP-006 | Performance Outcomes | CG-01 | CRITICAL
MCF-CAP-006 | Performance Outcomes | CG-08 | SUPPORTING
MCF-CAP-007 | Integrity Outcomes | CG-01 | CRITICAL
MCF-CAP-007 | Integrity Outcomes | CG-08 | SUPPORTING
MCF-CAP-008 | Recovery Outcomes | CG-01 | CRITICAL
MCF-CAP-008 | Recovery Outcomes | CG-10 | SUPPORTING
MCF-CAP-009 | Criticality Criteria | CG-01 | SUPPORTING
MCF-CAP-010 | Impact Tolerance | CG-01 | CRITICAL
MCF-CAP-011 | Stakeholder Consequence | CG-01 | SUPPORTING
MCF-CAP-012 | Priority Classification | CG-05 | SUPPORTING
MCF-CAP-012 | Priority Classification | CG-06 | SUPPORTING
MCF-CAP-013 | Current Demand Baseline | CG-05 | SUPPORTING
MCF-CAP-013 | Current Demand Baseline | CG-06 | SUPPORTING
MCF-CAP-014 | Peak and Transient Demand | CG-05 | SUPPORTING
MCF-CAP-014 | Peak and Transient Demand | CG-06 | SUPPORTING
MCF-CAP-016 | Scenario Demand | CG-10 | SUPPORTING
MCF-CAP-016 | Scenario Demand | CG-05 | SUPPORTING
MCF-CAP-017 | Load Envelope | CG-05 | SUPPORTING
MCF-CAP-017 | Load Envelope | CG-06 | SUPPORTING
MCF-CAP-018 | Environmental Envelope | CG-06 | SUPPORTING
MCF-CAP-019 | Duration Limits | CG-05 | SUPPORTING
MCF-CAP-019 | Duration Limits | CG-06 | SUPPORTING
MCF-CAP-019 | Duration Limits | CG-10 | SUPPORTING
MCF-CAP-020 | State-Specific Limits | CG-09 | SUPPORTING
MCF-CAP-020 | State-Specific Limits | CG-10 | SUPPORTING
MCF-CAP-021 | Design-to-Operation Traceability | CG-02 | SUPPORTING
MCF-CAP-022 | Commissioning Acceptance | CG-02 | SUPPORTING
MCF-CAP-022 | Commissioning Acceptance | CG-08 | SUPPORTING
MCF-CAP-022 | Commissioning Acceptance | CG-14 | SUPPORTING
MCF-CAP-023 | Material Change Impact | CG-14 | CRITICAL
MCF-CAP-023 | Material Change Impact | CG-01 | SUPPORTING
MCF-CAP-024 | Retirement Control | CG-14 | SUPPORTING
MCF-CAP-024 | Retirement Control | CG-02 | SUPPORTING
MCF-CAP-024 | Retirement Control | CG-04 | SUPPORTING
MCF-DEP-001 | Asset-to-Function Mapping | CG-03 | CRITICAL
MCF-DEP-001 | Asset-to-Function Mapping | CG-02 | SUPPORTING
MCF-DEP-002 | Upstream Dependency Mapping | CG-03 | CRITICAL
MCF-DEP-002 | Upstream Dependency Mapping | CG-15 | SUPPORTING
MCF-DEP-003 | Downstream Consequence Mapping | CG-03 | SUPPORTING
MCF-DEP-003 | Downstream Consequence Mapping | CG-09 | SUPPORTING
MCF-DEP-004 | Recovery Dependency Mapping | CG-03 | SUPPORTING
MCF-DEP-004 | Recovery Dependency Mapping | CG-10 | SUPPORTING
MCF-DEP-005 | Shared Source Analysis | CG-03 | CRITICAL
MCF-DEP-005 | Shared Source Analysis | CG-05 | SUPPORTING
MCF-DEP-005 | Shared Source Analysis | CG-06 | SUPPORTING
MCF-DEP-005 | Shared Source Analysis | CG-09 | SUPPORTING
MCF-DEP-006 | Common Controller Analysis | CG-03 | SUPPORTING
MCF-DEP-006 | Common Controller Analysis | CG-07 | SUPPORTING
MCF-DEP-006 | Common Controller Analysis | CG-09 | SUPPORTING
MCF-DEP-007 | Shared Route Analysis | CG-03 | CRITICAL
MCF-DEP-007 | Shared Route Analysis | CG-09 | SUPPORTING
MCF-DEP-008 | Shared Human Dependency Analysis | CG-03 | SUPPORTING
MCF-DEP-008 | Shared Human Dependency Analysis | CG-13 | SUPPORTING
MCF-DEP-009 | Utility Dependency | CG-03 | CRITICAL
MCF-DEP-009 | Utility Dependency | CG-05 | SUPPORTING
MCF-DEP-010 | Telecom Dependency | CG-03 | CRITICAL
MCF-DEP-010 | Telecom Dependency | CG-10 | SUPPORTING
MCF-DEP-011 | OEM Dependency | CG-03 | SUPPORTING
MCF-DEP-011 | OEM Dependency | CG-10 | SUPPORTING
MCF-DEP-012 | Cloud and Service Dependency | CG-03 | CRITICAL
MCF-DEP-012 | Cloud and Service Dependency | CG-15 | SUPPORTING
MCF-DEP-012 | Cloud and Service Dependency | CG-10 | SUPPORTING
MCF-DEP-013 | Capacity Concentration | CG-03 | SUPPORTING
MCF-DEP-013 | Capacity Concentration | CG-09 | SUPPORTING
MCF-DEP-014 | Supplier Concentration | CG-03 | SUPPORTING
MCF-DEP-015 | Knowledge Concentration | CG-13 | SUPPORTING
MCF-DEP-015 | Knowledge Concentration | CG-10 | SUPPORTING
MCF-DEP-016 | Substitution Readiness | CG-10 | SUPPORTING
MCF-DEP-016 | Substitution Readiness | CG-03 | SUPPORTING
MCF-DEP-017 | Assessment Boundary | CG-02 | CRITICAL
MCF-DEP-017 | Assessment Boundary | CG-03 | CRITICAL
MCF-DEP-018 | Provider Boundary | CG-13 | CRITICAL
MCF-DEP-018 | Provider Boundary | CG-03 | SUPPORTING
MCF-DEP-019 | Tenant Boundary | CG-09 | SUPPORTING
MCF-DEP-019 | Tenant Boundary | CG-13 | SUPPORTING
MCF-DEP-020 | Cross-Boundary Enforcement | CG-09 | SUPPORTING
MCF-DEP-020 | Cross-Boundary Enforcement | CG-15 | SUPPORTING
MCF-DEP-021 | Dependency Health Indicators | CG-03 | SUPPORTING
MCF-DEP-022 | Provider Performance | CG-13 | SUPPORTING
MCF-DEP-023 | Change Detection | CG-14 | SUPPORTING
MCF-DEP-023 | Change Detection | CG-03 | SUPPORTING
MCF-DEP-024 | Periodic Revalidation | CG-03 | SUPPORTING
MCF-PHY-001 | Site Hazard Assessment | CG-02 | SUPPORTING
MCF-PHY-001 | Site Hazard Assessment | CG-03 | SUPPORTING
MCF-PHY-001 | Site Hazard Assessment | CG-04 | SUPPORTING
MCF-PHY-002 | External Exposure | CG-09 | SUPPORTING
MCF-PHY-002 | External Exposure | CG-03 | SUPPORTING
MCF-PHY-003 | Access and Logistics | CG-10 | SUPPORTING
MCF-PHY-004 | Adjacent Risk | CG-03 | SUPPORTING
MCF-PHY-005 | Structural Capacity | CG-02 | SUPPORTING
MCF-PHY-005 | Structural Capacity | CG-04 | SUPPORTING
MCF-PHY-006 | Rack Loading | CG-04 | SUPPORTING
MCF-PHY-006 | Rack Loading | CG-14 | SUPPORTING
MCF-PHY-007 | Anchorage and Vibration | CG-09 | SUPPORTING
MCF-PHY-008 | Building Envelope | CG-06 | SUPPORTING
MCF-PHY-009 | Security Zones | CG-15 | SUPPORTING
MCF-PHY-009 | Security Zones | CG-09 | SUPPORTING
MCF-PHY-010 | Fire Zones | CG-09 | CRITICAL
MCF-PHY-010 | Fire Zones | CG-04 | SUPPORTING
MCF-PHY-011 | Water Zones | CG-09 | SUPPORTING
MCF-PHY-011 | Water Zones | CG-04 | SUPPORTING
MCF-PHY-012 | Tenant Segregation | CG-13 | SUPPORTING
MCF-PHY-012 | Tenant Segregation | CG-02 | SUPPORTING
MCF-PHY-013 | Identity-Based Access | CG-15 | SUPPORTING
MCF-PHY-018 | Equipment Movement | CG-04 | SUPPORTING
MCF-PHY-021 | Fire Detection | CG-04 | CRITICAL
MCF-PHY-021 | Fire Detection | CG-09 | SUPPORTING
MCF-PHY-022 | Suppression Interfaces | CG-04 | CRITICAL
MCF-PHY-022 | Suppression Interfaces | CG-06 | SUPPORTING
MCF-PHY-022 | Suppression Interfaces | CG-07 | SUPPORTING
MCF-PHY-023 | Egress and Emergency Access | CG-04 | CRITICAL
MCF-PHY-024 | Emergency Shutdown Governance | CG-04 | CRITICAL
MCF-PHY-024 | Emergency Shutdown Governance | CG-07 | SUPPORTING
MCF-PHY-024 | Emergency Shutdown Governance | CG-09 | SUPPORTING
MCF-POW-001 | Utility Capacity | CG-05 | CRITICAL
MCF-POW-001 | Utility Capacity | CG-03 | SUPPORTING
MCF-POW-002 | Grid Quality | CG-05 | SUPPORTING
MCF-POW-003 | Connection Reliability | CG-03 | SUPPORTING
MCF-POW-003 | Connection Reliability | CG-05 | SUPPORTING
MCF-POW-003 | Connection Reliability | CG-09 | SUPPORTING
MCF-POW-004 | Utility Contingency | CG-05 | SUPPORTING
MCF-POW-004 | Utility Contingency | CG-10 | SUPPORTING
MCF-POW-005 | Generator Capacity | CG-05 | CRITICAL
MCF-POW-006 | Start Reliability | CG-05 | CRITICAL
MCF-POW-006 | Start Reliability | CG-07 | SUPPORTING
MCF-POW-007 | Fuel Autonomy | CG-05 | CRITICAL
MCF-POW-008 | Fuel Replenishment | CG-05 | SUPPORTING
MCF-POW-008 | Fuel Replenishment | CG-03 | SUPPORTING
MCF-POW-008 | Fuel Replenishment | CG-10 | SUPPORTING
MCF-POW-009 | UPS Topology | CG-05 | CRITICAL
MCF-POW-009 | UPS Topology | CG-09 | SUPPORTING
MCF-POW-009 | UPS Topology | CG-02 | SUPPORTING
MCF-POW-010 | Battery Condition | CG-04 | CRITICAL
MCF-POW-010 | Battery Condition | CG-05 | SUPPORTING
MCF-POW-011 | Runtime and Derating | CG-05 | CRITICAL
MCF-POW-012 | Bypass Exposure | CG-05 | SUPPORTING
MCF-POW-012 | Bypass Exposure | CG-09 | SUPPORTING
MCF-POW-013 | Switchgear Integrity | CG-04 | CRITICAL
MCF-POW-013 | Switchgear Integrity | CG-05 | SUPPORTING
MCF-POW-014 | Selective Coordination | CG-09 | CRITICAL
MCF-POW-014 | Selective Coordination | CG-05 | SUPPORTING
MCF-POW-015 | Busway and PDU Capacity | CG-05 | SUPPORTING
MCF-POW-015 | Busway and PDU Capacity | CG-14 | SUPPORTING
MCF-POW-016 | Earthing and Bonding | CG-04 | CRITICAL
MCF-POW-016 | Earthing and Bonding | CG-05 | SUPPORTING
MCF-POW-017 | Voltage Quality | CG-05 | SUPPORTING
MCF-POW-018 | Harmonics | CG-05 | SUPPORTING
MCF-POW-019 | Transient Ride-Through | CG-05 | CRITICAL
MCF-POW-019 | Transient Ride-Through | CG-06 | SUPPORTING
MCF-POW-020 | Load-Step Response | CG-05 | CRITICAL
MCF-POW-020 | Load-Step Response | CG-03 | SUPPORTING
MCF-POW-021 | EPMS Coverage | CG-07 | CRITICAL
MCF-POW-021 | EPMS Coverage | CG-05 | SUPPORTING
MCF-POW-021 | EPMS Coverage | CG-15 | SUPPORTING
MCF-POW-022 | Preventive Maintenance | CG-05 | SUPPORTING
MCF-POW-023 | Switching Procedures | CG-04 | CRITICAL
MCF-POW-023 | Switching Procedures | CG-07 | SUPPORTING
MCF-POW-023 | Switching Procedures | CG-14 | SUPPORTING
MCF-POW-024 | Black-Start and Restoration | CG-10 | CRITICAL
MCF-POW-024 | Black-Start and Restoration | CG-05 | SUPPORTING
MCF-POW-024 | Black-Start and Restoration | CG-07 | SUPPORTING
MCF-THM-001 | Heat-Load Model | CG-06 | SUPPORTING
MCF-THM-001 | Heat-Load Model | CG-01 | SUPPORTING
MCF-THM-002 | Design Capacity | CG-06 | CRITICAL
MCF-THM-002 | Design Capacity | CG-02 | SUPPORTING
MCF-THM-003 | Resilient Capacity | CG-06 | CRITICAL
MCF-THM-003 | Resilient Capacity | CG-09 | SUPPORTING
MCF-THM-003 | Resilient Capacity | CG-05 | SUPPORTING
MCF-THM-004 | Seasonal Derating | CG-06 | CRITICAL
MCF-THM-004 | Seasonal Derating | CG-03 | SUPPORTING
MCF-THM-005 | Airflow Management | CG-06 | SUPPORTING
MCF-THM-006 | Containment | CG-06 | SUPPORTING
MCF-THM-006 | Containment | CG-04 | SUPPORTING
MCF-THM-007 | CRAH and In-Row Capacity | CG-06 | SUPPORTING
MCF-THM-008 | Air-Side Monitoring | CG-06 | SUPPORTING
MCF-THM-009 | Direct-to-Chip Architecture | CG-06 | SUPPORTING
MCF-THM-010 | CDU Capacity | CG-06 | CRITICAL
MCF-THM-010 | CDU Capacity | CG-07 | SUPPORTING
MCF-THM-011 | Secondary Loop Integrity | CG-06 | CRITICAL
MCF-THM-011 | Secondary Loop Integrity | CG-09 | SUPPORTING
MCF-THM-012 | Quick-Disconnect Management | CG-06 | SUPPORTING
MCF-THM-012 | Quick-Disconnect Management | CG-04 | SUPPORTING
MCF-THM-012 | Quick-Disconnect Management | CG-14 | SUPPORTING
MCF-THM-013 | Chiller Capacity | CG-06 | CRITICAL
MCF-THM-013 | Chiller Capacity | CG-04 | SUPPORTING
MCF-THM-014 | Cooling Tower or Dry Cooler | CG-06 | SUPPORTING
MCF-THM-015 | Water Continuity | CG-06 | CRITICAL
MCF-THM-015 | Water Continuity | CG-03 | SUPPORTING
MCF-THM-016 | Heat-Rejection Dependency | CG-03 | SUPPORTING
MCF-THM-016 | Heat-Rejection Dependency | CG-09 | SUPPORTING
MCF-THM-016 | Heat-Rejection Dependency | CG-06 | SUPPORTING
MCF-THM-017 | Coolant Compatibility | CG-04 | SUPPORTING
MCF-THM-017 | Coolant Compatibility | CG-06 | SUPPORTING
MCF-THM-018 | Water Quality | CG-04 | CRITICAL
MCF-THM-018 | Water Quality | CG-06 | SUPPORTING
MCF-THM-019 | Leak Detection | CG-06 | SUPPORTING
MCF-THM-019 | Leak Detection | CG-09 | SUPPORTING
MCF-THM-019 | Leak Detection | CG-04 | SUPPORTING
MCF-THM-020 | Isolation and Drainage | CG-09 | CRITICAL
MCF-THM-020 | Isolation and Drainage | CG-04 | SUPPORTING
MCF-THM-020 | Isolation and Drainage | CG-06 | SUPPORTING
MCF-THM-021 | Control Stability | CG-07 | CRITICAL
MCF-THM-021 | Control Stability | CG-06 | SUPPORTING
MCF-THM-021 | Control Stability | CG-15 | SUPPORTING
MCF-THM-022 | Sensor Trust | CG-07 | SUPPORTING
MCF-THM-022 | Sensor Trust | CG-06 | SUPPORTING
MCF-THM-023 | Maintenance States | CG-06 | SUPPORTING
MCF-THM-023 | Maintenance States | CG-14 | SUPPORTING
MCF-THM-023 | Maintenance States | CG-04 | SUPPORTING
MCF-THM-024 | Thermal Recovery | CG-10 | CRITICAL
MCF-THM-024 | Thermal Recovery | CG-06 | SUPPORTING
MCF-ENV-001 | Temperature Control | CG-06 | SUPPORTING
MCF-ENV-001 | Temperature Control | CG-08 | SUPPORTING
MCF-ENV-002 | Humidity Control | CG-06 | SUPPORTING
MCF-ENV-003 | Particulate and Corrosion | CG-08 | SUPPORTING
MCF-ENV-004 | Vibration and Acoustic Conditions | CG-08 | SUPPORTING
MCF-ENV-008 | Resilience-Efficiency Trade-Off | CG-05 | SUPPORTING
MCF-ENV-008 | Resilience-Efficiency Trade-Off | CG-06 | SUPPORTING
MCF-ENV-008 | Resilience-Efficiency Trade-Off | CG-14 | SUPPORTING
MCF-ENV-009 | Water Source and Quality | CG-06 | SUPPORTING
MCF-ENV-009 | Water Source and Quality | CG-04 | SUPPORTING
MCF-ENV-011 | Water Scarcity Response | CG-06 | SUPPORTING
MCF-ENV-011 | Water Scarcity Response | CG-03 | SUPPORTING
MCF-ENV-017 | Battery Materials | CG-04 | SUPPORTING
MCF-ENV-018 | Refrigerants and Coolants | CG-04 | CRITICAL
MCF-ENV-019 | Fuel and Suppressant Handling | CG-04 | SUPPORTING
MCF-ENV-021 | Heatwave Readiness | CG-06 | SUPPORTING
MCF-ENV-021 | Heatwave Readiness | CG-05 | SUPPORTING
MCF-ENV-022 | Drought Readiness | CG-03 | SUPPORTING
MCF-ENV-023 | Flood Adaptation | CG-09 | SUPPORTING
MCF-ENV-024 | Long-Term Resource Constraints | CG-01 | SUPPORTING
MCF-ENV-024 | Long-Term Resource Constraints | CG-03 | SUPPORTING
MCF-CMP-001 | Accelerator Architecture | CG-08 | SUPPORTING
MCF-CMP-001 | Accelerator Architecture | CG-01 | SUPPORTING
MCF-CMP-002 | Node Configuration | CG-08 | SUPPORTING
MCF-CMP-002 | Node Configuration | CG-15 | SUPPORTING
MCF-CMP-003 | Rack-Scale Composition | CG-08 | SUPPORTING
MCF-CMP-003 | Rack-Scale Composition | CG-06 | SUPPORTING
MCF-CMP-003 | Rack-Scale Composition | CG-05 | SUPPORTING
MCF-CMP-004 | Approved Baseline | CG-02 | SUPPORTING
MCF-CMP-004 | Approved Baseline | CG-08 | SUPPORTING
MCF-CMP-004 | Approved Baseline | CG-14 | SUPPORTING
MCF-CMP-005 | Cluster Topology | CG-08 | SUPPORTING
MCF-CMP-005 | Cluster Topology | CG-02 | SUPPORTING
MCF-CMP-006 | Scale-Up Domain Integrity | CG-08 | CRITICAL
MCF-CMP-006 | Scale-Up Domain Integrity | CG-09 | SUPPORTING
MCF-CMP-007 | Partitioning | CG-09 | SUPPORTING
MCF-CMP-007 | Partitioning | CG-15 | SUPPORTING
MCF-CMP-008 | Fault-Domain Design | CG-09 | CRITICAL
MCF-CMP-008 | Fault-Domain Design | CG-08 | SUPPORTING
MCF-CMP-008 | Fault-Domain Design | CG-03 | SUPPORTING
MCF-CMP-009 | Usable Accelerator Capacity | CG-08 | CRITICAL
MCF-CMP-009 | Usable Accelerator Capacity | CG-01 | SUPPORTING
MCF-CMP-010 | Scheduler Controls | CG-08 | SUPPORTING
MCF-CMP-010 | Scheduler Controls | CG-15 | SUPPORTING
MCF-CMP-011 | Resource Reservation | CG-10 | SUPPORTING
MCF-CMP-011 | Resource Reservation | CG-08 | SUPPORTING
MCF-CMP-012 | Contention Management | CG-08 | SUPPORTING
MCF-CMP-013 | Firmware Baseline | CG-08 | CRITICAL
MCF-CMP-013 | Firmware Baseline | CG-14 | SUPPORTING
MCF-CMP-013 | Firmware Baseline | CG-15 | SUPPORTING
MCF-CMP-014 | Driver Compatibility | CG-08 | SUPPORTING
MCF-CMP-015 | Upgrade Testing | CG-14 | CRITICAL
MCF-CMP-015 | Upgrade Testing | CG-09 | SUPPORTING
MCF-CMP-015 | Upgrade Testing | CG-08 | SUPPORTING
MCF-CMP-016 | Rollback Readiness | CG-10 | SUPPORTING
MCF-CMP-016 | Rollback Readiness | CG-14 | SUPPORTING
MCF-CMP-017 | GPU Telemetry | CG-08 | SUPPORTING
MCF-CMP-017 | GPU Telemetry | CG-06 | SUPPORTING
MCF-CMP-018 | Node Health | CG-08 | SUPPORTING
MCF-CMP-019 | Error and Degradation Detection | CG-08 | CRITICAL
MCF-CMP-020 | Performance Baselines | CG-08 | SUPPORTING
MCF-CMP-021 | Provisioning | CG-08 | SUPPORTING
MCF-CMP-021 | Provisioning | CG-14 | SUPPORTING
MCF-CMP-022 | Spares and RMA | CG-10 | SUPPORTING
MCF-CMP-022 | Spares and RMA | CG-03 | SUPPORTING
MCF-CMP-023 | Node Rebuild | CG-10 | CRITICAL
MCF-CMP-023 | Node Rebuild | CG-08 | SUPPORTING
MCF-CMP-024 | Secure Retirement | CG-02 | SUPPORTING
MCF-STO-001 | Training Data Tier | CG-08 | SUPPORTING
MCF-STO-001 | Training Data Tier | CG-01 | SUPPORTING
MCF-STO-002 | Checkpoint Tier | CG-08 | SUPPORTING
MCF-STO-002 | Checkpoint Tier | CG-10 | SUPPORTING
MCF-STO-003 | Model and Artifact Tier | CG-08 | SUPPORTING
MCF-STO-003 | Model and Artifact Tier | CG-10 | SUPPORTING
MCF-STO-004 | Archive Tier | CG-10 | SUPPORTING
MCF-STO-005 | Throughput and IOPS | CG-08 | CRITICAL
MCF-STO-006 | Metadata Performance | CG-08 | SUPPORTING
MCF-STO-007 | Capacity Headroom | CG-08 | SUPPORTING
MCF-STO-008 | Burst Handling | CG-08 | SUPPORTING
MCF-STO-008 | Burst Handling | CG-09 | SUPPORTING
MCF-STO-009 | Data Integrity | CG-08 | CRITICAL
MCF-STO-010 | Metadata Integrity | CG-08 | CRITICAL
MCF-STO-010 | Metadata Integrity | CG-10 | SUPPORTING
MCF-STO-011 | Checksum and Scrubbing | CG-08 | SUPPORTING
MCF-STO-012 | Configuration Consistency | CG-14 | SUPPORTING
MCF-STO-012 | Configuration Consistency | CG-08 | SUPPORTING
MCF-STO-013 | Snapshot Protection | CG-10 | SUPPORTING
MCF-STO-014 | Replication | CG-10 | SUPPORTING
MCF-STO-014 | Replication | CG-09 | SUPPORTING
MCF-STO-014 | Replication | CG-03 | SUPPORTING
MCF-STO-015 | Erasure Coding | CG-09 | CRITICAL
MCF-STO-015 | Erasure Coding | CG-08 | SUPPORTING
MCF-STO-016 | Immutable Recovery Copy | CG-10 | CRITICAL
MCF-STO-016 | Immutable Recovery Copy | CG-15 | SUPPORTING
MCF-STO-017 | Checkpoint Durability | CG-08 | CRITICAL
MCF-STO-017 | Checkpoint Durability | CG-10 | SUPPORTING
MCF-STO-018 | Restart Readiness | CG-10 | CRITICAL
MCF-STO-019 | Storage Recovery Sequencing | CG-10 | SUPPORTING
MCF-STO-019 | Storage Recovery Sequencing | CG-09 | SUPPORTING
MCF-STO-020 | Recovery Validation | CG-10 | CRITICAL
MCF-STO-021 | Storage Telemetry | CG-08 | SUPPORTING
MCF-STO-022 | Capacity Forecasting | CG-08 | SUPPORTING
MCF-STO-023 | Media Health | CG-08 | SUPPORTING
MCF-NET-001 | Fabric Topology | CG-08 | CRITICAL
MCF-NET-001 | Fabric Topology | CG-02 | SUPPORTING
MCF-NET-002 | Path Diversity | CG-03 | SUPPORTING
MCF-NET-002 | Path Diversity | CG-08 | SUPPORTING
MCF-NET-002 | Path Diversity | CG-09 | SUPPORTING
MCF-NET-003 | Oversubscription | CG-08 | SUPPORTING
MCF-NET-004 | Fabric Fault-Domain Design | CG-09 | CRITICAL
MCF-NET-004 | Fabric Fault-Domain Design | CG-08 | SUPPORTING
MCF-NET-004 | Fabric Fault-Domain Design | CG-03 | SUPPORTING
MCF-NET-005 | Latency Baseline | CG-08 | SUPPORTING
MCF-NET-006 | Loss and Retransmission | CG-08 | SUPPORTING
MCF-NET-007 | Congestion Control | CG-08 | CRITICAL
MCF-NET-007 | Congestion Control | CG-09 | SUPPORTING
MCF-NET-008 | Collective Communication Performance | CG-08 | CRITICAL
MCF-NET-009 | Storage Fabric | CG-08 | CRITICAL
MCF-NET-009 | Storage Fabric | CG-10 | SUPPORTING
MCF-NET-010 | Frontend Network | CG-08 | SUPPORTING
MCF-NET-011 | Service Gateways | CG-08 | SUPPORTING
MCF-NET-012 | Traffic Isolation | CG-09 | SUPPORTING
MCF-NET-012 | Traffic Isolation | CG-08 | SUPPORTING
MCF-NET-012 | Traffic Isolation | CG-15 | SUPPORTING
MCF-NET-013 | Management Separation | CG-15 | SUPPORTING
MCF-NET-013 | Management Separation | CG-08 | SUPPORTING
MCF-NET-014 | Console Access | CG-10 | SUPPORTING
MCF-NET-014 | Console Access | CG-15 | SUPPORTING
MCF-NET-015 | OOB Resilience | CG-10 | CRITICAL
MCF-NET-015 | OOB Resilience | CG-15 | SUPPORTING
MCF-NET-015 | OOB Resilience | CG-03 | SUPPORTING
MCF-NET-016 | Break-Glass Access | CG-15 | SUPPORTING
MCF-NET-016 | Break-Glass Access | CG-10 | SUPPORTING
MCF-NET-017 | Cabling Standards | CG-08 | SUPPORTING
MCF-NET-018 | Optics Compatibility | CG-08 | SUPPORTING
MCF-NET-018 | Optics Compatibility | CG-03 | SUPPORTING
MCF-NET-019 | Cross-Connect Control | CG-14 | SUPPORTING
MCF-NET-019 | Cross-Connect Control | CG-08 | SUPPORTING
MCF-NET-020 | Path Documentation | CG-02 | SUPPORTING
MCF-NET-020 | Path Documentation | CG-03 | SUPPORTING
MCF-NET-020 | Path Documentation | CG-10 | SUPPORTING
MCF-NET-021 | Controller Resilience | CG-08 | SUPPORTING
MCF-NET-021 | Controller Resilience | CG-09 | SUPPORTING
MCF-NET-021 | Controller Resilience | CG-10 | SUPPORTING
MCF-NET-022 | Configuration Management | CG-14 | CRITICAL
MCF-NET-022 | Configuration Management | CG-08 | SUPPORTING
MCF-NET-022 | Configuration Management | CG-10 | SUPPORTING
MCF-NET-023 | Flow Telemetry | CG-08 | SUPPORTING
MCF-NET-024 | Time and Core Services | CG-08 | SUPPORTING
MCF-NET-024 | Time and Core Services | CG-03 | SUPPORTING
MCF-NET-024 | Time and Core Services | CG-10 | SUPPORTING
MCF-OPS-001 | 24x7 Coverage | CG-13 | SUPPORTING
MCF-OPS-001 | 24x7 Coverage | CG-10 | SUPPORTING
MCF-OPS-002 | Role Clarity | CG-13 | CRITICAL
MCF-OPS-002 | Role Clarity | CG-14 | SUPPORTING
MCF-OPS-003 | Shift Handover | CG-04 | SUPPORTING
MCF-OPS-003 | Shift Handover | CG-14 | SUPPORTING
MCF-OPS-004 | Competence and Authorisation | CG-04 | CRITICAL
MCF-OPS-004 | Competence and Authorisation | CG-13 | SUPPORTING
MCF-OPS-005 | Standard Operating Procedures | CG-10 | SUPPORTING
MCF-OPS-005 | Standard Operating Procedures | CG-13 | SUPPORTING
MCF-OPS-005 | Standard Operating Procedures | CG-14 | SUPPORTING
MCF-OPS-006 | Method Statements | CG-14 | CRITICAL
MCF-OPS-006 | Method Statements | CG-04 | SUPPORTING
MCF-OPS-007 | Permit to Work | CG-04 | CRITICAL
MCF-OPS-008 | Lockout and Tagout | CG-04 | CRITICAL
MCF-OPS-009 | Maintenance Strategy | CG-05 | SUPPORTING
MCF-OPS-009 | Maintenance Strategy | CG-06 | SUPPORTING
MCF-OPS-010 | Condition Monitoring | CG-05 | SUPPORTING
MCF-OPS-010 | Condition Monitoring | CG-06 | SUPPORTING
MCF-OPS-011 | Calibration | CG-07 | SUPPORTING
MCF-OPS-012 | Deferred Maintenance | CG-05 | SUPPORTING
MCF-OPS-012 | Deferred Maintenance | CG-06 | SUPPORTING
MCF-OPS-012 | Deferred Maintenance | CG-13 | SUPPORTING
MCF-OPS-013 | Alarm Rationalisation | CG-07 | CRITICAL
MCF-OPS-013 | Alarm Rationalisation | CG-06 | SUPPORTING
MCF-OPS-013 | Alarm Rationalisation | CG-05 | SUPPORTING
MCF-OPS-014 | Incident Response | CG-10 | SUPPORTING
MCF-OPS-014 | Incident Response | CG-13 | SUPPORTING
MCF-OPS-015 | Root Cause Analysis | CG-09 | SUPPORTING
MCF-OPS-016 | Problem Elimination | CG-14 | SUPPORTING
MCF-OPS-017 | Configuration Baseline | CG-14 | CRITICAL
MCF-OPS-017 | Configuration Baseline | CG-02 | SUPPORTING
MCF-OPS-017 | Configuration Baseline | CG-07 | SUPPORTING
MCF-OPS-018 | Change Assessment | CG-14 | CRITICAL
MCF-OPS-018 | Change Assessment | CG-03 | SUPPORTING
MCF-OPS-019 | Temporary Configuration | CG-14 | SUPPORTING
MCF-OPS-019 | Temporary Configuration | CG-07 | SUPPORTING
MCF-OPS-019 | Temporary Configuration | CG-04 | SUPPORTING
MCF-OPS-020 | Rollback and Validation | CG-14 | CRITICAL
MCF-OPS-020 | Rollback and Validation | CG-10 | SUPPORTING
MCF-OPS-021 | Capacity Review | CG-05 | SUPPORTING
MCF-OPS-021 | Capacity Review | CG-06 | SUPPORTING
MCF-OPS-023 | Resource Balancing | CG-05 | SUPPORTING
MCF-OPS-023 | Resource Balancing | CG-06 | SUPPORTING
MCF-OPS-023 | Resource Balancing | CG-09 | SUPPORTING
MCF-OPS-024 | Operational Reporting | CG-13 | SUPPORTING
MCF-RES-001 | Minimum Service Outcome | CG-01 | SUPPORTING
MCF-RES-001 | Minimum Service Outcome | CG-10 | SUPPORTING
MCF-RES-001 | Minimum Service Outcome | CG-09 | SUPPORTING
MCF-RES-002 | Graceful Degradation | CG-09 | SUPPORTING
MCF-RES-002 | Graceful Degradation | CG-10 | SUPPORTING
MCF-RES-003 | Resilience Scenarios | CG-09 | SUPPORTING
MCF-RES-003 | Resilience Scenarios | CG-10 | SUPPORTING
MCF-RES-003 | Resilience Scenarios | CG-03 | SUPPORTING
MCF-RES-004 | Resilience Ownership | CG-13 | SUPPORTING
MCF-RES-005 | Fault-Domain Definition | CG-09 | CRITICAL
MCF-RES-005 | Fault-Domain Definition | CG-03 | SUPPORTING
MCF-RES-005 | Fault-Domain Definition | CG-02 | SUPPORTING
MCF-RES-006 | Containment Boundaries | CG-09 | SUPPORTING
MCF-RES-007 | Blast Radius | CG-09 | CRITICAL
MCF-RES-007 | Blast Radius | CG-03 | SUPPORTING
MCF-RES-008 | Isolation Validation | CG-09 | CRITICAL
MCF-RES-008 | Isolation Validation | CG-04 | SUPPORTING
MCF-RES-009 | Continuity Strategy | CG-10 | SUPPORTING
MCF-RES-009 | Continuity Strategy | CG-01 | SUPPORTING
MCF-RES-010 | Alternative Capacity | CG-10 | SUPPORTING
MCF-RES-010 | Alternative Capacity | CG-03 | SUPPORTING
MCF-RES-011 | Site and Provider Continuity | CG-03 | SUPPORTING
MCF-RES-011 | Site and Provider Continuity | CG-10 | SUPPORTING
MCF-RES-012 | Crisis Priorities | CG-10 | SUPPORTING
MCF-RES-012 | Crisis Priorities | CG-01 | SUPPORTING
MCF-RES-013 | Recovery Dependencies | CG-10 | CRITICAL
MCF-RES-013 | Recovery Dependencies | CG-03 | SUPPORTING
MCF-RES-014 | Recovery Sequencing | CG-10 | CRITICAL
MCF-RES-014 | Recovery Sequencing | CG-05 | SUPPORTING
MCF-RES-014 | Recovery Sequencing | CG-06 | SUPPORTING
MCF-RES-015 | Configuration Restoration | CG-10 | SUPPORTING
MCF-RES-015 | Configuration Restoration | CG-07 | SUPPORTING
MCF-RES-015 | Configuration Restoration | CG-14 | SUPPORTING
MCF-RES-016 | Data and Checkpoint Recovery | CG-10 | CRITICAL
MCF-RES-016 | Data and Checkpoint Recovery | CG-08 | SUPPORTING
MCF-RES-017 | Component Tests | CG-10 | SUPPORTING
MCF-RES-017 | Component Tests | CG-05 | SUPPORTING
MCF-RES-017 | Component Tests | CG-06 | SUPPORTING
MCF-RES-018 | Integrated Scenario Tests | CG-10 | CRITICAL
MCF-RES-018 | Integrated Scenario Tests | CG-09 | SUPPORTING
MCF-RES-018 | Integrated Scenario Tests | CG-05 | SUPPORTING
MCF-RES-018 | Integrated Scenario Tests | CG-06 | SUPPORTING
MCF-RES-019 | Tabletop Exercises | CG-10 | SUPPORTING
MCF-RES-019 | Tabletop Exercises | CG-13 | SUPPORTING
MCF-RES-020 | Lessons and Retest | CG-10 | SUPPORTING
MCF-RES-020 | Lessons and Retest | CG-14 | SUPPORTING
MCF-RES-021 | Crisis Command | CG-13 | SUPPORTING
MCF-RES-021 | Crisis Command | CG-10 | SUPPORTING
MCF-RES-022 | Stakeholder Communications | CG-13 | SUPPORTING
MCF-RES-023 | Emergency Change | CG-14 | SUPPORTING
MCF-RES-024 | Post-Event Adaptation | CG-14 | SUPPORTING
MCF-SUP-001 | Supplier Capability | CG-03 | SUPPORTING
MCF-SUP-002 | Financial and Operational Resilience | CG-03 | SUPPORTING
MCF-SUP-003 | Security and Quality Posture | CG-08 | SUPPORTING
MCF-SUP-003 | Security and Quality Posture | CG-15 | SUPPORTING
MCF-SUP-004 | Sub-Tier Visibility | CG-03 | CRITICAL
MCF-SUP-005 | Service Levels | CG-10 | SUPPORTING
MCF-SUP-005 | Service Levels | CG-13 | SUPPORTING
MCF-SUP-006 | Evidence Rights | CG-03 | SUPPORTING
MCF-SUP-007 | Incident Notification | CG-03 | SUPPORTING
MCF-SUP-007 | Incident Notification | CG-15 | SUPPORTING
MCF-SUP-008 | Exit and Transition Rights | CG-10 | SUPPORTING
MCF-SUP-009 | Approved Sourcing | CG-08 | SUPPORTING
MCF-SUP-009 | Approved Sourcing | CG-04 | SUPPORTING
MCF-SUP-010 | Counterfeit Prevention | CG-04 | SUPPORTING
MCF-SUP-010 | Counterfeit Prevention | CG-08 | SUPPORTING
MCF-SUP-011 | Chain of Custody | CG-08 | SUPPORTING
MCF-SUP-012 | Component Traceability | CG-08 | SUPPORTING
MCF-SUP-012 | Component Traceability | CG-03 | SUPPORTING
MCF-SUP-013 | Release Provenance | CG-15 | SUPPORTING
MCF-SUP-013 | Release Provenance | CG-14 | SUPPORTING
MCF-SUP-014 | Signature Validation | CG-15 | SUPPORTING
MCF-SUP-014 | Signature Validation | CG-08 | SUPPORTING
MCF-SUP-015 | Compatibility Assurance | CG-14 | SUPPORTING
MCF-SUP-015 | Compatibility Assurance | CG-08 | SUPPORTING
MCF-SUP-015 | Compatibility Assurance | CG-09 | SUPPORTING
MCF-SUP-016 | Vulnerability Response | CG-15 | SUPPORTING
MCF-SUP-017 | Critical Spares | CG-10 | SUPPORTING
MCF-SUP-017 | Critical Spares | CG-05 | SUPPORTING
MCF-SUP-017 | Critical Spares | CG-06 | SUPPORTING
MCF-SUP-018 | Lead Times | CG-10 | SUPPORTING
MCF-SUP-018 | Lead Times | CG-03 | SUPPORTING
MCF-SUP-019 | Logistics Continuity | CG-10 | SUPPORTING
MCF-SUP-019 | Logistics Continuity | CG-05 | SUPPORTING
MCF-SUP-020 | End-of-Life Planning | CG-03 | SUPPORTING
MCF-SUP-021 | Support Identity | CG-15 | CRITICAL
MCF-SUP-021 | Support Identity | CG-13 | SUPPORTING
MCF-SUP-022 | Activation and Approval | CG-15 | CRITICAL
MCF-SUP-022 | Activation and Approval | CG-14 | SUPPORTING
MCF-SUP-023 | Session Monitoring | CG-15 | SUPPORTING
MCF-SUP-024 | Revocation and Review | CG-15 | SUPPORTING
MCF-SUP-024 | Revocation and Review | CG-13 | SUPPORTING
MCF-SEC-001 | Human Identity | CG-15 | SUPPORTING
MCF-SEC-001 | Human Identity | CG-07 | SUPPORTING
MCF-SEC-001 | Human Identity | CG-13 | SUPPORTING
MCF-SEC-002 | Machine Identity | CG-15 | SUPPORTING
MCF-SEC-002 | Machine Identity | CG-08 | SUPPORTING
MCF-SEC-003 | Privileged Access | CG-15 | CRITICAL
MCF-SEC-003 | Privileged Access | CG-07 | SUPPORTING
MCF-SEC-004 | Break-Glass Governance | CG-15 | SUPPORTING
MCF-SEC-004 | Break-Glass Governance | CG-10 | SUPPORTING
MCF-SEC-005 | BMS and EPMS Security | CG-07 | CRITICAL
MCF-SEC-005 | BMS and EPMS Security | CG-15 | SUPPORTING
MCF-SEC-005 | BMS and EPMS Security | CG-05 | SUPPORTING
MCF-SEC-005 | BMS and EPMS Security | CG-06 | SUPPORTING
MCF-SEC-006 | Cluster Manager Security | CG-15 | CRITICAL
MCF-SEC-006 | Cluster Manager Security | CG-08 | SUPPORTING
MCF-SEC-007 | Fabric Controller Security | CG-15 | SUPPORTING
MCF-SEC-007 | Fabric Controller Security | CG-08 | SUPPORTING
MCF-SEC-008 | Storage Controller Security | CG-15 | SUPPORTING
MCF-SEC-008 | Storage Controller Security | CG-10 | SUPPORTING
MCF-SEC-008 | Storage Controller Security | CG-08 | SUPPORTING
MCF-SEC-009 | Security Zoning | CG-07 | CRITICAL
MCF-SEC-009 | Security Zoning | CG-15 | SUPPORTING
MCF-SEC-009 | Security Zoning | CG-09 | SUPPORTING
MCF-SEC-010 | Management-Plane Segmentation | CG-15 | CRITICAL
MCF-SEC-010 | Management-Plane Segmentation | CG-07 | SUPPORTING
MCF-SEC-011 | Filtering and Gateways | CG-07 | SUPPORTING
MCF-SEC-011 | Filtering and Gateways | CG-15 | SUPPORTING
MCF-SEC-012 | Remote Access | CG-15 | CRITICAL
MCF-SEC-012 | Remote Access | CG-07 | SUPPORTING
MCF-SEC-013 | Secure Baseline | CG-07 | SUPPORTING
MCF-SEC-013 | Secure Baseline | CG-15 | SUPPORTING
MCF-SEC-013 | Secure Baseline | CG-08 | SUPPORTING
MCF-SEC-014 | Vulnerability Management | CG-07 | SUPPORTING
MCF-SEC-014 | Vulnerability Management | CG-15 | SUPPORTING
MCF-SEC-015 | Patch Governance | CG-14 | SUPPORTING
MCF-SEC-015 | Patch Governance | CG-07 | SUPPORTING
MCF-SEC-016 | Exception and Compensating Control | CG-07 | SUPPORTING
MCF-SEC-016 | Exception and Compensating Control | CG-15 | SUPPORTING
MCF-SEC-017 | Security Telemetry | CG-15 | SUPPORTING
MCF-SEC-017 | Security Telemetry | CG-07 | SUPPORTING
MCF-SEC-018 | Behaviour Detection | CG-15 | SUPPORTING
MCF-SEC-018 | Behaviour Detection | CG-07 | SUPPORTING
MCF-SEC-019 | Incident Containment | CG-09 | SUPPORTING
MCF-SEC-019 | Incident Containment | CG-15 | SUPPORTING
MCF-SEC-019 | Incident Containment | CG-07 | SUPPORTING
MCF-SEC-019 | Incident Containment | CG-10 | SUPPORTING
MCF-SEC-020 | Forensic Readiness | CG-15 | SUPPORTING
MCF-SEC-021 | Agent or Automation Authority | CG-15 | CRITICAL
MCF-SEC-021 | Agent or Automation Authority | CG-07 | SUPPORTING
MCF-SEC-022 | Approval Controls | CG-15 | SUPPORTING
MCF-SEC-022 | Approval Controls | CG-14 | SUPPORTING
MCF-SEC-023 | Command Allowlisting | CG-07 | CRITICAL
MCF-SEC-023 | Command Allowlisting | CG-15 | SUPPORTING
MCF-SEC-024 | Safe Rollback | CG-15 | SUPPORTING
MCF-SEC-024 | Safe Rollback | CG-10 | SUPPORTING
MCF-SEC-024 | Safe Rollback | CG-07 | SUPPORTING
MCF-EVA-002 | Evidence Ownership | CG-13 | SUPPORTING
MCF-EVA-009 | Decision Question | CG-01 | CRITICAL
MCF-EVA-010 | Scope and Criteria | CG-02 | CRITICAL
MCF-EVA-011 | Sampling and Testing | CG-04 | SUPPORTING
MCF-EVA-019 | Independent Decision | CG-13 | SUPPORTING
MCF-EVA-022 | Change Triggers | CG-14 | SUPPORTING

## Critical Gates
Gate | Name | Scope | Evidence Floor | CRITICAL controls | SUPPORTING controls | CRITICAL control IDs
CG-01 | Capability and outcome definition | Capability Instance, Service Outcomes, tolerances, criticality and decision question are defined, owned and approved | S3 | 7 | 16 | MCF-CAP-001; MCF-CAP-005; MCF-CAP-006; MCF-CAP-007; MCF-CAP-008; MCF-CAP-010; MCF-EVA-009
CG-02 | Boundary and architecture integrity | Assessment boundary, current architecture, as-built reconciliation and exclusions | S3 | 3 | 16 | MCF-CAP-004; MCF-DEP-017; MCF-EVA-010
CG-03 | Critical dependency visibility | Material internal and external dependencies, common-mode exposure and concentration are identified and owned | S4 | 9 | 50 | MCF-DEP-001; MCF-DEP-002; MCF-DEP-005; MCF-DEP-007; MCF-DEP-009; MCF-DEP-010; MCF-DEP-012; MCF-DEP-017; MCF-SUP-004
CG-04 | Life safety and hazardous energy | Fire, electrical arc-flash and shock, hazardous fluids and chemicals, confined space, refrigerants, battery thermal runaway and safe work | S4 | 13 | 24 | MCF-PHY-021; MCF-PHY-022; MCF-PHY-023; MCF-PHY-024; MCF-POW-010; MCF-POW-013; MCF-POW-016; MCF-POW-023; MCF-THM-018; MCF-ENV-018; MCF-OPS-004; MCF-OPS-007; MCF-OPS-008
CG-05 | Resilient electrical supply | Utility, distribution, UPS/BESS, generation, fuel, protection and power quality sufficient for the Service Outcomes across operating states | S5 | 8 | 39 | MCF-POW-001; MCF-POW-005; MCF-POW-006; MCF-POW-007; MCF-POW-009; MCF-POW-011; MCF-POW-019; MCF-POW-020
CG-06 | Thermal continuity | Heat-removal path (air, liquid, facility water, heat rejection) sufficient across operating states including transients | S5 | 7 | 46 | MCF-THM-002; MCF-THM-003; MCF-THM-004; MCF-THM-010; MCF-THM-011; MCF-THM-013; MCF-THM-015
CG-07 | Critical control-system integrity | BMS, EPMS, CDU, PLC/SCADA and automation function safely, fail safe, and are configured and governed | S4 | 6 | 26 | MCF-POW-021; MCF-THM-021; MCF-OPS-013; MCF-SEC-005; MCF-SEC-009; MCF-SEC-023
CG-08 | Compute, storage and network functional integrity | Accelerators, storage and fabrics deliver the required function, performance and integrity | S4 | 12 | 63 | MCF-CMP-006; MCF-CMP-009; MCF-CMP-013; MCF-CMP-019; MCF-STO-005; MCF-STO-009; MCF-STO-010; MCF-STO-017; MCF-NET-001; MCF-NET-007; MCF-NET-008; MCF-NET-009
CG-09 | Failure containment | Fault domains, isolation and blast-radius limits prevent propagation beyond tolerance | S4 | 9 | 42 | MCF-PHY-010; MCF-POW-014; MCF-THM-020; MCF-CMP-008; MCF-STO-015; MCF-NET-004; MCF-RES-005; MCF-RES-007; MCF-RES-008
CG-10 | Recovery readiness | Restoration of outcomes (power, cooling, compute, data and checkpoint, network, control plane) within tolerance is planned and tested | S5 | 11 | 56 | MCF-POW-024; MCF-THM-024; MCF-CMP-023; MCF-STO-016; MCF-STO-018; MCF-STO-020; MCF-NET-015; MCF-RES-013; MCF-RES-014; MCF-RES-016; MCF-RES-018
CG-11 | Evidence sufficiency | Evidence for decisive claims meets the AIDCF-008 floors (meta-gate across all controls) | S4 | 0 | 0 | Meta-gate: evaluated across all controls
CG-12 | Critical UNKNOWN | No unresolved US4 or US5 UNKNOWN without disposition (meta-gate across all controls) | S3 | 0 | 0 | Meta-gate: evaluated across all controls
CG-13 | Responsibility and authority | Every critical function and dependency has an accountable owner and decision authority | S3 | 7 | 28 | MCF-GOV-002; MCF-GOV-005; MCF-GOV-006; MCF-GOV-007; MCF-CAP-002; MCF-DEP-018; MCF-OPS-002
CG-14 | Change control | Material changes are controlled, impact-assessed and validated | S4 | 7 | 35 | MCF-CAP-023; MCF-CMP-015; MCF-NET-022; MCF-OPS-006; MCF-OPS-017; MCF-OPS-018; MCF-OPS-020
CG-15 | Integrated digital authority over infrastructure | Identity, privilege, remote access and control-plane reach over facility and AI infrastructure are bounded, monitored and recoverable | S4 | 7 | 42 | MCF-SUP-021; MCF-SUP-022; MCF-SEC-003; MCF-SEC-006; MCF-SEC-010; MCF-SEC-012; MCF-SEC-021

## Parameters
Control ID | Parameter | Unit | Illustrative Default | Basis
MCF-GOV-001 | Governance charter review interval | months | 12 | Capability-profile parameter set by the governing body; illustrative, shortened where the capability is changing rapidly
MCF-GOV-002 | Decision sample size per decision class | records | 10 or the full population if smaller | Judgemental sample per AIDCF-008 sampling principles; illustrative, increased if exceptions are found
MCF-GOV-003 | Oversight meeting interval | months | 3 | Capability-profile parameter; illustrative, shortened during build, major change or after a gate FAIL
MCF-GOV-003 | Out-of-cycle notification time for gate FAIL or US4/US5 UNKNOWN | working days | 5 | Capability-profile parameter; illustrative
MCF-GOV-005 | RACI reconciliation interval | months | 6 | Capability-profile parameter; illustrative
MCF-GOV-007 | Maximum risk-acceptance validity | months | 12 | Capability-profile parameter; illustrative, shorter for acceptances touching gate-critical controls
MCF-GOV-011 | Maximum exception duration | months | 6 | Capability-profile parameter; illustrative, renewable once by the approver
MCF-GOV-012 | Runbook review interval | months | 12 | Capability-profile parameter; illustrative, shorter for emergency runbooks after change
MCF-GOV-013 | Assurance planning period | months | 12 | Programme parameter; illustrative
MCF-GOV-016 | Review effectiveness test frequency | tests per year | 1 | Programme parameter; illustrative
MCF-GOV-018 | Regulatory escalation time for safety or reporting-duty changes | working days | 10 | Programme parameter; illustrative
MCF-GOV-020 | External correction time after decision suspension | working days | 10 | Programme parameter; illustrative
MCF-GOV-021 | Self-review cooling-off period | months | 12 | Programme parameter; illustrative
MCF-GOV-023 | Competence currency period | months | 24 | Programme parameter; illustrative, shorter for rapidly changing technologies
MCF-CAP-001 | Capability register reconciliation interval | months | 3 | Capability-profile parameter; illustrative, aligned to the rate of cluster expansion
MCF-CAP-004 | Architecture reconciliation interval | months | 6 | Capability-profile parameter; illustrative
MCF-CAP-005 | Availability target | % of measurement window | 99.5 (training) / 99.9 (inference) | Capability-profile parameter set by the capability owner; illustrative only
MCF-CAP-005 | Availability measurement window | days | 30 | Capability-profile parameter; illustrative
MCF-CAP-005 | Maximum single-interruption duration | minutes | 60 | Capability-profile parameter; illustrative, derived from impact tolerance
MCF-CAP-006 | Training goodput floor | % of wall-clock time doing useful training progress | 90 | Capability-profile parameter; illustrative
MCF-CAP-006 | Inference latency percentile and bound | ms at p99 | set per service | Capability-profile parameter; no generic default
MCF-CAP-006 | Throttling event tolerance | accelerator-hours throttled per week | 0 attributable to facility conditions | Capability-profile parameter; illustrative
MCF-CAP-007 | Checkpoint integrity verification point | event | on write and before restore | Capability-profile parameter; illustrative
MCF-CAP-007 | Tolerated detection latency for dataset corruption | hours | 24 | Capability-profile parameter; illustrative
MCF-CAP-008 | Recovery time objective | hours to restore stated capacity | 4 to 80% capacity | Capability-profile parameter; illustrative
MCF-CAP-008 | Recovery point objective (training) | minutes of lost training | 30 | Capability-profile parameter; illustrative, constrained by checkpoint write time
MCF-CAP-008 | Recovered capacity fraction for RTO | % of committed accelerators | 80 | Capability-profile parameter; illustrative
MCF-CAP-010 | Maximum tolerable interruption | hours | 8 | Capability-profile parameter; illustrative
MCF-CAP-010 | Maximum tolerable capacity reduction | % of committed capacity for stated duration | 50% for 24 h | Capability-profile parameter; illustrative
MCF-CAP-010 | Maximum tolerable lost training progress | hours of training | 2 | Capability-profile parameter; illustrative
MCF-CAP-012 | Priority reconciliation interval | months | 6 | Capability-profile parameter; illustrative
MCF-CAP-013 | Baseline period | days | 90 | Capability-profile parameter; illustrative, should include representative workload cycles
MCF-CAP-013 | Baseline telemetry resolution | seconds | 60 | Capability-profile parameter; illustrative, transient characterisation is addressed in MCF-CAP-014
MCF-CAP-013 | Baseline refresh interval | months | 3 | Capability-profile parameter; illustrative
MCF-CAP-014 | Transient measurement resolution | ms | 100 or finer | Capability-profile parameter; illustrative, must resolve the fastest step of interest
MCF-CAP-014 | Maximum load step change | % of pod IT load | measured; no default | Measured characteristic, not a design default
MCF-CAP-014 | Maximum ramp rate | kW per second per pod | measured; no default | Measured characteristic, not a design default
MCF-CAP-015 | Planning horizon | months | 36 | Capability-profile parameter; illustrative
MCF-CAP-015 | Forecast review interval | months | 6 | Capability-profile parameter; illustrative
MCF-CAP-016 | Scenario demand exercise interval | months | 12 | Capability-profile parameter; illustrative
MCF-CAP-016 | Restart staging group size | % of instance accelerators per step | 25 | Capability-profile parameter; illustrative
MCF-CAP-017 | Design margin below lowest-rated element | % of rating | 10 | Capability-profile parameter; illustrative
MCF-CAP-018 | Air inlet temperature range | degC | 18-27 | ASHRAE TC 9.9 recommended envelope for air-cooled IT; OEM limits prevail where stricter
MCF-CAP-018 | Technology cooling system supply temperature upper limit | degC | per OEM specification | OEM specification; no generic default
MCF-CAP-019 | Duration validation interval | months | 12 | Capability-profile parameter; illustrative
MCF-CAP-019 | Thermal ride-through on loss of facility water | minutes | validated value; no default | Validated characteristic, not a design default
MCF-CAP-019 | Response margin before limit | % of validated duration | 50 | Capability-profile parameter; illustrative
MCF-CAP-020 | Maximum IT load in reduced-redundancy maintenance | % of normal envelope | per redundancy study; no default | Derived from POW/THM redundancy studies
MCF-CAP-021 | Traceability reconciliation interval | months | 12 | Capability-profile parameter; illustrative
MCF-CAP-022 | Commissioning test load | % of design IT load | 100 | Capability-profile parameter; illustrative, using load banks or representative workloads
MCF-CAP-024 | Record update time after retirement | working days | 10 | Capability-profile parameter; illustrative
MCF-DEP-001 | Mapping completeness for critical Required Functions | % of functions with verified mapping | 100 | Illustrative; any unmapped critical function defeats dependency visibility, so the profile normally sets 100%.
MCF-DEP-001 | Reconciliation sample size | assets per InfrastructureSystem | 10 or all if fewer | Illustrative; set by AIDCF-009 sampling rules and population size.
MCF-DEP-001 | Reconciliation interval | months | 12 | Illustrative; shorten for estates with high deployment churn such as accelerator cluster expansion.
MCF-DEP-002 | Minimum trace depth beyond boundary | upstream nodes | 1 (first shared upstream node) | Illustrative; deeper tracing is set in the profile where concentration risk is high.
MCF-DEP-002 | Corroboration sample | % of external dependency records | 25 (minimum 5 records) | Illustrative; set per AIDCF-009 sampling rules.
MCF-DEP-003 | Thermal ride-through at declared rack load | seconds | Site-specific (no default) | Derived from THM analysis and test; liquid-cooled high-density racks can have very short ride-through, so it is never assumed.
MCF-DEP-003 | Maximum training work lost per interruption | minutes of cluster time | Equal to checkpoint interval (illustrative 30) | Illustrative; set from the Service Outcome tolerance in CAP.
MCF-DEP-004 | Maximum acceptable unresolved circular dependencies on critical functions | count | 0 | Illustrative; any unresolved cycle on a critical function defeats recovery planning.
MCF-DEP-005 | Upstream depth examined for shared source | levels | To grid supply point / carrier POP / fuel terminal | Illustrative; profile sets depth based on the declared external hazard set.
MCF-DEP-007 | Minimum physical separation for diverse routes | m | Site-specific (no default) | Set in capability profile with reference to fire-zone design and the separation guidance in the cabling standard adopted (for example ANSI/TIA-942 or EN 50600-2-4).
MCF-DEP-007 | Route inspection interval | months | 24 | Illustrative; shorter where third-party works or construction occur nearby.
MCF-DEP-008 | Minimum authorised persons per critical switching task available within response time | persons | 2 | Illustrative; reflects a two-person rule for HV switching common in safe systems of work; set from the site safety rules.
MCF-DEP-009 | Firm capacity margin over declared peak demand | % of declared peak | 10 | Illustrative; set in the capability profile from load growth uncertainty and utility terms.
MCF-DEP-009 | Minimum fuel resupply commitment under emergency | hours from call-off to delivery | Site-specific (no default) | Set from POW fuel autonomy (MCF-POW-007/008) so that autonomy exceeds the committed resupply time with margin.
MCF-DEP-009 | Power quality history reviewed | months | 12 | Illustrative; longer history improves estimate of event frequency.
MCF-DEP-010 | Minimum number of independent carriers for production connectivity | carriers | 2 | Illustrative; set by the connectivity Service Outcome.
MCF-DEP-010 | Carrier time-to-repair commitment | hours | 4 | Illustrative; compare against outcome tolerance.
MCF-DEP-011 | Support entitlement expiry warning | days before expiry | 180 | Illustrative; allows renewal or replacement before entitlement lapses.
MCF-DEP-012 | Maximum dependency of safety or continuity loops on cloud/SaaS services | count | 0 | Illustrative; profile may allow exceptions only with accountable acceptance.
MCF-DEP-013 | Maximum share of usable capability in one fault domain | % of usable capacity | Site-specific (no default) | Derived from the CAP-03 impact tolerance; there is no universal value.
MCF-DEP-014 | Maximum share of a critical asset class from one supplier | % of installed base | Site-specific (no default) | Set in capability profile; standardisation benefits must be weighed against common-mode exposure.
MCF-DEP-015 | Minimum independent holders per critical knowledge item | persons | 2 | Illustrative; external parties count only where contractually available within response time.
MCF-DEP-016 | Substitution validation interval | months | 24 | Illustrative; shorter for dependencies with high event frequency.
MCF-DEP-016 | Time-to-substitute margin | % of tolerance | 75 (demonstrated time no more than 75% of tolerance) | Illustrative; provides margin for real-event degradation.
MCF-DEP-019 | Per-tenant load-step limit | kW per second | Site-specific (no default) | Derived from POW-05 load-step response analysis.
MCF-DEP-020 | Interface deviation review interval | months | 1 | Illustrative.
MCF-DEP-021 | Dependency trend review interval | months | 3 | Illustrative.
MCF-DEP-022 | Provider review interval | months | 3 | Illustrative.
MCF-DEP-023 | Maximum time to update dependency graph after detected change | working days | 10 | Illustrative.
MCF-DEP-024 | Revalidation interval for material dependencies | months | 12 | Illustrative; shorter for high-churn dependencies (cloud services, carriers).
MCF-PHY-001 | Design flood annual exceedance probability for critical plant | % per year | 0.1 (illustrative) | Capability profile; national flood-risk mapping commonly publishes 1% and 0.1% AEP extents
MCF-PHY-001 | Freeboard above design flood level for critical plant | mm | 300 (illustrative) | Capability profile; site flood-risk assessment
MCF-PHY-001 | Hazard assessment review interval | months | 36 (illustrative) | Capability profile
MCF-PHY-002 | External exposure assessment radius | km | 2 (illustrative) | Capability profile; threat assessment
MCF-PHY-002 | Hostile vehicle mitigation rating | vehicle mass / impact speed | 7,500 kg at 48 km/h (illustrative) | Threat assessment; rating per IWA 14-1 or PAS 68 test classification
MCF-PHY-002 | External exposure review interval | months | 12 (illustrative) | Capability profile
MCF-PHY-003 | Heaviest declared delivered item on IT route (crated rack) | kg | 3,000 (illustrative) | Capability profile; rack OEM shipping data
MCF-PHY-003 | Independent access routes for fuel and emergency vehicles | count | 2 (illustrative) | Capability profile; emergency services consultation
MCF-PHY-004 | Adjacent-risk register review interval | months | 12 (illustrative) | Capability profile
MCF-PHY-005 | Design uniformly distributed live load, data hall | kN/m² | 20 (illustrative) | Structural engineer of record; capability profile for dense liquid-cooled racks
MCF-PHY-005 | Planned-load utilisation threshold requiring structural re-check | % of rated capacity | 80 (illustrative) | Capability profile
MCF-PHY-006 | Maximum operating mass per rack position | kg | 2,000 (illustrative) | Structural capacity statement; capability profile
MCF-PHY-006 | Rack-load reconciliation sample | % of positions | 10 (illustrative) | Assessment sampling plan
MCF-PHY-007 | Transmitted vibration limit at IT equipment | mm/s RMS | per most restrictive OEM specification | OEM installation requirements
MCF-PHY-008 | Envelope inspection interval | months | 6 (illustrative) | Capability profile; roofing guidance
MCF-PHY-009 | Authentication factors at critical-space zone entry | count | 2 (illustrative) | Capability profile; threat assessment
MCF-PHY-010 | Fire resistance between compartments holding redundant paths | minutes | 120 (illustrative) | Fire strategy; national building regulations; capability profile
MCF-PHY-010 | Fire-stopping inspection sample per interval | % of penetrations | 20 (illustrative) | Capability profile
MCF-PHY-011 | Leak alarm to isolation time (automatic isolation zones) | s | 60 (illustrative) | Capability profile; CDU OEM guidance
MCF-PHY-011 | Maximum credible leak rate for drainage sizing | L/min | per largest pipe and pump capacity in zone | Thermal design basis
MCF-PHY-013 | Critical-zone access review interval | days | 90 (illustrative) | Capability profile
MCF-PHY-013 | Leaver revocation latency | hours | 4 (illustrative) | Capability profile
MCF-PHY-014 | Maximum visitors per escort in critical zones | ratio | 3:1 (illustrative) | Capability profile
MCF-PHY-015 | Recording retention | days | 90 (illustrative) | Capability profile; local privacy law limits
MCF-PHY-015 | Pixel density for identification views | px/m | 250 | IEC 62676-4 operational requirement categories
MCF-PHY-016 | Alarm acknowledgement time | s | 60 (illustrative) | Capability profile
MCF-PHY-016 | Attendance time at critical-zone alarm | minutes | 5 (illustrative) | Capability profile
MCF-PHY-016 | Unannounced response exercises | per year | 4 (illustrative) | Capability profile
MCF-PHY-017 | Inbound critical shipments with seal inspection | % | 100 (illustrative) | Capability profile
MCF-PHY-018 | Rack or plant mass requiring an approved move plan | kg | 1,500 (illustrative) | Capability profile
MCF-PHY-019 | Media custody inventory reconciliation interval | days | 30 (illustrative) | Capability profile
MCF-PHY-020 | Decommissioned data-bearing devices with per-serial certificate | % | 100 (illustrative) | Capability profile
MCF-PHY-021 | Aspirating detection maximum transport time | s | per design; not greater than the EN 54-20 class limit | EN 54-20 (aspirating smoke detectors); system design
MCF-PHY-021 | Detection functional test interval | months | 12 (illustrative) | NFPA 72 or national fire code; capability profile
MCF-PHY-021 | Maximum detection impairment duration without compensating measure | hours | 0 (illustrative) | Capability profile
MCF-PHY-022 | Gaseous agent design hold time | minutes | 10 (illustrative) | NFPA 2001 or ISO 14520 design practice; fire engineer's design
MCF-PHY-022 | Enclosure integrity test interval | months | 12 (illustrative) | Capability profile; agent standard
MCF-PHY-023 | Emergency lighting full-duration test interval | months | 12 (illustrative) | National emergency lighting standard (e.g. EN 50172); capability profile
MCF-PHY-024 | Emergency shutdown functional test interval | months | 12 (illustrative) | Capability profile; applicable electrical code
MCF-POW-001 | Margin of firm import capacity over modelled peak demand | % of firm capacity | 10 (illustrative) | Capability profile
MCF-POW-001 | Demand forecast horizon | months | 36 (illustrative) | Capability profile; utility lead times
MCF-POW-001 | Metered demand integration interval | minutes | 15 or finer | Utility tariff metering practice; finer resolution needed to capture AI load dynamics
MCF-POW-002 | Supply voltage variation assumed in design | % of nominal | ±10 (illustrative) | EN 50160 voltage characteristics or utility declaration
MCF-POW-002 | Power quality data retention | months | 24 (illustrative) | Capability profile
MCF-POW-003 | Interruption history period | years | 5 (illustrative) | Capability profile; network operator data
MCF-POW-004 | Time to achieve declared load reduction on curtailment instruction | minutes | 15 (illustrative) | Connection agreement; capability profile
MCF-POW-004 | Plan exercise interval | months | 12 (illustrative) | Capability profile
MCF-POW-005 | Generator redundancy | topology | N+1 (illustrative) | Capability profile; outcome tolerance
MCF-POW-005 | Site design ambient for generator derating | °C | site extreme design value (ASHRAE climatic data, n-year return; illustrative n=20) | ASHRAE Handbook climatic design data; capability profile
MCF-POW-005 | Periodic load-bank test duration at rated load | hours | 4 (illustrative) | NFPA 110 or national emergency power practice; capability profile
MCF-POW-006 | Maximum start-to-load-acceptance time | s | 10 (illustrative; NFPA 110 Type 10 defines 10 s) | NFPA 110 type classification; UPS autonomy
MCF-POW-006 | Monthly test load | % of nameplate | 30 (illustrative) | NFPA 110 monthly exercise practice
MCF-POW-006 | Start reliability threshold for incident review | failed or delayed starts per year | 0 (illustrative) | Capability profile
MCF-POW-007 | On-site fuel autonomy at declared load | hours | 48 (illustrative) | Capability profile; outcome tolerance and replenishment risk
MCF-POW-007 | Fuel quality test interval | months | 6 (illustrative) | Capability profile; fuel specification (EN 590, ASTM D975 or EN 15940)
MCF-POW-008 | Guaranteed emergency resupply lead time | hours | 12 (illustrative) | Supply contracts; capability profile
MCF-POW-008 | Independent fuel suppliers | count | 2 (illustrative) | Capability profile
MCF-POW-009 | Declared UPS redundancy | topology | 2N or distributed redundant (illustrative) | Capability profile
MCF-POW-009 | Maximum normal-state loading of each path in a 2N design | % of path rating | 45 (illustrative) | Capability profile; failure analysis
MCF-POW-010 | Battery end-of-life capacity threshold | % of rated capacity | 80 | IEEE 450 / IEEE 1188 replacement criterion for lead-acid; OEM criterion for lithium-ion
MCF-POW-010 | Battery capacity test interval | months | 12 (illustrative) | Capability profile; IEEE 450/1188
MCF-POW-010 | BMS critical alarm response time | minutes | 15 (illustrative) | Capability profile
MCF-POW-011 | Minimum UPS/BESS runtime at declared load, end of life | minutes | 5 (illustrative) | Capability profile; generator start time and workload preservation time
MCF-POW-011 | Load growth threshold triggering runtime recalculation | % of declared load | 10 (illustrative) | Capability profile
MCF-POW-012 | Cumulative bypass exposure limit per UPS system | hours per year | 24 (illustrative) | Capability profile
MCF-POW-012 | Unplanned bypass escalation time | minutes | 15 (illustrative) | Capability profile
MCF-POW-013 | Arc-flash study review interval | years | 5 | NFPA 70E review requirement
MCF-POW-013 | Incident energy threshold requiring reduction measure | cal/cm² | 8 (illustrative) | Capability profile; NFPA 70E / IEEE 1584 methodology
MCF-POW-013 | Infrared thermography interval | months | 12 (illustrative) | NFPA 70B / capability profile
MCF-POW-014 | Protection setting extraction and comparison interval | months | 24 (illustrative) | Capability profile
MCF-POW-014 | Permitted deviation of as-found settings from study | count | 0 (illustrative) | Capability profile
MCF-POW-015 | Continuous load limit | % of device rating | 80 (illustrative; for devices not rated for 100% continuous duty) | NFPA 70 / IEC 60364 continuous-load sizing conventions; device rating
MCF-POW-015 | Maximum phase imbalance at PDU/busway | % | 10 (illustrative) | Capability profile
MCF-POW-016 | Periodic inspection and test interval | years | 5 (illustrative) | IEC 60364-6 / national wiring regulations; capability profile
MCF-POW-017 | Steady-state voltage envelope at critical boards | % of nominal | ±5 (illustrative) | Equipment PSU specifications; capability profile
MCF-POW-017 | Voltage unbalance limit | % | 2 (illustrative) | EN 50160 / IEC 61000-2 compatibility levels
MCF-POW-018 | Voltage THD limit at PCC, 1 kV < V ≤ 69 kV | % | 5 | IEEE 519 voltage distortion limits
MCF-POW-018 | Voltage THD limit at PCC, V ≤ 1 kV | % | 8 | IEEE 519 voltage distortion limits
MCF-POW-019 | Static transfer switch transfer time | ms | 4 (illustrative; within PSU hold-up) | STS OEM data; PSU hold-up specification
MCF-POW-019 | Maximum restart time for non-UPS cooling plant | s | per thermal ride-through analysis (THM) | Thermal design basis
MCF-POW-020 | Maximum cluster power swing amplitude | % of cluster IT load | 50 (illustrative) | Measured cluster data or accelerator vendor specification
MCF-POW-020 | Power oscillation frequency band of concern | Hz | 0.1 to 20 (illustrative) | Cluster characterisation; generator and grid modal analysis
MCF-POW-020 | Maximum single load step on generator supply | % of generator rating | per ISO 8528-5 class and test data (illustrative: 50) | ISO 8528-5 load acceptance performance classes
MCF-POW-020 | Measurement resolution for AI load dynamics | ms | 100 or finer (illustrative) | Capability profile
MCF-POW-021 | Critical-node metering coverage | % of critical nodes | 100 (illustrative) | Capability profile
MCF-POW-021 | Clock synchronisation accuracy for sequence of events | ms | 1 (illustrative) | Capability profile; IEC 61850 time-sync practice
MCF-POW-021 | Maximum EPMS data gap per point | % of period | 1 (illustrative) | Capability profile
MCF-POW-022 | On-time completion of critical electrical maintenance | % | 95 (illustrative) | Capability profile
MCF-POW-022 | Maximum overdue period without approved deferral | days | 30 (illustrative) | Capability profile
MCF-POW-023 | Planned critical switching with approved, peer-checked MOP | % | 100 (illustrative) | Capability profile
MCF-POW-024 | Restoration time from dead site to full critical load | hours | 4 (illustrative) | Capability profile; recovery outcome
MCF-POW-024 | Black-start exercise interval | months | 12 (illustrative) | Capability profile
MCF-THM-001 | Rack design heat load (liquid-cooled AI rack) | kW per rack | 120 (illustrative) | Platform OEM thermal design data; site-specific
MCF-THM-001 | Liquid-capture ratio (direct-to-chip platform) | % of rack heat to liquid | 80 (illustrative) | OEM thermal data or measured; varies by platform generation
MCF-THM-001 | Synchronous load step | % of fault-domain design load within 1 s | 50 (illustrative) | Workload characterisation of synchronous training; to be measured
MCF-THM-001 | Model-to-measured reconciliation tolerance | % of measured heat load | ±10 (illustrative) | Capability profile
MCF-THM-002 | Design capacity margin above design heat load | % | 10 (illustrative) | Capability profile; design authority
MCF-THM-002 | Commissioning load-bank test level | % of design heat load | 100 (illustrative) | ASHRAE Guideline 0 practice; site commissioning plan
MCF-THM-003 | Declared redundancy for CDU stage | configuration | N+1 (illustrative) | Capability profile
MCF-THM-003 | Chiller restart-to-capacity time after power interruption | s | 300 (illustrative) | Manufacturer rapid-restart data; verify by test
MCF-THM-003 | Thermal ride-through required | s | 600 (illustrative) | Derived: restart time plus margin; capability profile
MCF-THM-003 | Maximum TCS supply temperature rise during transient | K | 5 (illustrative) | OEM coolant inlet limit minus normal setpoint
MCF-THM-004 | Design ambient dry-bulb | °C | site-specific (illustrative: 0.4% annual extreme) | ASHRAE climatic design conditions or national equivalent
MCF-THM-004 | Design ambient wet-bulb (evaporative systems) | °C | site-specific | ASHRAE climatic design conditions
MCF-THM-004 | Climate-change allowance on design ambient | K | 2 (illustrative) | Capability profile; regional projections
MCF-THM-004 | High-ambient action threshold | % of derated capacity | 90 (illustrative) | Capability profile
MCF-THM-005 | IT inlet temperature envelope | °C | 18–27 | ASHRAE TC 9.9 recommended envelope (classes A1–A4); site may adopt narrower OEM limits
MCF-THM-005 | Air-handler ΔT lower bound (bypass indicator) | K | 8 (illustrative) | Capability profile
MCF-THM-005 | Hot-spot closure time | h | 24 (illustrative) | Capability profile
MCF-THM-006 | Maximum leakage area of containment | % of containment area | declared by design (illustrative 2) | Design authority
MCF-THM-007 | Air-side redundancy per zone | configuration | N+1 (illustrative) | Capability profile
MCF-THM-007 | Entering-water temperature for rating | °C | site design value | Design basis
MCF-THM-008 | Inlet sensor density | sensors per row | ≥ 3 (illustrative) | Capability profile
MCF-THM-008 | Sensor accuracy | K | ±0.5 (illustrative) | Capability profile; instrument specification
MCF-THM-008 | Calibration interval | months | 12 (illustrative) | Instrument manufacturer / site metrology policy
MCF-THM-009 | Facility water class at CDU interface | ASHRAE W-class | W32 (illustrative) | ASHRAE TC 9.9 liquid-cooling classes W17–W45 and W+
MCF-THM-009 | TCS supply temperature to cold plates | °C | OEM-specified (illustrative 30–40) | Platform OEM specification
MCF-THM-009 | CDU heat-exchanger approach temperature | K | 3 (illustrative) | CDU manufacturer data
MCF-THM-009 | TCS filtration rating | µm | 50 (illustrative; OEM may require finer) | Platform OEM specification; OCP cold-plate guidance
MCF-THM-010 | CDU pump failover recovery time | s | 10 (illustrative) | CDU manufacturer data; verify by test
MCF-THM-010 | Minimum TCS flow per rack | l/min | OEM-specified | Platform OEM specification
MCF-THM-010 | CDU group redundancy | configuration | N+1 (illustrative) | Capability profile
MCF-THM-011 | Pressure test level | × maximum operating pressure | 1.5 (illustrative) | Piping code or manufacturer specification
MCF-THM-011 | Pressure test hold time | min | 30 (illustrative) | Piping code or manufacturer specification
MCF-THM-011 | Unexplained make-up volume investigation threshold | l per week per loop | 5 (illustrative) | Capability profile
MCF-THM-012 | Coupling inspection interval | months | 12 (illustrative) | Coupling manufacturer guidance
MCF-THM-012 | Rated connect/disconnect cycles | cycles | manufacturer-rated | Coupling manufacturer data
MCF-THM-013 | Chiller restart-to-capacity | s | 300 (illustrative) | Manufacturer rapid-restart data
MCF-THM-013 | Chiller redundancy | configuration | N+1 (illustrative) | Capability profile
MCF-THM-014 | Approach temperature degradation threshold | K above commissioned | 2 (illustrative) | Capability profile
MCF-THM-015 | Water autonomy at peak consumption | h | 48 (illustrative) | Capability profile; utility risk assessment
MCF-THM-015 | Peak water consumption | m³/h | site-calculated | Design calculation at design wet-bulb and load
MCF-THM-017 | Glycol concentration | % by volume | OEM-specified (illustrative 25) | Platform OEM coolant specification; OCP propylene-glycol guidance
MCF-THM-018 | TCS sampling frequency | per month | 1 (illustrative) | OEM/fluid supplier guidance
MCF-THM-018 | Out-of-limit corrective-action time | days | 7 (illustrative) | Capability profile
MCF-THM-018 | Legionella risk assessment review interval | months | 24 or on change (illustrative) | Applicable national regulation/ACOP
MCF-THM-019 | Leak detection functional test interval | months | 12 (illustrative) | Manufacturer guidance; capability profile
MCF-THM-019 | Alarm-to-acknowledgement time | min | 5 (illustrative) | Capability profile
MCF-THM-020 | Maximum release volume per isolated section | l | design-specific (illustrative 50) | Design authority
MCF-THM-020 | Valve exercise interval | months | 12 (illustrative) | Manufacturer guidance
MCF-THM-021 | Settling time after load step | s | 120 (illustrative) | Controls design; capability profile
MCF-THM-021 | Temperature control band | K | ±1 (illustrative) | Controls design
MCF-THM-022 | Control-critical sensor calibration interval | months | 12 (illustrative) | Instrument manufacturer / metrology policy
MCF-THM-022 | Redundant-sensor divergence alarm | K | 1.5 (illustrative) | Capability profile
MCF-THM-023 | Minimum residual redundancy during maintenance | configuration | N (illustrative) | Capability profile; risk acceptance
MCF-THM-024 | Thermal recovery time objective | min | 30 (illustrative) | Capability profile
MCF-THM-024 | IT readmission step | % of fault-domain design load | 25 (illustrative) | Capability profile; recovering capacity
MCF-ENV-001 | Recommended IT inlet air temperature envelope | °C | 18 to 27 | ASHRAE TC 9.9 thermal guidelines recommended envelope
MCF-ENV-001 | Liquid-cooling facility/TCS supply class | ASHRAE W class | W32 or W45 (illustrative) | ASHRAE TC 9.9 liquid cooling classes; OEM requirement
MCF-ENV-001 | Rack inlet sensor density | sensors per rack | 3 (top, middle, bottom; illustrative) | Capability profile; ASHRAE measurement practice
MCF-ENV-001 | Permitted excursion time outside recommended envelope | hours per year | per OEM allowable (illustrative: 50) | Capability profile
MCF-ENV-002 | Recommended dew point envelope | °C dew point | -9 to 15, and ≤ 60% RH | ASHRAE TC 9.9 thermal guidelines recommended envelope
MCF-ENV-002 | Minimum margin of coolant supply temperature above room dew point | K | 2 (illustrative) | Capability profile; CDU OEM guidance
MCF-ENV-003 | Gaseous corrosion severity level | ANSI/ISA-71.04 class | G1 | ASHRAE TC 9.9 gaseous and particulate contamination guidance
MCF-ENV-003 | Particulate cleanliness | ISO 14644-1 class | 8 | ASHRAE TC 9.9 contamination guidance
MCF-ENV-003 | Corrosion coupon interval | months | 3 (illustrative) | Capability profile
MCF-ENV-004 | Occupational noise lower / upper exposure action values | dB(A) daily exposure | 80 / 85 | EU Directive 2003/10/EC (noise at work) or national equivalent
MCF-ENV-004 | Sound pressure limit at storage arrays during discharge | dB | per storage OEM threshold | Storage OEM guidance; suppression designer
MCF-ENV-004 | Site boundary noise limit | dB(A) | per planning or environmental permit | Permit conditions
MCF-ENV-005 | PUE measurement period | months | 12 | ISO/IEC 30134-2
MCF-ENV-005 | PUE measurement category | category | Category 2 or higher (illustrative) | ISO/IEC 30134-2; capability profile
MCF-ENV-005 | Revenue/sub-meter accuracy class | class | 0.5S or better (illustrative) | IEC 62053 series
MCF-ENV-006 | Maximum unallocated energy | % of site total | 2 (illustrative) | Capability profile
MCF-ENV-007 | IT load points for efficiency characterisation | % of design IT load | 25 / 50 / 75 / 100 (illustrative) | Capability profile
MCF-ENV-007 | Energy reuse factor reporting | ratio | measured annually | ISO/IEC 30134-6
MCF-ENV-009 | Legionella risk assessment review interval | months | 24 (illustrative) | National Legionella guidance (e.g. HSE L8, ASHRAE 188); capability profile
MCF-ENV-010 | WUE measurement period | months | 12 | ISO/IEC 30134-9
MCF-ENV-011 | On-site water storage autonomy at design-day consumption | hours | 48 (illustrative) | Capability profile
MCF-ENV-011 | Heat-rejection capacity in reduced-water mode at design ambient | % of design IT load | per thermal design (illustrative: 80) | Thermal design basis
MCF-ENV-012 | Discharge monitoring frequency | per consent | per permit conditions | Discharge consent
MCF-ENV-013 | Materiality threshold for boundary exclusions | % of total emissions | 5 (illustrative) | Capability profile; GHG Protocol guidance on exclusions
MCF-ENV-014 | Temporal matching granularity | interval | annual or hourly (declared) | GHG Protocol Scope 2 Guidance; hourly matching frameworks
MCF-ENV-015 | Embodied data coverage | % of hardware and plant by spend | 80 (illustrative) | Capability profile
MCF-ENV-016 | Restatement threshold | % change in reported metric | 5 (illustrative) | Capability profile
MCF-ENV-017 | Maximum state of charge for stored lithium-ion spares | % SoC | 30 (illustrative) | OEM guidance; aligns with air-transport limit for UN 3480 lithium-ion batteries
MCF-ENV-018 | Refrigerant leak-check frequency | per system | tiered by CO2e charge per applicable regulation | EU F-gas Regulation (EU) 2024/573 or national equivalent
MCF-ENV-018 | Refrigerant detector alarm setpoint | % of practical limit or ATEL/ODL | per EN 378 / ISO 5149 (illustrative: 50% of practical limit) | EN 378 / ISO 5149 refrigerating systems safety
MCF-ENV-019 | Secondary containment capacity | % of largest tank volume | 110 (illustrative) | Common oil-storage regulation and bunding practice; local permit
MCF-ENV-021 | Design extreme ambient dry-bulb | °C | site n=20-year extreme (illustrative) | ASHRAE Handbook climatic design data
MCF-ENV-021 | Climate-adjusted design ambient uplift | K | 2 (illustrative) | Owner-adopted climate projection (e.g. IPCC AR6 scenario)
MCF-ENV-021 | Forecast trigger margin below design ambient | K | 3 (illustrative) | Capability profile
MCF-ENV-022 | Water-stress planning horizon | years | 20 (illustrative) | Capability profile
MCF-ENV-023 | Climate scenario and horizon for flood adaptation | scenario / year | SSP2-4.5 to 2060 (illustrative) | IPCC AR6 scenarios; owner-adopted projection
MCF-ENV-023 | Demountable defence deployment time | hours | less than flood warning lead time (illustrative: 4) | Flood response plan
MCF-ENV-024 | Resource planning horizon | years | 15 (illustrative) | Capability profile
MCF-CMP-001 | Accelerators per scale-up domain | count | platform-specific (illustrative: 8 node-scale; 72 rack-scale) | Platform OEM architecture
MCF-CMP-001 | Scale-out bandwidth per accelerator | Gb/s | 400 (illustrative) | Fabric design; platform OEM reference architecture
MCF-CMP-001 | Rack power envelope | kW | 120 (illustrative) | Platform OEM data; facility power budget
MCF-CMP-002 | Configuration conformance coverage | % of nodes | 100 (illustrative) | Capability profile
MCF-CMP-002 | Conformance scan interval | days | 7 (illustrative) | Capability profile
MCF-CMP-002 | Nonconforming node remediation time | days | 3 (illustrative) | Capability profile
MCF-CMP-003 | Rack weight | kg | platform-specific (illustrative 1,500) | Platform OEM data; structural rating
MCF-CMP-004 | Fleet on current baseline | % of nodes | 98 (illustrative) | Capability profile
MCF-CMP-004 | Maximum exception age | days | 30 (illustrative) | Capability profile
MCF-CMP-006 | Minimum scale-up bandwidth | % of rated all-reduce bandwidth | 90 (illustrative) | Platform OEM performance data; capability profile
MCF-CMP-006 | Re-validation interval | days | 30 (illustrative) | Capability profile
MCF-CMP-006 | Link-error drain threshold | errors per hour per link | platform-specific | Platform OEM RAS guidance
MCF-CMP-008 | Maximum capacity fraction in a single facility fault domain | % of Capability Instance accelerators | 25 (illustrative) | Capability profile; outcome tolerance
MCF-CMP-008 | Job resumption time after fault-domain loss | min | 60 (illustrative) | Capability profile; checkpoint interval
MCF-CMP-009 | Required usable capacity | % of installed accelerators | 92 (illustrative) | Capability profile; Service Outcome
MCF-CMP-009 | Throttle performance threshold | % of rated clock or throughput | 95 (illustrative) | Capability profile
MCF-CMP-010 | Scheduler controller failover time | s | 60 (illustrative) | Capability profile
MCF-CMP-011 | Recovery reserve | % of job size | 5 (illustrative) | Capability profile; observed node failure rate
MCF-CMP-011 | Reclaim time | min | 15 (illustrative) | Capability profile
MCF-CMP-012 | Priority job slowdown tolerance | % versus baseline | 10 (illustrative) | Capability profile
MCF-CMP-013 | Firmware drift remediation time | days | 7 (illustrative) | Capability profile
MCF-CMP-013 | Firmware inventory coverage | % of devices | 100 (illustrative) | Capability profile
MCF-CMP-015 | Canary cohort size | % of fleet | 2 (illustrative) | Capability profile
MCF-CMP-015 | Soak period per stage | h | 72 (illustrative) | Capability profile
MCF-CMP-015 | Halt criterion: error-rate increase | × baseline | 2 (illustrative) | Capability profile
MCF-CMP-016 | Rollback time objective | h | 4 (illustrative) | Capability profile
MCF-CMP-017 | Telemetry interval | s | 10 (illustrative) | Capability profile
MCF-CMP-017 | Collection completeness | % of expected samples | 99 (illustrative) | Capability profile
MCF-CMP-017 | Retention | days | 90 (illustrative) | Capability profile
MCF-CMP-018 | Periodic health-check interval | h | 24 (illustrative) | Capability profile
MCF-CMP-018 | Maximum drained-node age before escalation | days | 5 (illustrative) | Capability profile
MCF-CMP-019 | Drain time after fatal error event | min | 5 (illustrative) | Capability profile
MCF-CMP-019 | SDC screening interval | days | 30 (illustrative) | Capability profile; OCP SDC practice
MCF-CMP-019 | Correctable ECC escalation threshold | events per day per accelerator | platform-specific | Platform OEM RAS guidance
MCF-CMP-020 | Performance regression threshold | % below baseline | 5 (illustrative) | Capability profile
MCF-CMP-021 | Burn-in duration | h | 48 (illustrative) | Capability profile; OEM guidance
MCF-CMP-022 | On-site spares | % of installed by class | 3 (illustrative) | Capability profile; failure-rate analysis
MCF-CMP-022 | RMA turnaround obligation | days | contractual | Supplier contract
MCF-CMP-023 | Single-node rebuild time objective | h | 2 (illustrative) | Capability profile
MCF-CMP-023 | Mass rebuild fraction | % of cluster | 25 (illustrative) | Capability profile
MCF-CMP-023 | Mass rebuild time objective | h | 12 (illustrative) | Capability profile
MCF-STO-001 | Data-loader read throughput per accelerator | GB/s | workload-specific (illustrative 1) | Workload characterisation
MCF-STO-001 | Permitted data jurisdictions | list | capability-specific | Data owner; applicable law and contracts
MCF-STO-002 | Checkpoint size (large training job) | TB | job-specific (illustrative 10) | Model architecture and optimiser state
MCF-STO-002 | Checkpoint write window | s | 120 (illustrative) | Capability profile; acceptable step stall
MCF-STO-002 | Checkpoint interval | min | derived (illustrative 30) | Young/Daly model using measured interruption rate
MCF-STO-002 | Retained good checkpoints | count | 3 (illustrative) | Capability profile
MCF-STO-004 | Archive copies | count | 2 (illustrative) | Capability profile
MCF-STO-004 | Retrieval time objective | h | 48 (illustrative) | Capability profile
MCF-STO-005 | Required aggregate checkpoint write throughput | GB/s | derived: checkpoint size ÷ window (illustrative 100) | MCF-STO-002 derivation
MCF-STO-005 | Degraded-state minimum | % of required throughput | 70 (illustrative) | Capability profile
MCF-STO-005 | Required aggregate read throughput | GB/s | derived from MCF-STO-001 | Workload characterisation
MCF-STO-006 | Metadata operation p99 latency | ms | 10 (illustrative) | Capability profile
MCF-STO-006 | Required metadata operations | ops/s | workload-specific | Workload characterisation
MCF-STO-007 | Critical utilisation threshold | % of usable capacity | 80 (illustrative) | Storage vendor guidance; capability profile
MCF-STO-007 | Warning threshold | % of usable capacity | 70 (illustrative) | Capability profile
MCF-STO-008 | Concurrent checkpointing jobs | count | 3 (illustrative) | Workload characterisation
MCF-STO-008 | Restart read-storm completion time | min | 15 (illustrative) | Capability profile
MCF-STO-009 | Checksum coverage of checkpoints and artefacts | % | 100 (illustrative) | Capability profile
MCF-STO-010 | Metadata failover time | s | 60 (illustrative) | Capability profile; vendor data
MCF-STO-010 | Consistency check interval | days | 30 (illustrative) | Vendor guidance
MCF-STO-011 | Scrub cycle | days | 30 (illustrative) | Vendor guidance; capability profile
MCF-STO-013 | Snapshot recovery point objective | h | 4 (illustrative) | Capability profile
MCF-STO-013 | Snapshot retention | days | 14 (illustrative) | Capability profile
MCF-STO-014 | Replication RPO (checkpoints) | min | 60 (illustrative) | Capability profile
MCF-STO-014 | Replication RPO (datasets and artefacts) | h | 24 (illustrative) | Capability profile
MCF-STO-015 | Protection scheme | k+m | 8+2 (illustrative) | Capability profile; vendor options
MCF-STO-015 | Concurrent failure-domain tolerance | count | 2 (illustrative) | Capability profile
MCF-STO-015 | Rebuild time objective | h | 24 (illustrative) | Capability profile; vendor data
MCF-STO-016 | Immutable retention | days | 30 (illustrative) | Capability profile
MCF-STO-016 | Restore time from immutable copy | h | 24 (illustrative) | Capability profile
MCF-STO-017 | Retained good checkpoints | count | 3 (illustrative) | Capability profile
MCF-STO-018 | Restart time objective | min | 30 (illustrative) | Capability profile
MCF-STO-018 | Lost work tolerance | min of training | 60 (illustrative) | Capability profile; checkpoint interval
MCF-STO-019 | Storage recovery time objective | h | 4 (illustrative) | Capability profile
MCF-STO-020 | Restore test interval | months | 3 (illustrative) | Capability profile
MCF-STO-021 | Telemetry interval | s | 30 (illustrative) | Capability profile
MCF-STO-022 | Forecast horizon | months | 9 (illustrative) | Procurement lead time
MCF-STO-023 | NVMe wear replacement threshold | % of rated endurance used | 90 (illustrative) | Vendor endurance rating
MCF-STO-023 | AFR investigation threshold | % | 2× fleet baseline (illustrative) | Capability profile
MCF-NET-001 | Rail-mapping conformance | % of accelerator ports on design rail/leaf | 100 (illustrative) | Rail-optimised designs assume ordinal NIC n connects to rail n; any deviation alters collective paths. Site-specific.
MCF-NET-001 | Maximum topology reconciliation age | days | 90 (illustrative) | Capability-profile parameter; shorten where change rate is high.
MCF-NET-002 | Minimum physical separation between diverse routes | m | Site-specific; set by risk analysis (illustrative: separate containment and entry points) | Capability-profile parameter; no universal distance applies.
MCF-NET-002 | Route evidence age | months | 12 (illustrative) | Carriers re-groom circuits; evidence ages.
MCF-NET-003 | Back-end fabric design oversubscription | ratio (downlink:uplink) | 1:1 (illustrative) | Common design choice for large training fabrics; site and workload specific.
MCF-NET-003 | Front-end/storage uplink oversubscription | ratio | Workload-derived (illustrative 3:1) | Capability-profile parameter justified by traffic analysis.
MCF-NET-003 | Minimum tolerated effective ratio under N-1 | ratio | Set per Service Outcome (illustrative 1.15:1 for back-end) | Derived from performance outcome tolerance.
MCF-NET-004 | Maximum endpoints affected by a single switch failure | accelerator ports | Equal to leaf downlink count (illustrative) | Derived from topology; outcome-specific tolerance.
MCF-NET-004 | Maximum reroute/reconvergence time after single spine loss | s | Set by job collective timeout margin (illustrative 30) | Must be below framework collective timeouts; site-specific.
MCF-NET-004 | Subnet-manager failover time | s | Vendor- and scale-dependent (illustrative 60) | Capability-profile parameter verified by test.
MCF-NET-005 | Latency deviation alert threshold | % above baseline at p99 | 25 (illustrative) | Capability-profile parameter tuned to measurement noise.
MCF-NET-005 | Baseline percentile set | percentiles | p50, p99, p99.9 (illustrative) | Tail latency drives synchronous collective step time.
MCF-NET-006 | Link flap isolation threshold | flaps per hour | 3 (illustrative) | Capability-profile parameter.
MCF-NET-006 | Post-FEC uncorrectable codeword threshold | count per interval | Any non-zero sustained (illustrative) | Post-FEC errors become packet loss; vendor guidance applies.
MCF-NET-006 | Pre-FEC BER warning threshold | BER | Vendor/PHY specific (illustrative: one order of magnitude below FEC limit) | Set from IEEE 802.3 FEC capability and vendor guidance.
MCF-NET-007 | PFC watchdog detection time | ms | Vendor default unless tuned (illustrative 200) | Configured per NOS; verified by test.
MCF-NET-007 | Maximum tolerated pause propagation | hops from congestion point | 1 (illustrative) | Design objective to keep pause local.
MCF-NET-007 | Lossless traffic classes | count | 1 or 2 (illustrative) | Fewer lossless classes reduce deadlock and headroom exposure.
MCF-NET-008 | Collective acceptance target | % of design bus bandwidth | 90 (illustrative) | Capability-profile parameter derived from performance outcome.
MCF-NET-008 | Benchmark periodic interval | days | 30 (illustrative) | Detects slow drift.
MCF-NET-009 | Checkpoint write window | s | Derived from checkpoint size and goodput target (illustrative 120) | Capability-profile parameter; see RES-016.
MCF-NET-009 | Tolerated collective degradation during checkpoint | % bus bandwidth reduction | 10 (illustrative) | Capability-profile parameter.
MCF-NET-010 | Front-end peak utilisation ceiling | % of uplink capacity | 70 (illustrative) | Capability-profile parameter for headroom.
MCF-NET-011 | Gateway capacity alert threshold | % of rated connections/throughput | 70 (illustrative) | Capability-profile parameter.
MCF-NET-011 | Tolerated failover disruption | s | Set by inference availability outcome (illustrative 5) | Derived from Service Outcome.
MCF-NET-012 | Guaranteed bandwidth share per tenant class | % of link | Contract-specific (illustrative 25) | Set by tenant commitments (GOV-021).
MCF-NET-012 | Tolerated cross-tenant degradation | % throughput reduction | 5 (illustrative) | Capability-profile parameter.
MCF-NET-014 | Console reachability check interval | days | 30 (illustrative) | Capability-profile parameter.
MCF-NET-015 | OOB power autonomy | h | Equal to or greater than black-start sequence duration (illustrative 4) | Derived from RES-014 restoration sequence.
MCF-NET-015 | OOB test interval | months | 6 (illustrative) | Capability-profile parameter.
MCF-NET-016 | Break-glass post-use review time | h | 24 (illustrative) | Capability-profile parameter.
MCF-NET-016 | Break-glass test interval | months | 6 (illustrative) | Capability-profile parameter.
MCF-NET-017 | Maximum containment fill | % cross-section | Per adopted standard (illustrative 50) | From adopted cabling standard; site-specific.
MCF-NET-017 | Fibre link loss acceptance margin | dB below transceiver budget | Set from optics budget (illustrative 1.0) | Ensures operating margin; see NET-018.
MCF-NET-018 | Rx power warning margin | dB above receiver sensitivity | 2 (illustrative) | Capability-profile parameter derived from vendor budget.
MCF-NET-018 | Optics failure-rate review trigger | failures per 1000 per month | Site baseline-derived (illustrative) | Triggers lot-level analysis.
MCF-NET-019 | Record update time after change | h | 24 (illustrative) | Capability-profile parameter.
MCF-NET-020 | Path record accuracy target | % of audited links correct end-to-end | 99 (illustrative) | Capability-profile parameter.
MCF-NET-020 | Audit sample size | links per audit | Statistically justified (illustrative 200) | Sampling per AIDCF-009.
MCF-NET-021 | Controller failover time tolerance | s | Below job collective timeout margin (illustrative 60) | Capability-profile parameter.
MCF-NET-021 | Controller failover test interval | months | 12 (illustrative) | Capability-profile parameter.
MCF-NET-022 | Drift detection interval | h | 24 (illustrative) | Capability-profile parameter.
MCF-NET-022 | Canary stage size | % of devices | ≤5 (illustrative) | Limits firmware common-mode exposure (X08).
MCF-NET-023 | Telemetry collection interval for congestion counters | s | 10 (illustrative) | Capability-profile parameter; finer for diagnosis.
MCF-NET-023 | Telemetry retention | days | Per evidence retention class (illustrative 395) | AIDCF-008 retention classes.
MCF-NET-024 | Time offset tolerance | ms | Workload- and log-correlation-dependent (illustrative 1 for NTP; sub-microsecond for PTP where required) | Capability-profile parameter.
MCF-NET-024 | Holdover duration | h | Covers time-source repair time (illustrative 24) | Capability-profile parameter.
MCF-OPS-001 | Minimum on-site staff per shift | persons by discipline | Site-specific (no default) | Derived from emergency task analysis; there is no universal staffing ratio.
MCF-OPS-001 | On-call specialist attendance time | minutes | 60 | Illustrative; must be shorter than the time available after on-site staff stabilise the event.
MCF-OPS-001 | Maximum shift length | hours | 12 | Illustrative; set with reference to HSE HSG256 guidance and local working-time law.
MCF-OPS-004 | Authorisation revalidation interval | months | 36 | Illustrative; set by site safety rules and legal requirements.
MCF-OPS-005 | Procedure review interval | months | 12 | Illustrative.
MCF-OPS-007 | Permit audit frequency | audits per month | 4 | Illustrative.
MCF-OPS-008 | LOTO field audit interval | months | 3 | Illustrative.
MCF-OPS-009 | Generator load test frequency | per year | Per NFPA 110 or site standard (no default) | Set from the adopted standard and OEM requirements.
MCF-OPS-010 | Thermography frequency for critical switchgear and busway | per year | 1 | Illustrative; NFPA 70B provides guidance.
MCF-OPS-010 | Coolant quality sampling interval | weeks | 4 | Illustrative; set from CDU and cold-plate OEM requirements.
MCF-OPS-011 | Calibration interval for control-loop temperature sensors | months | 12 | Illustrative; set from OEM and criticality.
MCF-OPS-012 | Maximum deferral without re-approval | days | 30 | Illustrative.
MCF-OPS-013 | Target average alarm rate per operator in normal operation | alarms per hour | Per alarm philosophy (no default) | Set in the alarm philosophy with reference to IEC 62682 / ANSI/ISA-18.2 and EEMUA 191 benchmarks.
MCF-OPS-013 | Alarm performance review interval | months | 1 | Illustrative.
MCF-OPS-014 | Escalation time for Service Outcome-impacting incidents | minutes | 15 | Illustrative.
MCF-OPS-015 | RCA completion time | working days | 20 | Illustrative.
MCF-OPS-016 | Effectiveness verification period | months | 6 | Illustrative.
MCF-OPS-017 | Baseline reconciliation interval | months | 6 | Illustrative; continuous automated drift detection where available.
MCF-OPS-018 | Emergency change retrospective review time | working days | 5 | Illustrative.
MCF-OPS-019 | Maximum temporary configuration duration without re-approval | days | 7 | Illustrative.
MCF-OPS-020 | Post-change observation period for facility control changes | hours | 24 | Illustrative.
MCF-OPS-021 | Capacity planning threshold | % of N-1 available capacity | 80 | Illustrative.
MCF-OPS-022 | Indicator reporting interval | months | 1 | Illustrative.
MCF-OPS-023 | Maximum phase imbalance | % | Site-specific (no default) | Set from UPS and transformer OEM limits.
MCF-OPS-024 | Operational reporting interval | months | 1 | Illustrative.
MCF-RES-001 | Maximum tolerable disruption (training outcome) | h | Business-impact derived (illustrative 24) | ISO/TS 22317-style impact analysis; capability-specific.
MCF-RES-001 | Maximum tolerable disruption (inference outcome) | min | Business-impact derived (illustrative 15) | Capability-specific.
MCF-RES-001 | Maximum lost training progress | h of cluster time | Equal to checkpoint interval plus restart time (illustrative 2) | Links to RES-016.
MCF-RES-001 | Minimum retained capacity in DEGRADED state | % of nominal | 50 (illustrative) | Capability-profile parameter.
MCF-RES-002 | Time to shed load to residual target | min | Less than UPS autonomy minus margin (illustrative 5) | Derived from POW and THM ride-through.
MCF-RES-002 | Accelerator power-cap floor | % of TDP | Vendor-supported range (illustrative 60) | Capability-profile parameter; vendor limits apply.
MCF-RES-005 | Fault-domain model reconciliation age | days | 180 (illustrative) | Capability-profile parameter.
MCF-RES-007 | Maximum blast radius per single credible failure | % of Capability Instance capacity | Impact-tolerance derived (illustrative 25) | Capability-profile parameter.
MCF-RES-008 | Isolation validation cycle | months | 24 (illustrative) | Capability-profile parameter.
MCF-RES-010 | Alternate capacity activation time | h | Within maximum tolerable disruption (illustrative 8) | Derived from RES-001.
MCF-RES-010 | Relocation test interval | months | 12 (illustrative) | Capability-profile parameter.
MCF-RES-011 | Provider continuity evidence age | months | 12 (illustrative) | Capability-profile parameter.
MCF-RES-014 | Target black-start-to-service time | h | Within RTO (illustrative 12) | Derived from RES-001.
MCF-RES-014 | Maximum IT load step during restoration | % of generator rating | Generator- and UPS-specific (illustrative 25) | From POW-020 load-step analysis.
MCF-RES-014 | Integrated restoration test interval | months | 24 (illustrative) | Capability-profile parameter.
MCF-RES-015 | Configuration backup interval | h | 24 or on change (illustrative) | Capability-profile parameter.
MCF-RES-015 | Restore test interval per class | months | 12 (illustrative) | Capability-profile parameter.
MCF-RES-016 | Checkpoint interval | min | Optimised from failure rate and checkpoint cost (illustrative 60) | Young/Daly-style approximation; capability-specific.
MCF-RES-016 | Durable checkpoint copies outside cluster failure domain | count | 1 (illustrative) | Capability-profile parameter.
MCF-RES-016 | Restart-from-checkpoint time | min | Within RTO (illustrative 30) | Derived from RES-001.
MCF-RES-017 | Programme adherence target | % of scheduled tests completed on time | 95 (illustrative) | Capability-profile parameter.
MCF-RES-018 | Integrated test cycle | months | 24 (illustrative) | Capability-profile parameter.
MCF-RES-018 | Representative load during test | % of design IT load | As high as safely authorised (illustrative 70) | Load banks or real workload; site-specific.
MCF-RES-019 | Tabletop cycle | months | 6 (illustrative) | Capability-profile parameter.
MCF-RES-020 | Maximum age of open gate-critical lesson | days | 90 (illustrative) | Capability-profile parameter.
MCF-RES-021 | Crisis command activation time | min from trigger | 30 (illustrative) | Capability-profile parameter.
MCF-RES-023 | Emergency change retrospective review deadline | working days | 5 (illustrative) | Capability-profile parameter.
MCF-RES-024 | Post-event review deadline | days | 30 (illustrative) | Capability-profile parameter.
MCF-SUP-002 | Supplier monitoring interval | months | 6 | Illustrative; quarterly for sole-source suppliers.
MCF-SUP-004 | Sub-tier depth for critical classes | tiers | 2 | Illustrative; deeper where single-source components are known.
MCF-SUP-005 | Maximum on-site attendance time for critical electrical/mechanical faults | hours | 4 | Illustrative; set from DEP-003 time-to-impact and spares held.
MCF-SUP-006 | Evidence delivery time on request | working days | 10 | Illustrative.
MCF-SUP-007 | Notification intake test interval | months | 6 | Illustrative.
MCF-SUP-008 | Minimum transition assistance period | months | 12 | Illustrative.
MCF-SUP-010 | Serial verification coverage for safety-critical protection devices | % of units received | 100 | Illustrative.
MCF-SUP-012 | Target time to identify all affected units | hours | 24 | Illustrative.
MCF-SUP-012 | Traceability exercise interval | months | 12 | Illustrative.
MCF-SUP-015 | Maximum share of a redundant group updated per wave | % of group | 50 (and never all members) | Illustrative.
MCF-SUP-015 | Soak time between waves | hours | 24 | Illustrative.
MCF-SUP-016 | Remediation target for critical, exposed vulnerabilities | days | 14 | Illustrative; OT may require longer with compensating controls.
MCF-SUP-017 | Spares stock review interval | months | 6 | Illustrative.
MCF-SUP-017 | Spare-to-installed ratio for accelerator trays | % of installed | Site-specific (no default) | Derived from observed failure rates, RMA turnaround and the compute availability outcome.
MCF-SUP-018 | Lead-time refresh interval | months | 6 | Illustrative; lead times for electrical equipment can change materially within a year.
MCF-SUP-019 | Logistics continuity validation interval | months | 24 | Illustrative.
MCF-SUP-020 | Obsolescence planning horizon | months | 24 | Illustrative.
MCF-SUP-022 | Maximum default session duration | hours | 4 | Illustrative.
MCF-SUP-022 | Emergency activation review time | hours | 24 | Illustrative.
MCF-SUP-023 | Session recording retention | days | 90 | Illustrative.
MCF-SUP-024 | Maximum revocation time after notification | hours | 24 | Illustrative.
MCF-SUP-024 | Recertification interval | months | 3 | Illustrative.
MCF-SEC-001 | Leaver access removal deadline | h | 24 (illustrative) | Capability-profile parameter.
MCF-SEC-001 | Access recertification interval | months | 3 for privileged, 6 for standard (illustrative) | Capability-profile parameter.
MCF-SEC-002 | Maximum static credential lifetime (consequential authority) | days | 90 (illustrative) | Capability-profile parameter.
MCF-SEC-002 | Certificate expiry warning window | days | 30 (illustrative) | Capability-profile parameter.
MCF-SEC-003 | Maximum JIT elevation duration | h | 4 (illustrative) | Capability-profile parameter.
MCF-SEC-003 | Privilege boundary test interval | months | 6 (illustrative) | Capability-profile parameter.
MCF-SEC-004 | Break-glass rotation after use | h | 24 (illustrative) | Capability-profile parameter.
MCF-SEC-005 | Target security level for power and cooling control zones | SL (ISA/IEC 62443) | SL-T 2 minimum; SL-T 3 for zones whose compromise defeats CG-05/CG-06 (illustrative) | Assigned by risk assessment per ISA/IEC 62443-3-2.
MCF-SEC-005 | Controller logic integrity check interval | days | 7 (illustrative) | Capability-profile parameter.
MCF-SEC-006 | Escalation test interval | months | 12 (illustrative) | Capability-profile parameter.
MCF-SEC-008 | Destructive-operation delay | h | 24 (illustrative) | Capability-profile parameter.
MCF-SEC-009 | Zone reconciliation interval | months | 6 (illustrative) | Capability-profile parameter.
MCF-SEC-010 | Management segmentation test interval | months | 6 (illustrative) | Capability-profile parameter.
MCF-SEC-011 | Rule review interval | months | 6 (illustrative) | Capability-profile parameter.
MCF-SEC-012 | Maximum vendor session duration | h | 8 (illustrative) | Capability-profile parameter.
MCF-SEC-012 | Revocation effect time | min | 15 (illustrative) | Capability-profile parameter.
MCF-SEC-013 | Baseline compliance assessment interval | days | 30 (illustrative) | Capability-profile parameter.
MCF-SEC-013 | Baseline compliance target | % devices compliant | 98 (illustrative) | Capability-profile parameter.
MCF-SEC-014 | Remediation time for known-exploited vulnerabilities on reachable management planes | days | 14 (illustrative) | Capability-profile parameter.
MCF-SEC-015 | Maximum fraction of a redundancy group patched in one stage | % | 50 (illustrative) | Avoids common-mode failure (X08).
MCF-SEC-016 | Maximum exception duration | months | 12 (illustrative) | Capability-profile parameter.
MCF-SEC-017 | Silent-source alert threshold | min | 60 (illustrative) | Capability-profile parameter.
MCF-SEC-018 | Detection-to-triage target | min | 15 (illustrative) | Capability-profile parameter.
MCF-SEC-018 | Detection validation interval | months | 6 (illustrative) | Capability-profile parameter.
MCF-SEC-019 | Containment decision time target | min | 30 (illustrative) | Capability-profile parameter.
MCF-SEC-019 | Playbook exercise interval | months | 12 (illustrative) | Capability-profile parameter.
MCF-SEC-021 | Maximum automated setpoint change per interval | units per min | System-specific (illustrative: 1 °C per 5 min for supply temperature) | Capability-profile parameter set by engineering authority.
MCF-SEC-021 | Maximum nodes acted on per automated action | count | Fault-domain size (illustrative) | Limits blast radius.
MCF-SEC-023 | Allowlist test interval | months | 6 (illustrative) | Capability-profile parameter.
MCF-SEC-024 | Kill-switch halt time | s | 60 (illustrative) | Capability-profile parameter.
MCF-EVA-002 | Evidence request response time | working days | 10 | Engagement parameter; illustrative
MCF-EVA-004 | Evidence repository restoration test interval | months | 12 | Programme parameter; illustrative
MCF-EVA-006 | Integrity detection test interval | months | 12 | Programme parameter; illustrative
MCF-EVA-007 | Independent re-rating sample | % of supporting Evidence Objects | 10 | Programme parameter; illustrative, minimum of 10 objects
MCF-EVA-014 | UNKNOWN traceability test set size | UNKNOWN Records | 10 | Programme parameter; illustrative
MCF-EVA-021 | Expiry response time | working days | 20 | Programme parameter; illustrative
MCF-EVA-022 | Trigger test interval | months | 6 | Programme parameter; illustrative
MCF-EVA-023 | Maximum tolerated feed gap | % of period | 5 | Programme parameter; illustrative
MCF-EVA-024 | Suspension time after qualifying trigger | working days | 5 | Programme parameter; illustrative
MCF-EVA-024 | Suspension rehearsal interval | months | 12 | Programme parameter; illustrative

## Assessment Template
Control ID | Control Title | Claim Type | Required AL | In Scope (Y/N) | Result (CONFORMING/PARTIAL/NONCONFORMING/UNKNOWN/NOT_APPLICABLE/NOT_ASSESSED) | Evidence Package ID | Quality Vector | Sufficiency (S0-S5) | Confidence (CONF-0..4) | UNKNOWN Type/Severity | Findings | CRITICAL Gates Affected | Assessor | Reviewer | Date
MCF-GOV-001 | Governance Charter | DESIGN | AL2 |  | NOT_ASSESSED
MCF-GOV-002 | Decision Rights | IMPLEMENTATION | AL3 |  | NOT_ASSESSED | [6 empty] | CG-13
MCF-GOV-003 | Committee Oversight | OPERATION | AL4 |  | NOT_ASSESSED
MCF-GOV-004 | Methodology Ownership | IMPLEMENTATION | AL3 |  | NOT_ASSESSED
MCF-GOV-005 | RACI and Role Ownership | IMPLEMENTATION | AL3 |  | NOT_ASSESSED | [6 empty] | CG-13
MCF-GOV-006 | Critical Function Accountability | IMPLEMENTATION | AL3 |  | NOT_ASSESSED | [6 empty] | CG-13
MCF-GOV-007 | Risk Acceptance Authority | OPERATION | AL4 |  | NOT_ASSESSED | [6 empty] | CG-13
MCF-GOV-008 | Evidence Custody | OPERATION | AL4 |  | NOT_ASSESSED
MCF-GOV-009 | Policy Hierarchy | DESIGN | AL2 |  | NOT_ASSESSED
MCF-GOV-010 | Technical Standard Baselines | IMPLEMENTATION | AL3 |  | NOT_ASSESSED
MCF-GOV-011 | Exception Governance | OPERATION | AL4 |  | NOT_ASSESSED
MCF-GOV-012 | Document Lifecycle | IMPLEMENTATION | AL3 |  | NOT_ASSESSED
MCF-GOV-013 | Assurance Plan | DESIGN | AL2 |  | NOT_ASSESSED
MCF-GOV-014 | Risk Appetite Linkage | DESIGN | AL2 |  | NOT_ASSESSED
MCF-GOV-015 | Critical Gate Governance | OPERATION | AL4 |  | NOT_ASSESSED
MCF-GOV-016 | Independent Review | EFFECTIVENESS | AL5 |  | NOT_ASSESSED
MCF-GOV-017 | Stakeholder Obligations | DESIGN | AL2 |  | NOT_ASSESSED
MCF-GOV-018 | Regulatory Monitoring | OPERATION | AL4 |  | NOT_ASSESSED
MCF-GOV-019 | Customer Commitments | IMPLEMENTATION | AL3 |  | NOT_ASSESSED
MCF-GOV-020 | External Reporting | OPERATION | AL4 |  | NOT_ASSESSED
MCF-GOV-021 | Conflict Management | OPERATION | AL4 |  | NOT_ASSESSED
MCF-GOV-022 | Assessor Independence | IMPLEMENTATION | AL3 |  | NOT_ASSESSED
MCF-GOV-023 | Competence Management | OPERATION | AL4 |  | NOT_ASSESSED
MCF-GOV-024 | Appeal and Challenge | OPERATION | AL4 |  | NOT_ASSESSED
MCF-CAP-001 | Capability Register | IMPLEMENTATION | AL3 |  | NOT_ASSESSED | [6 empty] | CG-01
MCF-CAP-002 | Capability Ownership | IMPLEMENTATION | AL3 |  | NOT_ASSESSED | [6 empty] | CG-13
MCF-CAP-003 | Lifecycle Status | OPERATION | AL4 |  | NOT_ASSESSED
MCF-CAP-004 | Architecture Linkage | IMPLEMENTATION | AL3 |  | NOT_ASSESSED | [6 empty] | CG-02
MCF-CAP-005 | Availability Outcomes | DESIGN | AL2 |  | NOT_ASSESSED | [6 empty] | CG-01
MCF-CAP-006 | Performance Outcomes | DESIGN | AL2 |  | NOT_ASSESSED | [6 empty] | CG-01
MCF-CAP-007 | Integrity Outcomes | DESIGN | AL2 |  | NOT_ASSESSED | [6 empty] | CG-01
MCF-CAP-008 | Recovery Outcomes | DESIGN | AL2 |  | NOT_ASSESSED | [6 empty] | CG-01
MCF-CAP-009 | Criticality Criteria | DESIGN | AL2 |  | NOT_ASSESSED
MCF-CAP-010 | Impact Tolerance | DESIGN | AL2 |  | NOT_ASSESSED | [6 empty] | CG-01
MCF-CAP-011 | Stakeholder Consequence | DESIGN | AL2 |  | NOT_ASSESSED
MCF-CAP-012 | Priority Classification | IMPLEMENTATION | AL3 |  | NOT_ASSESSED
MCF-CAP-013 | Current Demand Baseline | OPERATION | AL4 |  | NOT_ASSESSED
MCF-CAP-014 | Peak and Transient Demand | OPERATION | AL4 |  | NOT_ASSESSED
MCF-CAP-015 | Growth Forecast | DESIGN | AL2 |  | NOT_ASSESSED
MCF-CAP-016 | Scenario Demand | RESILIENCE | AL5 |  | NOT_ASSESSED
MCF-CAP-017 | Load Envelope | IMPLEMENTATION | AL3 |  | NOT_ASSESSED
MCF-CAP-018 | Environmental Envelope | IMPLEMENTATION | AL3 |  | NOT_ASSESSED
MCF-CAP-019 | Duration Limits | EFFECTIVENESS | AL5 |  | NOT_ASSESSED
MCF-CAP-020 | State-Specific Limits | OPERATION | AL4 |  | NOT_ASSESSED
MCF-CAP-021 | Design-to-Operation Traceability | IMPLEMENTATION | AL3 |  | NOT_ASSESSED
MCF-CAP-022 | Commissioning Acceptance | EFFECTIVENESS | AL5 |  | NOT_ASSESSED
MCF-CAP-023 | Material Change Impact | OPERATION | AL4 |  | NOT_ASSESSED | [6 empty] | CG-14
MCF-CAP-024 | Retirement Control | IMPLEMENTATION | AL3 |  | NOT_ASSESSED
MCF-DEP-001 | Asset-to-Function Mapping | IMPLEMENTATION | AL3 |  | NOT_ASSESSED | [6 empty] | CG-03
MCF-DEP-002 | Upstream Dependency Mapping | IMPLEMENTATION | AL3 |  | NOT_ASSESSED | [6 empty] | CG-03
MCF-DEP-003 | Downstream Consequence Mapping | DESIGN | AL2 |  | NOT_ASSESSED
MCF-DEP-004 | Recovery Dependency Mapping | IMPLEMENTATION | AL3 |  | NOT_ASSESSED
MCF-DEP-005 | Shared Source Analysis | IMPLEMENTATION | AL3 |  | NOT_ASSESSED | [6 empty] | CG-03
MCF-DEP-006 | Common Controller Analysis | IMPLEMENTATION | AL3 |  | NOT_ASSESSED
MCF-DEP-007 | Shared Route Analysis | IMPLEMENTATION | AL3 |  | NOT_ASSESSED | [6 empty] | CG-03
MCF-DEP-008 | Shared Human Dependency Analysis | DESIGN | AL2 |  | NOT_ASSESSED
MCF-DEP-009 | Utility Dependency | IMPLEMENTATION | AL3 |  | NOT_ASSESSED | [6 empty] | CG-03
MCF-DEP-010 | Telecom Dependency | IMPLEMENTATION | AL3 |  | NOT_ASSESSED | [6 empty] | CG-03
MCF-DEP-011 | OEM Dependency | IMPLEMENTATION | AL3 |  | NOT_ASSESSED
MCF-DEP-012 | Cloud and Service Dependency | IMPLEMENTATION | AL3 |  | NOT_ASSESSED | [6 empty] | CG-03
MCF-DEP-013 | Capacity Concentration | DESIGN | AL2 |  | NOT_ASSESSED
MCF-DEP-014 | Supplier Concentration | DESIGN | AL2 |  | NOT_ASSESSED
MCF-DEP-015 | Knowledge Concentration | DESIGN | AL2 |  | NOT_ASSESSED
MCF-DEP-016 | Substitution Readiness | EFFECTIVENESS | AL5 |  | NOT_ASSESSED
MCF-DEP-017 | Assessment Boundary | IMPLEMENTATION | AL3 |  | NOT_ASSESSED | [6 empty] | CG-02; CG-03
MCF-DEP-018 | Provider Boundary | IMPLEMENTATION | AL3 |  | NOT_ASSESSED | [6 empty] | CG-13
MCF-DEP-019 | Tenant Boundary | IMPLEMENTATION | AL3 |  | NOT_ASSESSED
MCF-DEP-020 | Cross-Boundary Enforcement | OPERATION | AL4 |  | NOT_ASSESSED
MCF-DEP-021 | Dependency Health Indicators | OPERATION | AL4 |  | NOT_ASSESSED
MCF-DEP-022 | Provider Performance | OPERATION | AL4 |  | NOT_ASSESSED
MCF-DEP-023 | Change Detection | OPERATION | AL4 |  | NOT_ASSESSED
MCF-DEP-024 | Periodic Revalidation | OPERATION | AL4 |  | NOT_ASSESSED
MCF-PHY-001 | Site Hazard Assessment | DESIGN | AL2 |  | NOT_ASSESSED
MCF-PHY-002 | External Exposure | DESIGN | AL2 |  | NOT_ASSESSED
MCF-PHY-003 | Access and Logistics | OPERATION | AL4 |  | NOT_ASSESSED
MCF-PHY-004 | Adjacent Risk | DESIGN | AL2 |  | NOT_ASSESSED
MCF-PHY-005 | Structural Capacity | DESIGN | AL2 |  | NOT_ASSESSED
MCF-PHY-006 | Rack Loading | IMPLEMENTATION | AL3 |  | NOT_ASSESSED
MCF-PHY-007 | Anchorage and Vibration | IMPLEMENTATION | AL3 |  | NOT_ASSESSED
MCF-PHY-008 | Building Envelope | OPERATION | AL4 |  | NOT_ASSESSED
MCF-PHY-009 | Security Zones | IMPLEMENTATION | AL3 |  | NOT_ASSESSED
MCF-PHY-010 | Fire Zones | IMPLEMENTATION | AL3 |  | NOT_ASSESSED | [6 empty] | CG-09
MCF-PHY-011 | Water Zones | IMPLEMENTATION | AL3 |  | NOT_ASSESSED
MCF-PHY-012 | Tenant Segregation | IMPLEMENTATION | AL3 |  | NOT_ASSESSED
MCF-PHY-013 | Identity-Based Access | OPERATION | AL4 |  | NOT_ASSESSED
MCF-PHY-014 | Visitor Control | OPERATION | AL4 |  | NOT_ASSESSED
MCF-PHY-015 | Surveillance Coverage | IMPLEMENTATION | AL3 |  | NOT_ASSESSED
MCF-PHY-016 | Alarm Response | EFFECTIVENESS | AL5 |  | NOT_ASSESSED
MCF-PHY-017 | Delivery Controls | OPERATION | AL4 |  | NOT_ASSESSED
MCF-PHY-018 | Equipment Movement | OPERATION | AL4 |  | NOT_ASSESSED
MCF-PHY-019 | Media Custody | OPERATION | AL4 |  | NOT_ASSESSED
MCF-PHY-020 | Decommissioning Custody | OPERATION | AL4 |  | NOT_ASSESSED
MCF-PHY-021 | Fire Detection | EFFECTIVENESS | AL5 |  | NOT_ASSESSED | [6 empty] | CG-04
MCF-PHY-022 | Suppression Interfaces | EFFECTIVENESS | AL5 |  | NOT_ASSESSED | [6 empty] | CG-04
MCF-PHY-023 | Egress and Emergency Access | OPERATION | AL4 |  | NOT_ASSESSED | [6 empty] | CG-04
MCF-PHY-024 | Emergency Shutdown Governance | EFFECTIVENESS | AL5 |  | NOT_ASSESSED | [6 empty] | CG-04
MCF-POW-001 | Utility Capacity | OPERATION | AL4 |  | NOT_ASSESSED | [6 empty] | CG-05
MCF-POW-002 | Grid Quality | OPERATION | AL4 |  | NOT_ASSESSED
MCF-POW-003 | Connection Reliability | DESIGN | AL2 |  | NOT_ASSESSED
MCF-POW-004 | Utility Contingency | RESILIENCE | AL5 |  | NOT_ASSESSED
MCF-POW-005 | Generator Capacity | EFFECTIVENESS | AL5 |  | NOT_ASSESSED | [6 empty] | CG-05
MCF-POW-006 | Start Reliability | OPERATION | AL4 |  | NOT_ASSESSED | [6 empty] | CG-05
MCF-POW-007 | Fuel Autonomy | OPERATION | AL4 |  | NOT_ASSESSED | [6 empty] | CG-05
MCF-POW-008 | Fuel Replenishment | RESILIENCE | AL5 |  | NOT_ASSESSED
MCF-POW-009 | UPS Topology | IMPLEMENTATION | AL3 |  | NOT_ASSESSED | [6 empty] | CG-05
MCF-POW-010 | Battery Condition | OPERATION | AL4 |  | NOT_ASSESSED | [6 empty] | CG-04
MCF-POW-011 | Runtime and Derating | EFFECTIVENESS | AL5 |  | NOT_ASSESSED | [6 empty] | CG-05
MCF-POW-012 | Bypass Exposure | OPERATION | AL4 |  | NOT_ASSESSED
MCF-POW-013 | Switchgear Integrity | OPERATION | AL4 |  | NOT_ASSESSED | [6 empty] | CG-04
MCF-POW-014 | Selective Coordination | IMPLEMENTATION | AL3 |  | NOT_ASSESSED | [6 empty] | CG-09
MCF-POW-015 | Busway and PDU Capacity | OPERATION | AL4 |  | NOT_ASSESSED
MCF-POW-016 | Earthing and Bonding | IMPLEMENTATION | AL3 |  | NOT_ASSESSED | [6 empty] | CG-04
MCF-POW-017 | Voltage Quality | OPERATION | AL4 |  | NOT_ASSESSED
MCF-POW-018 | Harmonics | OPERATION | AL4 |  | NOT_ASSESSED
MCF-POW-019 | Transient Ride-Through | EFFECTIVENESS | AL5 |  | NOT_ASSESSED | [6 empty] | CG-05
MCF-POW-020 | Load-Step Response | EFFECTIVENESS | AL5 |  | NOT_ASSESSED | [6 empty] | CG-05
MCF-POW-021 | EPMS Coverage | IMPLEMENTATION | AL3 |  | NOT_ASSESSED | [6 empty] | CG-07
MCF-POW-022 | Preventive Maintenance | OPERATION | AL4 |  | NOT_ASSESSED
MCF-POW-023 | Switching Procedures | OPERATION | AL4 |  | NOT_ASSESSED | [6 empty] | CG-04
MCF-POW-024 | Black-Start and Restoration | RESILIENCE | AL5 |  | NOT_ASSESSED | [6 empty] | CG-10
MCF-THM-001 | Heat-Load Model | DESIGN | AL2 |  | NOT_ASSESSED
MCF-THM-002 | Design Capacity | IMPLEMENTATION | AL3 |  | NOT_ASSESSED | [6 empty] | CG-06
MCF-THM-003 | Resilient Capacity | RESILIENCE | AL5 |  | NOT_ASSESSED | [6 empty] | CG-06
MCF-THM-004 | Seasonal Derating | OPERATION | AL4 |  | NOT_ASSESSED | [6 empty] | CG-06
MCF-THM-005 | Airflow Management | OPERATION | AL4 |  | NOT_ASSESSED
MCF-THM-006 | Containment | IMPLEMENTATION | AL3 |  | NOT_ASSESSED
MCF-THM-007 | CRAH and In-Row Capacity | IMPLEMENTATION | AL3 |  | NOT_ASSESSED
MCF-THM-008 | Air-Side Monitoring | OPERATION | AL4 |  | NOT_ASSESSED
MCF-THM-009 | Direct-to-Chip Architecture | DESIGN | AL2 |  | NOT_ASSESSED
MCF-THM-010 | CDU Capacity | EFFECTIVENESS | AL5 |  | NOT_ASSESSED | [6 empty] | CG-06
MCF-THM-011 | Secondary Loop Integrity | OPERATION | AL4 |  | NOT_ASSESSED | [6 empty] | CG-06
MCF-THM-012 | Quick-Disconnect Management | OPERATION | AL4 |  | NOT_ASSESSED
MCF-THM-013 | Chiller Capacity | EFFECTIVENESS | AL5 |  | NOT_ASSESSED | [6 empty] | CG-06
MCF-THM-014 | Cooling Tower or Dry Cooler | OPERATION | AL4 |  | NOT_ASSESSED
MCF-THM-015 | Water Continuity | RESILIENCE | AL5 |  | NOT_ASSESSED | [6 empty] | CG-06
MCF-THM-016 | Heat-Rejection Dependency | DESIGN | AL2 |  | NOT_ASSESSED
MCF-THM-017 | Coolant Compatibility | DESIGN | AL2 |  | NOT_ASSESSED
MCF-THM-018 | Water Quality | OPERATION | AL4 |  | NOT_ASSESSED | [6 empty] | CG-04
MCF-THM-019 | Leak Detection | EFFECTIVENESS | AL5 |  | NOT_ASSESSED
MCF-THM-020 | Isolation and Drainage | EFFECTIVENESS | AL5 |  | NOT_ASSESSED | [6 empty] | CG-09
MCF-THM-021 | Control Stability | EFFECTIVENESS | AL5 |  | NOT_ASSESSED | [6 empty] | CG-07
MCF-THM-022 | Sensor Trust | OPERATION | AL4 |  | NOT_ASSESSED
MCF-THM-023 | Maintenance States | OPERATION | AL4 |  | NOT_ASSESSED
MCF-THM-024 | Thermal Recovery | RESILIENCE | AL5 |  | NOT_ASSESSED | [6 empty] | CG-10
MCF-ENV-001 | Temperature Control | OPERATION | AL4 |  | NOT_ASSESSED
MCF-ENV-002 | Humidity Control | OPERATION | AL4 |  | NOT_ASSESSED
MCF-ENV-003 | Particulate and Corrosion | OPERATION | AL4 |  | NOT_ASSESSED
MCF-ENV-004 | Vibration and Acoustic Conditions | IMPLEMENTATION | AL3 |  | NOT_ASSESSED
MCF-ENV-005 | PUE Measurement | OPERATION | AL4 |  | NOT_ASSESSED
MCF-ENV-006 | Energy Allocation | IMPLEMENTATION | AL3 |  | NOT_ASSESSED
MCF-ENV-007 | Efficiency Under Load | OPERATION | AL4 |  | NOT_ASSESSED
MCF-ENV-008 | Resilience-Efficiency Trade-Off | DESIGN | AL2 |  | NOT_ASSESSED
MCF-ENV-009 | Water Source and Quality | OPERATION | AL4 |  | NOT_ASSESSED
MCF-ENV-010 | WUE Measurement | OPERATION | AL4 |  | NOT_ASSESSED
MCF-ENV-011 | Water Scarcity Response | RESILIENCE | AL5 |  | NOT_ASSESSED
MCF-ENV-012 | Discharge Control | OPERATION | AL4 |  | NOT_ASSESSED
MCF-ENV-013 | Carbon Accounting Boundary | DESIGN | AL2 |  | NOT_ASSESSED
MCF-ENV-014 | Energy Attribute Evidence | IMPLEMENTATION | AL3 |  | NOT_ASSESSED
MCF-ENV-015 | Embodied Resource Data | DESIGN | AL2 |  | NOT_ASSESSED
MCF-ENV-016 | Reporting Traceability | OPERATION | AL4 |  | NOT_ASSESSED
MCF-ENV-017 | Battery Materials | OPERATION | AL4 |  | NOT_ASSESSED
MCF-ENV-018 | Refrigerants and Coolants | OPERATION | AL4 |  | NOT_ASSESSED | [6 empty] | CG-04
MCF-ENV-019 | Fuel and Suppressant Handling | OPERATION | AL4 |  | NOT_ASSESSED
MCF-ENV-020 | Hardware and Media Waste | OPERATION | AL4 |  | NOT_ASSESSED
MCF-ENV-021 | Heatwave Readiness | RESILIENCE | AL5 |  | NOT_ASSESSED
MCF-ENV-022 | Drought Readiness | DESIGN | AL2 |  | NOT_ASSESSED
MCF-ENV-023 | Flood Adaptation | DESIGN | AL2 |  | NOT_ASSESSED
MCF-ENV-024 | Long-Term Resource Constraints | DESIGN | AL2 |  | NOT_ASSESSED
MCF-CMP-001 | Accelerator Architecture | DESIGN | AL2 |  | NOT_ASSESSED
MCF-CMP-002 | Node Configuration | IMPLEMENTATION | AL3 |  | NOT_ASSESSED
MCF-CMP-003 | Rack-Scale Composition | IMPLEMENTATION | AL3 |  | NOT_ASSESSED
MCF-CMP-004 | Approved Baseline | IMPLEMENTATION | AL3 |  | NOT_ASSESSED
MCF-CMP-005 | Cluster Topology | DESIGN | AL2 |  | NOT_ASSESSED
MCF-CMP-006 | Scale-Up Domain Integrity | EFFECTIVENESS | AL5 |  | NOT_ASSESSED | [6 empty] | CG-08
MCF-CMP-007 | Partitioning | IMPLEMENTATION | AL3 |  | NOT_ASSESSED
MCF-CMP-008 | Fault-Domain Design | RESILIENCE | AL5 |  | NOT_ASSESSED | [6 empty] | CG-09
MCF-CMP-009 | Usable Accelerator Capacity | OPERATION | AL4 |  | NOT_ASSESSED | [6 empty] | CG-08
MCF-CMP-010 | Scheduler Controls | IMPLEMENTATION | AL3 |  | NOT_ASSESSED
MCF-CMP-011 | Resource Reservation | OPERATION | AL4 |  | NOT_ASSESSED
MCF-CMP-012 | Contention Management | OPERATION | AL4 |  | NOT_ASSESSED
MCF-CMP-013 | Firmware Baseline | IMPLEMENTATION | AL3 |  | NOT_ASSESSED | [6 empty] | CG-08
MCF-CMP-014 | Driver Compatibility | IMPLEMENTATION | AL3 |  | NOT_ASSESSED
MCF-CMP-015 | Upgrade Testing | EFFECTIVENESS | AL5 |  | NOT_ASSESSED | [6 empty] | CG-14
MCF-CMP-016 | Rollback Readiness | RESILIENCE | AL5 |  | NOT_ASSESSED
MCF-CMP-017 | GPU Telemetry | OPERATION | AL4 |  | NOT_ASSESSED
MCF-CMP-018 | Node Health | OPERATION | AL4 |  | NOT_ASSESSED
MCF-CMP-019 | Error and Degradation Detection | EFFECTIVENESS | AL5 |  | NOT_ASSESSED | [6 empty] | CG-08
MCF-CMP-020 | Performance Baselines | OPERATION | AL4 |  | NOT_ASSESSED
MCF-CMP-021 | Provisioning | IMPLEMENTATION | AL3 |  | NOT_ASSESSED
MCF-CMP-022 | Spares and RMA | OPERATION | AL4 |  | NOT_ASSESSED
MCF-CMP-023 | Node Rebuild | RESILIENCE | AL5 |  | NOT_ASSESSED | [6 empty] | CG-10
MCF-CMP-024 | Secure Retirement | IMPLEMENTATION | AL3 |  | NOT_ASSESSED
MCF-STO-001 | Training Data Tier | DESIGN | AL2 |  | NOT_ASSESSED
MCF-STO-002 | Checkpoint Tier | DESIGN | AL2 |  | NOT_ASSESSED
MCF-STO-003 | Model and Artifact Tier | IMPLEMENTATION | AL3 |  | NOT_ASSESSED
MCF-STO-004 | Archive Tier | IMPLEMENTATION | AL3 |  | NOT_ASSESSED
MCF-STO-005 | Throughput and IOPS | EFFECTIVENESS | AL5 |  | NOT_ASSESSED | [6 empty] | CG-08
MCF-STO-006 | Metadata Performance | OPERATION | AL4 |  | NOT_ASSESSED
MCF-STO-007 | Capacity Headroom | OPERATION | AL4 |  | NOT_ASSESSED
MCF-STO-008 | Burst Handling | EFFECTIVENESS | AL5 |  | NOT_ASSESSED
MCF-STO-009 | Data Integrity | EFFECTIVENESS | AL5 |  | NOT_ASSESSED | [6 empty] | CG-08
MCF-STO-010 | Metadata Integrity | EFFECTIVENESS | AL5 |  | NOT_ASSESSED | [6 empty] | CG-08
MCF-STO-011 | Checksum and Scrubbing | OPERATION | AL4 |  | NOT_ASSESSED
MCF-STO-012 | Configuration Consistency | IMPLEMENTATION | AL3 |  | NOT_ASSESSED
MCF-STO-013 | Snapshot Protection | OPERATION | AL4 |  | NOT_ASSESSED
MCF-STO-014 | Replication | RESILIENCE | AL5 |  | NOT_ASSESSED
MCF-STO-015 | Erasure Coding | RESILIENCE | AL5 |  | NOT_ASSESSED | [6 empty] | CG-09
MCF-STO-016 | Immutable Recovery Copy | RESILIENCE | AL5 |  | NOT_ASSESSED | [6 empty] | CG-10
MCF-STO-017 | Checkpoint Durability | EFFECTIVENESS | AL5 |  | NOT_ASSESSED | [6 empty] | CG-08
MCF-STO-018 | Restart Readiness | RESILIENCE | AL5 |  | NOT_ASSESSED | [6 empty] | CG-10
MCF-STO-019 | Storage Recovery Sequencing | RESILIENCE | AL5 |  | NOT_ASSESSED
MCF-STO-020 | Recovery Validation | RESILIENCE | AL5 |  | NOT_ASSESSED | [6 empty] | CG-10
MCF-STO-021 | Storage Telemetry | OPERATION | AL4 |  | NOT_ASSESSED
MCF-STO-022 | Capacity Forecasting | OPERATION | AL4 |  | NOT_ASSESSED
MCF-STO-023 | Media Health | OPERATION | AL4 |  | NOT_ASSESSED
MCF-STO-024 | Secure Sanitisation | IMPLEMENTATION | AL3 |  | NOT_ASSESSED
MCF-NET-001 | Fabric Topology | IMPLEMENTATION | AL3 |  | NOT_ASSESSED | [6 empty] | CG-08
MCF-NET-002 | Path Diversity | IMPLEMENTATION | AL3 |  | NOT_ASSESSED
MCF-NET-003 | Oversubscription | DESIGN | AL2 |  | NOT_ASSESSED
MCF-NET-004 | Fabric Fault-Domain Design | RESILIENCE | AL5 |  | NOT_ASSESSED | [6 empty] | CG-09
MCF-NET-005 | Latency Baseline | OPERATION | AL4 |  | NOT_ASSESSED
MCF-NET-006 | Loss and Retransmission | OPERATION | AL4 |  | NOT_ASSESSED
MCF-NET-007 | Congestion Control | EFFECTIVENESS | AL5 |  | NOT_ASSESSED | [6 empty] | CG-08
MCF-NET-008 | Collective Communication Performance | EFFECTIVENESS | AL5 |  | NOT_ASSESSED | [6 empty] | CG-08
MCF-NET-009 | Storage Fabric | EFFECTIVENESS | AL5 |  | NOT_ASSESSED | [6 empty] | CG-08
MCF-NET-010 | Frontend Network | IMPLEMENTATION | AL3 |  | NOT_ASSESSED
MCF-NET-011 | Service Gateways | OPERATION | AL4 |  | NOT_ASSESSED
MCF-NET-012 | Traffic Isolation | EFFECTIVENESS | AL5 |  | NOT_ASSESSED
MCF-NET-013 | Management Separation | IMPLEMENTATION | AL3 |  | NOT_ASSESSED
MCF-NET-014 | Console Access | IMPLEMENTATION | AL3 |  | NOT_ASSESSED
MCF-NET-015 | OOB Resilience | RESILIENCE | AL5 |  | NOT_ASSESSED | [6 empty] | CG-10
MCF-NET-016 | Break-Glass Access | EFFECTIVENESS | AL5 |  | NOT_ASSESSED
MCF-NET-017 | Cabling Standards | DESIGN | AL2 |  | NOT_ASSESSED
MCF-NET-018 | Optics Compatibility | IMPLEMENTATION | AL3 |  | NOT_ASSESSED
MCF-NET-019 | Cross-Connect Control | OPERATION | AL4 |  | NOT_ASSESSED
MCF-NET-020 | Path Documentation | IMPLEMENTATION | AL3 |  | NOT_ASSESSED
MCF-NET-021 | Controller Resilience | EFFECTIVENESS | AL5 |  | NOT_ASSESSED
MCF-NET-022 | Configuration Management | OPERATION | AL4 |  | NOT_ASSESSED | [6 empty] | CG-14
MCF-NET-023 | Flow Telemetry | OPERATION | AL4 |  | NOT_ASSESSED
MCF-NET-024 | Time and Core Services | EFFECTIVENESS | AL5 |  | NOT_ASSESSED
MCF-OPS-001 | 24x7 Coverage | OPERATION | AL4 |  | NOT_ASSESSED
MCF-OPS-002 | Role Clarity | IMPLEMENTATION | AL3 |  | NOT_ASSESSED | [6 empty] | CG-13
MCF-OPS-003 | Shift Handover | OPERATION | AL4 |  | NOT_ASSESSED
MCF-OPS-004 | Competence and Authorisation | OPERATION | AL4 |  | NOT_ASSESSED | [6 empty] | CG-04
MCF-OPS-005 | Standard Operating Procedures | IMPLEMENTATION | AL3 |  | NOT_ASSESSED
MCF-OPS-006 | Method Statements | OPERATION | AL4 |  | NOT_ASSESSED | [6 empty] | CG-14
MCF-OPS-007 | Permit to Work | OPERATION | AL4 |  | NOT_ASSESSED | [6 empty] | CG-04
MCF-OPS-008 | Lockout and Tagout | OPERATION | AL4 |  | NOT_ASSESSED | [6 empty] | CG-04
MCF-OPS-009 | Maintenance Strategy | DESIGN | AL2 |  | NOT_ASSESSED
MCF-OPS-010 | Condition Monitoring | OPERATION | AL4 |  | NOT_ASSESSED
MCF-OPS-011 | Calibration | OPERATION | AL4 |  | NOT_ASSESSED
MCF-OPS-012 | Deferred Maintenance | OPERATION | AL4 |  | NOT_ASSESSED
MCF-OPS-013 | Alarm Rationalisation | OPERATION | AL4 |  | NOT_ASSESSED | [6 empty] | CG-07
MCF-OPS-014 | Incident Response | OPERATION | AL4 |  | NOT_ASSESSED
MCF-OPS-015 | Root Cause Analysis | OPERATION | AL4 |  | NOT_ASSESSED
MCF-OPS-016 | Problem Elimination | EFFECTIVENESS | AL5 |  | NOT_ASSESSED
MCF-OPS-017 | Configuration Baseline | IMPLEMENTATION | AL3 |  | NOT_ASSESSED | [6 empty] | CG-14
MCF-OPS-018 | Change Assessment | OPERATION | AL4 |  | NOT_ASSESSED | [6 empty] | CG-14
MCF-OPS-019 | Temporary Configuration | OPERATION | AL4 |  | NOT_ASSESSED
MCF-OPS-020 | Rollback and Validation | EFFECTIVENESS | AL5 |  | NOT_ASSESSED | [6 empty] | CG-14
MCF-OPS-021 | Capacity Review | OPERATION | AL4 |  | NOT_ASSESSED
MCF-OPS-022 | Service Level Monitoring | OPERATION | AL4 |  | NOT_ASSESSED
MCF-OPS-023 | Resource Balancing | OPERATION | AL4 |  | NOT_ASSESSED
MCF-OPS-024 | Operational Reporting | OPERATION | AL4 |  | NOT_ASSESSED
MCF-RES-001 | Minimum Service Outcome | DESIGN | AL2 |  | NOT_ASSESSED
MCF-RES-002 | Graceful Degradation | EFFECTIVENESS | AL5 |  | NOT_ASSESSED
MCF-RES-003 | Resilience Scenarios | DESIGN | AL2 |  | NOT_ASSESSED
MCF-RES-004 | Resilience Ownership | DESIGN | AL2 |  | NOT_ASSESSED
MCF-RES-005 | Fault-Domain Definition | IMPLEMENTATION | AL3 |  | NOT_ASSESSED | [6 empty] | CG-09
MCF-RES-006 | Containment Boundaries | IMPLEMENTATION | AL3 |  | NOT_ASSESSED
MCF-RES-007 | Blast Radius | IMPLEMENTATION | AL3 |  | NOT_ASSESSED | [6 empty] | CG-09
MCF-RES-008 | Isolation Validation | RESILIENCE | AL5 |  | NOT_ASSESSED | [6 empty] | CG-09
MCF-RES-009 | Continuity Strategy | DESIGN | AL2 |  | NOT_ASSESSED
MCF-RES-010 | Alternative Capacity | EFFECTIVENESS | AL5 |  | NOT_ASSESSED
MCF-RES-011 | Site and Provider Continuity | IMPLEMENTATION | AL3 |  | NOT_ASSESSED
MCF-RES-012 | Crisis Priorities | DESIGN | AL2 |  | NOT_ASSESSED
MCF-RES-013 | Recovery Dependencies | IMPLEMENTATION | AL3 |  | NOT_ASSESSED | [6 empty] | CG-10
MCF-RES-014 | Recovery Sequencing | RESILIENCE | AL5 |  | NOT_ASSESSED | [6 empty] | CG-10
MCF-RES-015 | Configuration Restoration | EFFECTIVENESS | AL5 |  | NOT_ASSESSED
MCF-RES-016 | Data and Checkpoint Recovery | RESILIENCE | AL5 |  | NOT_ASSESSED | [6 empty] | CG-10
MCF-RES-017 | Component Tests | OPERATION | AL4 |  | NOT_ASSESSED
MCF-RES-018 | Integrated Scenario Tests | RESILIENCE | AL5 |  | NOT_ASSESSED | [6 empty] | CG-10
MCF-RES-019 | Tabletop Exercises | OPERATION | AL4 |  | NOT_ASSESSED
MCF-RES-020 | Lessons and Retest | OPERATION | AL4 |  | NOT_ASSESSED
MCF-RES-021 | Crisis Command | EFFECTIVENESS | AL5 |  | NOT_ASSESSED
MCF-RES-022 | Stakeholder Communications | OPERATION | AL4 |  | NOT_ASSESSED
MCF-RES-023 | Emergency Change | OPERATION | AL4 |  | NOT_ASSESSED
MCF-RES-024 | Post-Event Adaptation | OPERATION | AL4 |  | NOT_ASSESSED
MCF-SUP-001 | Supplier Capability | DESIGN | AL2 |  | NOT_ASSESSED
MCF-SUP-002 | Financial and Operational Resilience | OPERATION | AL4 |  | NOT_ASSESSED
MCF-SUP-003 | Security and Quality Posture | IMPLEMENTATION | AL3 |  | NOT_ASSESSED
MCF-SUP-004 | Sub-Tier Visibility | IMPLEMENTATION | AL3 |  | NOT_ASSESSED | [6 empty] | CG-03
MCF-SUP-005 | Service Levels | IMPLEMENTATION | AL3 |  | NOT_ASSESSED
MCF-SUP-006 | Evidence Rights | IMPLEMENTATION | AL3 |  | NOT_ASSESSED
MCF-SUP-007 | Incident Notification | OPERATION | AL4 |  | NOT_ASSESSED
MCF-SUP-008 | Exit and Transition Rights | DESIGN | AL2 |  | NOT_ASSESSED
MCF-SUP-009 | Approved Sourcing | IMPLEMENTATION | AL3 |  | NOT_ASSESSED
MCF-SUP-010 | Counterfeit Prevention | OPERATION | AL4 |  | NOT_ASSESSED
MCF-SUP-011 | Chain of Custody | OPERATION | AL4 |  | NOT_ASSESSED
MCF-SUP-012 | Component Traceability | EFFECTIVENESS | AL5 |  | NOT_ASSESSED
MCF-SUP-013 | Release Provenance | IMPLEMENTATION | AL3 |  | NOT_ASSESSED
MCF-SUP-014 | Signature Validation | EFFECTIVENESS | AL5 |  | NOT_ASSESSED
MCF-SUP-015 | Compatibility Assurance | EFFECTIVENESS | AL5 |  | NOT_ASSESSED
MCF-SUP-016 | Vulnerability Response | OPERATION | AL4 |  | NOT_ASSESSED
MCF-SUP-017 | Critical Spares | OPERATION | AL4 |  | NOT_ASSESSED
MCF-SUP-018 | Lead Times | DESIGN | AL2 |  | NOT_ASSESSED
MCF-SUP-019 | Logistics Continuity | RESILIENCE | AL5 |  | NOT_ASSESSED
MCF-SUP-020 | End-of-Life Planning | OPERATION | AL4 |  | NOT_ASSESSED
MCF-SUP-021 | Support Identity | IMPLEMENTATION | AL3 |  | NOT_ASSESSED | [6 empty] | CG-15
MCF-SUP-022 | Activation and Approval | OPERATION | AL4 |  | NOT_ASSESSED | [6 empty] | CG-15
MCF-SUP-023 | Session Monitoring | OPERATION | AL4 |  | NOT_ASSESSED
MCF-SUP-024 | Revocation and Review | OPERATION | AL4 |  | NOT_ASSESSED
MCF-SEC-001 | Human Identity | IMPLEMENTATION | AL3 |  | NOT_ASSESSED
MCF-SEC-002 | Machine Identity | IMPLEMENTATION | AL3 |  | NOT_ASSESSED
MCF-SEC-003 | Privileged Access | EFFECTIVENESS | AL5 |  | NOT_ASSESSED | [6 empty] | CG-15
MCF-SEC-004 | Break-Glass Governance | OPERATION | AL4 |  | NOT_ASSESSED
MCF-SEC-005 | BMS and EPMS Security | EFFECTIVENESS | AL5 |  | NOT_ASSESSED | [6 empty] | CG-07
MCF-SEC-006 | Cluster Manager Security | EFFECTIVENESS | AL5 |  | NOT_ASSESSED | [6 empty] | CG-15
MCF-SEC-007 | Fabric Controller Security | IMPLEMENTATION | AL3 |  | NOT_ASSESSED
MCF-SEC-008 | Storage Controller Security | IMPLEMENTATION | AL3 |  | NOT_ASSESSED
MCF-SEC-009 | Security Zoning | IMPLEMENTATION | AL3 |  | NOT_ASSESSED | [6 empty] | CG-07
MCF-SEC-010 | Management-Plane Segmentation | EFFECTIVENESS | AL5 |  | NOT_ASSESSED | [6 empty] | CG-15
MCF-SEC-011 | Filtering and Gateways | OPERATION | AL4 |  | NOT_ASSESSED
MCF-SEC-012 | Remote Access | EFFECTIVENESS | AL5 |  | NOT_ASSESSED | [6 empty] | CG-15
MCF-SEC-013 | Secure Baseline | IMPLEMENTATION | AL3 |  | NOT_ASSESSED
MCF-SEC-014 | Vulnerability Management | OPERATION | AL4 |  | NOT_ASSESSED
MCF-SEC-015 | Patch Governance | OPERATION | AL4 |  | NOT_ASSESSED
MCF-SEC-016 | Exception and Compensating Control | OPERATION | AL4 |  | NOT_ASSESSED
MCF-SEC-017 | Security Telemetry | OPERATION | AL4 |  | NOT_ASSESSED
MCF-SEC-018 | Behaviour Detection | EFFECTIVENESS | AL5 |  | NOT_ASSESSED
MCF-SEC-019 | Incident Containment | RESILIENCE | AL5 |  | NOT_ASSESSED
MCF-SEC-020 | Forensic Readiness | IMPLEMENTATION | AL3 |  | NOT_ASSESSED
MCF-SEC-021 | Agent or Automation Authority | IMPLEMENTATION | AL3 |  | NOT_ASSESSED | [6 empty] | CG-15
MCF-SEC-022 | Approval Controls | EFFECTIVENESS | AL5 |  | NOT_ASSESSED
MCF-SEC-023 | Command Allowlisting | EFFECTIVENESS | AL5 |  | NOT_ASSESSED | [6 empty] | CG-07
MCF-SEC-024 | Safe Rollback | RESILIENCE | AL5 |  | NOT_ASSESSED
MCF-EVA-001 | Evidence Taxonomy | DESIGN | AL2 |  | NOT_ASSESSED
MCF-EVA-002 | Evidence Ownership | IMPLEMENTATION | AL3 |  | NOT_ASSESSED
MCF-EVA-003 | Evidence Repository | IMPLEMENTATION | AL3 |  | NOT_ASSESSED
MCF-EVA-004 | Retention and Protection | RESILIENCE | AL5 |  | NOT_ASSESSED
MCF-EVA-005 | Source Provenance | OPERATION | AL4 |  | NOT_ASSESSED
MCF-EVA-006 | Integrity and Custody | EFFECTIVENESS | AL5 |  | NOT_ASSESSED
MCF-EVA-007 | Relevance and Reliability | OPERATION | AL4 |  | NOT_ASSESSED
MCF-EVA-008 | Currency and Coverage | OPERATION | AL4 |  | NOT_ASSESSED
MCF-EVA-009 | Decision Question | DESIGN | AL2 |  | NOT_ASSESSED | [6 empty] | CG-01
MCF-EVA-010 | Scope and Criteria | DESIGN | AL2 |  | NOT_ASSESSED | [6 empty] | CG-02
MCF-EVA-011 | Sampling and Testing | IMPLEMENTATION | AL3 |  | NOT_ASSESSED
MCF-EVA-012 | Specialist Involvement | IMPLEMENTATION | AL3 |  | NOT_ASSESSED
MCF-EVA-013 | Finding Traceability | OPERATION | AL4 |  | NOT_ASSESSED
MCF-EVA-014 | UNKNOWN Preservation | EFFECTIVENESS | AL5 |  | NOT_ASSESSED
MCF-EVA-015 | Conflict Handling | OPERATION | AL4 |  | NOT_ASSESSED
MCF-EVA-016 | Limitation Disclosure | OPERATION | AL4 |  | NOT_ASSESSED
MCF-EVA-017 | Gate Applicability | DESIGN | AL2 |  | NOT_ASSESSED
MCF-EVA-018 | Gate Evidence | OPERATION | AL4 |  | NOT_ASSESSED
MCF-EVA-019 | Independent Decision | IMPLEMENTATION | AL3 |  | NOT_ASSESSED
MCF-EVA-020 | Claim Language | OPERATION | AL4 |  | NOT_ASSESSED
MCF-EVA-021 | Evidence Expiry | OPERATION | AL4 |  | NOT_ASSESSED
MCF-EVA-022 | Change Triggers | EFFECTIVENESS | AL5 |  | NOT_ASSESSED
MCF-EVA-023 | Monitoring Coverage | OPERATION | AL4 |  | NOT_ASSESSED
MCF-EVA-024 | Decision Suspension and Supersession | RESILIENCE | AL5 |  | NOT_ASSESSED

## Amendment Log
Amendment ID | Date | Status | Summary
AIDCF-007A-AMD-001 | (as stated in v1.0 issue) | Approved by baseline owner; independent ratification pending | Adopted the 15/90/360 cardinality and MCF identifier baseline and deprecated narrative statements of 14/84/336.
AIDCF-007A-AMD-002 | 2026-10-10 | PROPOSED - Draft for controlled review | Per-control content rewrite, duplicate-title fixes, control-specific CRITICAL/SUPPORTING gate mapping, per-control assurance levels, evidence requirement profiles, assessment template restored.